## Notes
Data Sources
Dataset | Dodge 2023
CEUS 2022
CBECS 2018
ComStock 2023
Prototype | CEC prototype (CBECC 2022.3.1) | https://bees.noresco.com/software2022.html
| PNNL prototype (90.1-2022) | https://www.energycodes.gov/prototype-building-models#Commercial
| DEER prototype (June 2023) | https://github.com/sound-data/DEER-Prototypes-EnergyPlus
Codes | Title 24, part 6, referred to as T24 (1986, 1992, 2001, 2007, 2013, 2016, 2019, 2022, 2025)
ASHRAE 90.1 (2022)
| CFR Title 10 (2009) | https://www.govinfo.gov/content/pkg/FR-2009-03-23/pdf/FR-2009-03-23.pdf
| CFR Title 10 ( 2013) | https://www.govinfo.gov/content/pkg/CFR-2013-title10-vol3/pdf/CFR-2013-title10-vol3-part431.pdf
| CFR Title 10 ( 2024) | https://www.govinfo.gov/content/pkg/CFR-2024-title10-vol3/pdf/CFR-2024-title10-vol3-part431-subpartF.pdf
Others | ACM (2013, 2019, 2022, 2025)
| Title 24, 2022 - Appendix 5.4A and Appendix 5.4B | https://www.energy.ca.gov/publications/2022/2022-nonresidential-and-multifamily-alternative-calculation-method-reference
| 2022 Reduced infiltration CASE report | https://title24stakeholders.com/wp-content/uploads/2020/10/2022-T24-Final-CASE-Report_Reduce-Infiltration.pdf
| 2019 Outdoor Lighting CASE Report | https://title24stakeholders.com/wp-content/uploads/2016/10/T24-2019-CASE-Study-Results-Report-Outdoor-Sources_Final_with-Attachments.pdf
| PNNL 20405, 2010 | https://www.pnnl.gov/main/publications/external/technical_reports/PNNL-20405.pdf
| Air leakage Memo, NORESCO, 2025 | https://2050partners.sharepoint.com/:w:/r/sites/CalBEMCollaborativeEfforts/_layouts/15/Doc.aspx?sourcedoc=%7B3BEF8F74-7FAC-44F2-A70C-D76617660066%7D&file=Infiltration_rate_report_14May2025-Short-Version.docx&action=default&mobileredirect=true
| Design Guide: Advanced Water Heating for Foodservice (2022) (by GTI and Frontier funded by SoCalGas and Pacific Gas and Electric Company | https://caenergywise.com/design-guides/Advanced-Water-Heating-Design-Guide.pdf
| Design Guide 1 : Improving Commercial Kitchen Ventilation System Performance : Selecting & Sizing Exhaust Hoods referred as CKV (2004) (by SCE) | https://www.streivor.com/wp-content/uploads/2020/11/CKV-Design-Guide-1-Selecting-and-Sizing-Exhaust-Hoods.pdf
| Proposed Updates to Equipment Power Densities and Building Schedules for the 2028 Energy Code, referred to as "Plug load and schedules project with CEC, 2025" (Docket Number =25-BSTD-03 & TN=265693) | https://efiling.energy.ca.gov/GetDocument.aspx?tn=265693&DocumentContentId=102545
Construction Rate
Notes
RestaurantFastFood | Is a subcategory of food service building used for prepared-food sales. These places are often quick-service operations (e.g., drive-throughs, counter-service eateries,...).
EIS, 2018: | U.S. Energy Information Administration - EIA - Independent Statistics and Analysis
RestaurantFastFood (STC:3)
Year | Total floor area (k ft2) | Count
1967 | 5361.9 | 152
1968 | 8271 | 452
1969 | 13593.6 | 655
1970 | 14323.7 | 601
1971 | 13719.8 | 592
1972 | 16513.9 | 687
1973 | 27619.6 | 920
1974 | 26732 | 804
1975 | 13654.6 | 710
1976 | 19608.4 | 853
1977 | 29745.3 | 1055
1978 | 40044.4 | 1359
1979 | 40268.5 | 1053
1980 | 26862.2 | 851
1981 | 21498.2 | 812
1982 | 14017.9 | 606
1983 | 19364.4 | 880
1984 | 31271.7 | 1271
1985 | 44833.1 | 1461
1986 | 46291.2 | 1382
1987 | 46613.6 | 1265
1988 | 50555.2 | 1237
1989 | 48019.1 | 1233
1990 | 37809.8 | 1111
1991 | 20082.4 | 768
1992 | 11010.9 | 426
1993 | 7511.2 | 470
1994 | 11961.3 | 465
1995 | 13270.9 | 521
1996 | 20653.8 | 570
1997 | 27588.9 | 407
1998 | 41631.3 | 476
1999 | 48039.6 | 533
2000 | 52612.2 | 500
2001 | 40337.2 | 432
2002 | 33147.2 | 399
2003 | 30982.8 | 398
2004 | 29560.8 | 417
2005 | 27484.1 | 347
2006 | 25891.9 | 299
2007 | 25769.2 | 248
2008 | 20632.6 | 236
2009 | 5608 | 122
2010 | 2602.9 | 47
2011 | 3617.9 | 36
2012 | 8233.2 | 63
2013 | 17625.9 | 46
2014 | 13973.9 | 72
2015 | 29759.5 | 104
2016 | 25538.8 | 152
2017 | 27796.9 | 105
2018 | 32684.7 | 117
2019 | 30948.5 | 141
2020 | 34022.9 | 162
2021 | 53815 | 225
2022 | 41442.1 | 218
2023 | 10975.7 | 44
Dodge Construction data , 2023

## Prototype
NORESCO, Updated August 2025
RestaurantFastFood
Characteristic | Value | Data Sources
Building Type | Fast Food Restaurant
Building Category | Nonresidential
Vintages | 4 Vintages: Pre-1978 , 1978-1997 ,1998-2007 , 2008-2018 New Construction (2019+) | Based on the vintage bin analysis | NonRes-Vintage bins-Draft Report-30Nov2023-Final.docx
Shape |  | CEC Prototype 2022
Total Floor Area (ft²) | 2502 (50 ft * 50 ft) | CEC Prototype 2022
Aspect Ratio | 1 | CEC Prototype 2022
Number of Floors | 1 | CEC Prototype 2022
Roof type | Attic (17°) | CEC Prototype 2022
WWR | Average 14% (South: 28% , East: 14% ,North: 0% ,West: 14% | CEC Prototype 2022
Shading Geometry | No shades
Floor to floor height (ft) | N/A | CEC Prototype 2022
Floor to ceiling height (ft) | 10 | CEC Prototype 2022
Glazing sill height (ft) | 3.5 (top of the window is 6.5 ft high with 3 ft high glass) | CEC Prototype 2022
Background Data [To be deleted prior to publication]
According to CBECS 2018, small restaurants mostly have flat or shallow pitch roofs.
Existing public prototypes
|  | PNNL (Fast Food) | CEC (Small Restaurant) | CPUC (Fast Food)
Geometry | Whole building
Floor area (ft²) | Total | 2500 | 2500 | 1998
Height (ft) | All | 10 | 10 | 10
Zones |  | Dining 50%, Kitchen 50%, Attic (NOT conditioned) | Dining 50% , Kitchen 50%, Attic (NOT conditioned) | Dining 40% , Kitchen 40% , Waiting Area 15% , Restroom 5% (100 sf)
Internal Load
People (person/ft²) | Dining | 0.07 | 0.033 | 0.033
| Kitchen | 0.005 (6.3 people) | 0.0025 | 0.0025
| Other zones (if any) | - | - | 0.033 Lobby & 0.005 Restroom
Lights (W/ft²) | Dining | 0.38 | 0.45 | 0.45
| Kitchen | 0.89 | 0.95 | 0.95
| Other zones (if any) |  |  | 0.7 Lobby, 0.65 Restroom
Ext lights (W) | Whole building | 952 (209 and 743) | - | -
Gas Equipment (Btu/h-ft2) | Kitchen | 237.4 (296,748 Btu/h) | 32.4 | 17.5
Electric Equipment (W/ft²) | Dining | 10.3 (12,835 W) | 0.75 (0.5 receptacle & 0.25 refrigerator ) | 0.75 (0.5 & 0.25)
| Kitchen | 24.29 (29,769 W receptacle & 313 W ReachIn Refrigerator & 277 W ReachInFreezer) | 2.62 (1.5 receptacle & 1.12 refrigerator) | 2.62 (1.5 & 1.12)
| Other zones (if any) | - | - | 0.5 Lobby
Refrigerator | Kitchen | In addition to the Reachin freezer and refrigerator load defined as electric load, it has : 2 Case refrigerator : 716 and 763 Btu/hr-ft for 8 and 10 ft cases 2.5 COP for design compressor rack 1126 Btu/h for fan power of design compressor | Two refrigerator loads is defined as electric equipment load for dining and kitchen | expected to simulate the Refrigerator loads as electric equipment load ( like CEC)
HVAC System
Heating Sizing Factor | All | H&C: 1.2 | H&C:1 | H: 2.5 , C: 2.3
HVAC | Dining | PSZ AC: CAV no reheat, DX cooling coil: multi speed, Gas heating coil | (BAseAirSys 13): VAV no Reheat +DX cooling coil:two speed, Gas Heating coil | Single Zone VAV no Reheat , DX cooling coil:multi speed, Gas heating coil
| Kitchen | PSZ AC : CAV no reheat, DX cooling coil: multi speed, Gas heating coil | (sys7or3a): CAV no Reheat+DX cooling coil: single speed+ Gas Heating coil | Single Zone VAV no Reheat , DX cooling coil:single speed, Gas heating coil
| Other zones (if any) | - | - | For each Lobby and Restroom: Single Zone VAV no Reheat, DX cooling coil:multi speed , Gas heating coil
Exhaust Fan | Dining | 881 cfm with efficiency of 1
| Kitchen | 3300 cfm with efficiency of 0.385 | 2400 cfm with efficiency of 0.43
Thermostat Setpoint (F) | Dining Heating | 70 (setback: 60) | 70 (setback: 60) | 70 (setback: 60)
| Dining Cooling | 75 (setback: 86) | 75 (setback: 85) | 75 (setback: 85)
| Kitchen Heating | 66 (setback: 60) | 70 (setback: 60) | 70 (setback: 60)
| Kitchen Cooling | 79 (setback: 86) | 75 (setback: 85) | 75 (setback: 85)
Water Heater
Tank Volume (gal |  | 100 | 30 | Autosize (Nominal tank volume for autosizing: 39.6) Output file :69 gal
Peak Flow Rate (gpm) | Dining | - | 0.4 | 0.51
| Kitchen | 1.52 | 0.03 | 0.04
| Other zones (if any) |  |  | 0.03 Lobby
Loop Max and Min Temperature (F) |  | 140, 50 | 212, 32 | 212 , 50
Tank Max Temperature (F) |  | 180 | 180 | 212
Yealy Water Usage (gal) from the output files |  | 204731.75 | 71224 | 95967.6776
ASHRAE DOE
Kitchen loads are included in the EnergyPlus Electric Equipment and Gas Equipment objects

## Zones
Proposed Layout - RestaurantFastFood
Space Type | Space/Thermal Zone | HVAC zone | Schedule Category | Conditioned (Y/N) | Area Fraction | Area (ft²) | Volume (ft³) | Multipliers | Number of People | People (Persons/1,000 ft²) [T24, 2025,Table 120.1-A] | Kitchen (North) , Dining (south)
Dining Area (Cafeteria/Fast Food) | Dining | AHU 1 | Restaurant | Y | 50% | 1250 | 12500 | 1 | 41.25 | 33
Kitchen/Food Preparation Area | Kitchen | AHU 2 | Kitchen | Y | 50% | 1250 | 12500 | 1 | 3.75 | 3
Attic | Attic | n/a |  | N |  | 2500 | 25000 | 1 | 0
Total (3 space type) | Total (3 Space) | Total ( 2 HVAC Zones) | Total (2 category) | Total (2 Conditioned zones) | 1 | 2500 | 25000
Background Data [To be deleted prior to publication]
N

## Envelope
Envelope - RestaurantFastFood
Element | Prototype | Assembly Type | Construction | Thermal properties | Vintage | Selected T24 | Note | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
External Wall | RestaurantFastFood | ExtWall_WoodFramed_NonRes | Stucco + insulation + wood framing + gypsum board | U-factor IP | Pre 1978 | N/A | ASHRAE 90.1, 2022 Table A3.4.3.1, 3.5", R-0 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292
[5 empty] | 1978-1997 | 1986 | Copied from low-rise office alternative table: Package A with heat capacity of 0.0-3.99 (Btu/F-ft²) | 0.13298 | 0.13298 | 0.13298 | 0.13298 | 0.13298 | 0.13298 | 0.13298 | 0.13298 | 0.13298 | 0.13298 | 0.13298 | 0.13298 | 0.13298 | 0.13298 | 0.13298 | 0.13298
[5 empty] | 1998-2007 | 2001 | Table 1-H | 0.084 | 0.084 | 0.092 | 0.092 | 0.092 | 0.092 | 0.092 | 0.092 | 0.092 | 0.084 | 0.084 | 0.084 | 0.084 | 0.084 | 0.084 | 0.084
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.102 | 0.059 | 0.11 | 0.059 | 0.102 | 0.11 | 0.11 | 0.102 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.042 | 0.059
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.078 | 0.053 | 0.102 | 0.053 | 0.095 | 0.102 | 0.102 | 0.095 | 0.053 | 0.053 | 0.042 | 0.053 | 0.053 | 0.053 | 0.038 | 0.053
Ceiling/Roof | RestaurantFastFood | AtticFloor Reversed | Attic roof (no insulation): asphalt shingles + gypsum board Ceiling (wood-joist): insulation + gypsum board | U-factor IP | Pre 1978 | N/A | Considering 30 years for roof/ insulation replacement. | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 1978-1997 | 1992 |  | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 1998-2007 | 2001 | Table 1-H | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.049 | 0.039 | 0.039 | 0.039 | 0.049 | 0.075 | 0.067 | 0.067 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.047 | 0.047 | 0.047 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028
Windows | RestaurantFastFood | FixedWindow_NonRes | Single Pane (CBECS 2018, ~ 30 % of windows of Restaurant built before 2000 are single pane) | U-factor IP | Pre 1978 | N/A | ASHRAE Handbook of Fundamentals for single pane & T24 2013 for double pane (30%-70%) | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624
[5 empty] | 1978-1997 | N/A |  | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | These vintages have better performance because of partial retrofit
|  |  | Double pane |  | 1998-2007 | 2001 | Table 1-H | 0.49 | 0.49 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.34 | 0.36 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.36
|  |  | Single Pane (CBECS 2018, ~ 30 % of windows of Restaurant built before 2000 are single pane) | SHGC | Pre 1978 | N/A | ASHRAE Handbook of Fundamentals for single pane & T24 2013 for double pane (30%-70%) | 0.415 | 0.415 | 0.415 | 0.415 | 0.415 | 0.415 | 0.415 | 0.415 | 0.415 | 0.415 | 0.415 | 0.415 | 0.415 | 0.415 | 0.415 | 0.415
[5 empty] | 1978-1997 | N/A |  | 0.415 | 0.415 | 0.415 | 0.415 | 0.415 | 0.415 | 0.415 | 0.415 | 0.415 | 0.415 | 0.415 | 0.415 | 0.415 | 0.415 | 0.415 | 0.415 | These vintages have better performance because of partial retrofit
|  |  | Double pane |  | 1998-2007 | 2001 | Table 1-H (Non North, 10-20% total WWR) | 0.43 | 0.36 | 0.55 | 0.55 | 0.55 | 0.61 | 0.61 | 0.61 | 0.61 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.43
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.22 | 0.25 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.25
Infiltration
[5 empty] | Vintage | I_75 (cfm/ft2) 6-sdied Infiltration rate @ 75 pa | Source | CZ1: I-design (cfm/ft²) (4-sided Infiltration rate at normal pressure) (Design flow rate approach and Flow/Exterior Wall Area calculation method)
|  |  |  | Infiltration | Pre 1978 | 1.1 | 2022 CASE report (Table 38) | CZ1: 0.4312
[5 empty] | 1978-1997 | 1.1 | 2022 CASE report (Table 38) | CZ1: 0.4312
[5 empty] | 1998-2007 | 1.1 | 2022 CASE report (Table 38) | CZ1: 0.4312
[5 empty] | 2008-2018 | 1 | 2022 CASE report (Table 38) & T24, 2008-2016 (Table 140.3-B) | CZ1: 0.3945
[5 empty] | 2019+ | 0.6 | 2022 CASE report (Table 38) & T24, 2025 (Table 140.3-B) | CZ1: 0.2352
Source: T24 air barrier requirements (all editions) , the standardized infiltration rate reported in the 2022 CASE report, and Dodge 2023 data
Infiltration_rate_report_14May2025-Short-Version.docx
Background Data [To be deleted prior to publication]
T24, 1986
For NEW NONRESIDENTIAL BUILDINGS OF OCCUPANCIES A, 5, E AND H:
HDD for each CZ in CA | <3500
weight of wall | <10 lb/ft²
TD eq (<10 lb/ft²) | 44 |  | U wall base on HDD | 0.33302
MCF (<10 lb/ft²) | 1 |  | U wall base on CDD | 0.8165
Aow (ft²)= | 5600
Awall (ft²) | 4816 |  | U wall (Btu/hr-ft²-F) | 0.33302
Awindows(ft²) ~ | 784
0
Min OTTV | 31 | Frame Fig 2-53E
Min Uow (HDD< 3500) | 0.39 | Frame Fig 2-53B

## HVAC System
HVAC system - RestaurantFastFood
Vintage | Space/Thermal Zone | Heating | Cooling | Air Distribution | Other Systems | Source
Existing | Dining | Gas Furnace (PSZAC) | DX Coil (PSZAC) | CAV (PSZAC) | Economizer for after 2008 | CEUS 2022 + Engineering Judgement
| Kitchen | Gas Furnace (PSZAC) | DX Coil (PSZAC) | CAV (PSZAC) | Makeup Air Unit (Combo with RTU) to supply make-up air exceeding transfer air from dining space (can be included in system13b)
New Construction | Dining | Gas Furnace (PSZAC) | DX Coil (PSZAC) | CAV (PSZAC) | Economizer | T24, 2025 | Deman control ventilation
| Kitchen | Gas Furnace (PSZAC) | DX Coil (PSZAC) | CAV (PSZAC) | HR-Makeup Air Unit (systems that integrate make-up air and heat recovery functions) (can be included in system13b)
Efficiency of HVAC system (Efficiency is capacity-dependent. The following Table provides a general estimate of system efficiency based on what we saw in the existing prototype runs, or assuming cooling load based on rule of thumb)
Vintage | Upgrade/Installed year | Gas Furnace | Dining DX cooling (<65,000 Btu/h) | Kitchen DX cooling (>=65,000 and < 135,000 Btu/h ) | Source | Note
Pre 1978 | 2008 | Efficiency 80% | SEER 13 | EER 10.3 | System <65,000: 10 CFR, 2009 (Vol. 74, No. 54 , page 12074) system >65,000: T24, 2008, Table 112-A | Econ Max Position=0.9. *Econ Max Position is set to below 1 to approximate effects of not having fault detection and diagnostics (FDD) requirements, which began in 2013. it can be modeled in E+ either by: - Reducing Maximum Outdoor Air Flow Rate in Controller:OutdoorAir. - Or using FaultModel objects to simulate pre-2013 “no FDD” conditions
1978-1997
1998-2007
2008-2018 | 2013 | Efficiency 80% | SEER 13 | EER 11.2 | System <65,000: 10 CFR, 2013, Table 1 TO § 431.97 System >65,000: T24, 2013, Table 110.2-A | Econ Max Position=0.9
New Construction | 2025 | Efficiency 80% | SEER2 13.4 | EER 11.2 | System <65,000: 10 CFR, 2024 ,Table 19 TO § 431.97(h) System >65,000: T24, 2025, Table 110.2-A | - Econ Max Position=1 - Deduct 0.2 from the required EERs and IEERs for units with a heating section other than electric resistance heat.
Fan Power
Vintage | Approach | System | Total Static Pressure (TSP) (in w.c.) [PNNL 20405, 2010, Table 5.11] | Fan Efficiency [ACM 2025] | Fan Motor and Drive Efficiency [ACM 2025, Table 13] | W/cfm [ACM 2025, Table 14 and 15] | Data Source
Existing | PNNL TSP | CAV Kitchen (system <7,437 cfm) | 2.5 | 0.65 | ~0.9 (The full-load efficiency of the motor serving the fan- will be determined based on ACM 2025, Table 13) |  | ACM 2025, PNNL 20405, 2010
|  | CAV Dining (system <7,437 cfm) | 2.5 | 0.65
Brake horse power (bhp)=(Supply cfm*TSP in w.c.)/(6356*Fan efficiency)
Fan power (w/cfm) = bhp/motor and drive efficiency *746
New Construction | ACM 2025 | CAV Kitchen (system <5000 cfm) | 3.9974 | 0.65 | 0.9 | 0.802 (SZAC system <5,000 cfm ) | ACM 2025
|  | CAV Dining (system <5000 cfm) | 3.9974 |  |  | 0.802 (SZAC system <5,000 cfm )
* 0.9 is an average fan efficiency according to ACM 2025, Table 13
Fan total eff (E+ input) = 0.65 x Motor_eff
TSP (E+ input) in w.c. = Motor_eff/746 x (6356 x Fan_eff) x W/cfm
Fan_eff=0.65
Background Data [To be deleted prior to publication]
CEUS 2022:
| Heating |  |  | Cooling |  | Air Distribution | Water Heater
| Floorspace Heated | Primary Heating The default is the floorspace method unless otherwise specified | Fuel Type | Floorspace Cooled | Primary Cooling The default is the floorspace method unless otherwise specified | Primary Air Dis The default is the floorspace method unless otherwise specified | Fuel Type
RestaurantFastFood | 89.71% | Package System / Heat Pump (83.0%) | (65 % Gas, 34% Elec) | 91.01% | Package System / Heat Pump (83.1%) | Single Duct CAV (95.0%) | (Gas 78%, 18% Elec)
System13b
ACM 2025, Section: 5.1.3 : System 13b – PKITCHMAU serving the restaurant commercial kitchen zone
ACM 2025, |  | PNNL 20405, 2010 |  |  | T24 2019, same as 90.1:

## Thermostat
Thermostat Setpoints - RestaurantFastFood
Space/Thermal Zone | Setpoint | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16 | Source
Dining | Heating Setpoint (F) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | T24 2022 - Appendix 5.4B
| Heating Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
| Cooling Setpoint (F) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
| Cooling Setback (F) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
Kitchen | Heating Setpoint (F) | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | PNNL 09.1, 2022 Restaurant prototype
| Heating Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
| Cooling Setpoint (F) | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79
| Cooling Setback (F) | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86
PNNL's comfort range in kitchen is 4 F wider : 66 -79 F (with Heating setback of 60 F and Cooling setback of 86 F)
CPUC has the same setpoint and setback as CEC

## Ventilation
Outdoor Airflow Rate - RestaurantFastFood
Space/Thermal Zone | Number of People | Floor Area (ft²) | cfm/person [T24, 2025, Equation 120.1-F and Table 120.1-A] | cfm/ft² [T24, 2025, Equation 120.1-F and Table 120.1-A] | Required Exhaust Rate [T24, 2025, Table 120.1-B – minimum exhaust rates] | Total cfm Driven by People | Total cfm Driven by Area | Total cfm Driven by Exhaust | Total cfm | Notes
Dining | 41.25 | 1250 | 15 | 0.15 | 2 restroom, each 25/50 cfm pr unit | 618.75 | 187.5 | 100 | 618.75
Kitchen | 3.75 | 1250 | 15 | 0.15 | 0.7 cfm/ft2 | 56.25 | 187.5 | 875 | 875
Attic
Fine storage is defined for normal inventory that doesn't require an extra exhaust rate based on the space functions in T24, Part6, 2025, Table 120.1 B.
Exhaust hood
Type of Hood |  | Max Exhaust Flow Rate (cfm/ft) [T24, 2025, Table 140.9-C] | Hood Length (ft) * [CKV, 2004] & | Hood Exhaust Rate (cfm) | Note
Type I , wall-mounted canopy, medium duty hood |  | 210 | 15.25 | 3202.5
Efficiency of exhaust fan is 50% (according to ACM, 2025,section 5.7.3)
Quick Service Restaurant Hood Appliance
Appliance | Count | Length (ft) | Source
Two Fryers side | 2 | 2.5 | CKV Design Guide, 2004
Fryer drip station (doesn't generate heat or grease but still need to be covered) | 1 | 1.25
Griddle | 1 | 4
Convection oven | 1 | 2.5
Charbroiler | 1 | 4 | Charbroiler is common in fast food with burgers in the menu (e.g., KFC). So, we've decide to add this appliance to the above mentioned ones
Total cooking line length (ft) | 14.25
Hood length (ft) (+1 ft buffer) | 15.25
Background Data [To be deleted prior to publication]
T24, 2025:
ACM 2025, 5.7.3: EXHAUST FAN CONTROL METHOD
202 Commercial Kitchen Design Guide by SCE
CKV Design Guide
Kitchen photos from google browsing

## Water Heater
Water Heater Summary - RestaurantFastFood
Vintage | WH Type | Efficiency | Tank Volume (gal) | Tank Loss
Existing | Gas | 80% | 50 | 903 (Btu/hr)
New Construction | Gas | 80% | 50 | 903 (Btu/hr)
Peak Hot Water Consumption
Space Name | Baseline WH Type [T24, 2022, Appendix 5.4A , sheet: "2022 SpaceFuncData-Input"] | Total Area (ft²) | Number of People | Hot Water Usage Specification (gal/hr per person) [T24, 2022, Appendix 5.4A , sheet: "2022 SpaceFuncData-Input"] | Peak Hot Water Usage (gal/hr) | Peak Hot Water Usage (gal/min)
Dining | Gas | 1250 | 41.25 | 0.116 | 4.785 | 0.07975 |  | 9
Kitchen | Gas | 1250 | 3.75 |  | 54 | 0.9
Water Heater Capacity, Tank Capacity, and Tank Loss*
WH Type | Peak Hot Water Usage (gal/hr) | Heat Output (Btu/hr) | WH Capacity (Btu/hr) | Required Energy Input (Btu/hr) | Storage Volume (gal) | Standby Loss |  | Off/On Cycle Loss Coefficient to Ambient Temperature (Btu/h-F) | Source
Gas Storage WH | 125 | 82877 | 49726.2 | 62157.75 | 50 | 855.5146 | Btu/hr | 12.7689 | Standby loss equation: Title 20, §1605.1 Table F-4 WH capacity equation: ACM, 2025, 5.9.2: Rated capacity section)
*Path 2 for calculation of WH capacity and tank loss and off/on cycle loss (Occupancy based)
Design supply temperature (F) | 135 | Ref: T24 2022 - Appendix 5.4B
Cold Water supply temperature (F) | 55 | Ref: ACM, 2025, 5.9.2: Rated capacity section
WH system factor | 0.6 | Ref: ACM, 2025, 5.9.2: Rated capacity section
Reheat multiplier | 0.4 | Ref: ACM, 2025, 5.9.2: Rated capacity section
* The 0.40 multiplier is a storage sizing factor used to account for the fact that the water heater doesn't need to store the full peak hour demand—it can reheat water during that time. This factor assumes that the heater will recover part of the hot water used during the peak hour, so only 40% of the peak hour demand needs to be stored at any given moment.
Path 1 for calculation of WH capacity and tank loss and off/on cycle loss (Fixture based)
Water Heater Capacity, Tank Capacity, and Tank Loss
Fixture | Tank Recovery Rate (gal/h) | Fixture Count | Storage Heater Min Recovery Rate (gal/hr) | Source
Room sinks | 5 | 1 | 5 | Design Guide: Advanced Water Heating for Foodservice (2022) , Table 6 and 7: Small Quick Restaurant Kitchen
Hand sinks | 5 | 1 | 5
3-Compartment sinks | 42 | 1 | 42
Mop sink | 15 | 1 | 15
Utility or pre-soak sinks | 5
Minimum Recovery Rate (gal/h) |  |  | 54 | Design Guide: Advanced Water Heating for Foodservice, 2022, Table 8] *Minimum recovery rate discount factor of 20% for using single service utensils.
Minimum Input Rate (Btu/h) |  |  | 76000 |  | https://caenergywise.com/design-guides/Advanced-Water-Heating-Design-Guide.pdf
Standby Loss (Btu/hr) |  |  | 903.3316 | Title 20, §1605.1 Table F-4 (Standby loss equation: )
Off/On Cycle Loss Coefficient to Ambient Temperature (Btu/h-F) |  |  | 13.4826
**For Gas Water Heater: UA(Btu/h-°F)​=Q˙​SL​ (Btu/h)/ΔT (∘F)​
Ambient temp | 68
Delta T | 67
** For Electric Water Heater: UA(Btu/h-°F)​= 0.0834 *SL​ (%/hr)*V gal
Background Data [To be deleted prior to publication]
https://caenergywise.com/design-guides/Advanced-Water-Heating-Design-Guide.pdf

## Interior Lights
Interior Lighting - RestaurantFastFood
Space Type | New Construction |  |  | Existing
| LPD (W/ft²) | Additional LPD for Portable Lighting (W/ft²) | Source | LPD (W/ft²) | Additional LPD for Portable Lighting (W/ft²) | Source
Dining Area (Cafeteria/Fast Food) | 0.45 | 0.25 (decorative/Display) | T24, 2025, Table 140.6-C (Area category method) | 1 | 0.5 (Ornamental) | T24, 2016, Table 140.6-C (Area category method) LPD of "All other spaces" is considered for storage space
Kitchen/Food Preparation Area | 0.95 |  |  | 1.2
Attic
Background Data [To be deleted prior to publication]
|  |  | Dining Area (Cafeteria/Fast Food) | 0.4 | 0.3 (Ornamental) | T24, 2019, Table 140.6-C (Area category method) LPD of "All other spaces" is considered for storage space | *ComStock
|  |  | Kitchen/Food Preparation Area | 0.95
#REF!
Background Data [To be deleted prior to publication]
Existing | Whole Building | All other building | 0.4 |  | T24, 2019, Table 140.6 B
| Area Category | 0 | 0.65 |  | T24, 2019, Table 140.6-C
|  | 0 | 0.4
|  | 0 | 0.4
Existing | Whole Building | All other building | 0.5 |  | T24, 2016, Table 140.6 B
| Area Category | ZONE1 OFFICE | 0.75 |  | T24, 2016, Table 140.6-C
|  | ZONE2 FINE STORAGE | 0.5
|  | ZONE3 BULK STORAGE | 0.5
Existing | Whole Building | All other building | 0.6 |  | T24, 2013, Table 140.6 B
| Area Category | ZONE1 OFFICE | 0.75 |  | T24, 2013, Table 140.6-C
|  | ZONE2 FINE STORAGE | 0.6
|  | ZONE3 BULK STORAGE | 0.6
Note on D34: Yousefi, Fatemeh: All other
Note on D35: Yousefi, Fatemeh: All other
Note on D37: Yousefi, Fatemeh: All other
Note on D39: Yousefi, Fatemeh: All other
Note on D40: Yousefi, Fatemeh: All other
Note on D42: Yousefi, Fatemeh: All other
Note on D44: Yousefi, Fatemeh: All other
Note on D45: Yousefi, Fatemeh: All other

## Ext Lighting
Exterior Lighting - RestaurantFastFood
Motion Controlled Luminaires (W) | Non-motion Controlled Luminaires (W) | Total (W) | Source
351 | 116.75 | 467.75 | T24, 2022
Exterior Lighting
Items (Assume LZ2) | Assumptions [2019 Outdoor Lighting CASE Report & PNNL 90.1-2010 TSD] |  | Unit | Lighting Power Allowance [T24, 2025, Table 140.7-A & 140.7-B] | Unit | Exterior Lighting Power (W)
IWA (Initial Wattage Allowance) |  |  |  | 200 | (W) | 200
Parking area | 400 ft² for every parking space 1 parking space per 250 ft² of gross building area | 4000 | (ft²) | 0.019 | (W/ft²) | 76
Building Entrance | 2 building entrance (1 per 10,000 ft² footprint) | 1 | (count) | 15 | (W/ea) | 15
Hardscape Ornamental Light | 0.1 ft² per 1 ft² of gross building area for hardscape ornamental light | 250 | (ft²) | 0.007 | (W/ft²) | 1.75
Building façade | 0.1 W per 1 ft² of facade area Façade Area = Perimeter × 0.5 × 10 ft (10 ft is the building height ) * The 0.5 factor assumes that only half of the perimeter walls are lit. -Formula ia developed based on the 2019 Outdoor Lighting CASE report | 1000 | (ft²) | 0.1 | (W/ft²) | 100
Drive up windows | 1 per 1500 ft² of gross building area | 2 | (count) | 30 | (W/ea) | 60
Outdoor dining | 1 ft² per 5 ft² of gross building area | 500 | (ft²) | 0.03 | (W/ft²) | 15
Motion controlled Luminaires | [5 empty] | 351
Non-motion-controlled Luminaires | [5 empty] | 116.75
TOTAL | [5 empty] | 467.75
Perimeter (ft) | 200
Total floor area (ft²) | 2500
Floors | 1
Height (ft) | 10
Background Data [To be deleted prior to publication]
T24, part6, 2025, 130.2(c)3
Title 24, 2025

## Equipment
Equipment - RestaurantFastFood
Space Type | Plug Load Power Density (W/ft²) | ReachIn Refrigerator and ReachInFreezer Power (W) - 24/7 | Refrigerator Power Density (W/ft²) | Gas Power Density (Btu/hr-ft²) | Source
Dining Area (Cafeteria/Fast Food) | 0.5 |  | 0.25 |  | Others inputs: T24 2025 - Appendix 5.4A: "2022 SpaceFuncData-Input"
Kitchen/Food Preparation Area | 1.5 | 590 | 1.12 | 35.08 | - ReachIn Refrigerator and ReachInFreezer load : [PNNL ASHRAE 90.1 2022 Fast Food prototype] - Other inputs: T24 2025 - Appendix 5.4A: "2022 SpaceFuncData-Input" Plug load density is confirmed by the findings Plug load and schedules project with CEC, 2025
Attic
*ReachIn Refrigerator and ReachInFreezer Power is based on PNNL model. It doesn’t exist in the CEC prototype model.
* Gas load is very low compared to PNNL model (237.4 Btu/hr-ft2 for Kitchen)
Refrigerator load will be simulated as equipment load
Background Data [To be deleted prior to publication]
Existing Dataset | FullServiceRestaurant | QuickServiceRestaurant
ComStock (electricity intensity per sf) | 0.8 | 2.7
Existing prototypes |  | PNNL (Fast Food) | CEC (Small Restaurant) | CPUC (Fast Food)
Model input | Electric Equipment (W/ft² ) | Dining: 10.3 receptacle | Dining: 0.5 receptacle & 0.25 refrigerator | Dining: 0.5 & 0.25
|  | Kitchen: 23.8 receptacle & 0.5 ReachInRerigerator and ReachInFreezer (always ON) | Kitchen: 1.5 receptacle & 1.12 refrigerator | Kitchen: 1.5 & 1.12
Lobby: 0.5
| Refrigerator Cases input power (W/ft²) | 1.2524
| Refrigerator (object) | 2 Case refrigerator : 716 and 763 Btu/hr-ft for 8 and 10 ft cases (always ON) | Two refrigerator loads is defined as electric equipment load for dining and kitchen | follow the CEC approach and simulated the refrigerator loads as electric equipment load
2.5 COP for design compressor rack
1126 Btu/h for fan power of design compressor (for each of the two racks)
HTML output | Total electricity of interior equipment (kWh) | 66527.544 | 26161.1704 | 18425.04
| Refrigeration load (kWh) | 10823.088
3 times greater than CEC
| Schedules | Always 1 | Always 0.9 | Always 1
| EER | 11
Gas Equipment (Btu/h-ft2) |  | 237.4 Kitchen (296,748 Btu/h) | 32.4 Kitchen | 17.5 Kitchen
Note on C27: Yousefi, Fatemeh: (313+277)/1250
Note on C28: Yousefi, Fatemeh: COP 2.5 1W=3.413 Btu/h Kitchen area= 1250 ft2
Note on C29: Yousefi, Fatemeh: 2 Case refrigerator : 716 and 763 Btu/hr-ft for 8 and 10 ft cases (always ON) 2.5 COP for design compressor rack 1126 Btu/h for fan power of design compressor
Note on C31: Yousefi, Fatemeh:
Note on C32: Yousefi, Fatemeh: 220.85 GJ Cooking equipment load 8.75 GJ ReachInFreezer equipment load 9.88 GJ ReachInRefrigerator equipment load 7.94 GJ General load of Refrigeration load 12.08 GJ LowTempRefrigeration load 18.94 GJ MedTempRefrigeration load
Note on C33: Yousefi, Fatemeh: 7.94 GJ General load of Refrigeration load 12.08 GJ LowTempRefrigeration load 18.94 GJ MedTempRefrigeration load

## Occupnacy
HVAC Operating Hour
Period | Hour | Weekdays Multiplier |  | Saturday | Sunday
12:00 am - 6:00 am | 6 |  | 0
6:00 am -7:00 am | 1 | 20% capcaity | 0.2
7:00 am - 8:00 am | 1 | 70% Capacity | 0.7
8:00 am - 17:00 pm | 9 | Full capacity | 1
17:00 pm - 18:00 pm | 1 | 70% Capacity | 0.7
18:00 pm - 19:00 pm | 1 | 50% capacity | 0.5
19:00 pm - 20:00 pm | 1 | 20% capcaity | 0.3
20:00 pm - 22:00 pm | 2 | 20% capcaity | 0.2
22:00 pm - 12:00 am | 2 |  | 0
|  |  | 11.8 | 3.0267 | 0
Background Data [To be deleted prior to publication]
CEUS 2022 data
Total Weighted Average Annual Operating Hours |  |  | Office, Small | 3286.2707 |  | Working day | 249
Weighted Average Operating Hours Per Day |  |  | Office, Small | 9.0035
Weighted average operating hours per working day (assuming zeo load for weekends) |  |  | Office, Small | 13.1979
Operating Hours Per Day (in 4-hrs bin) By Planning Area & Forecast Zone
Calculation Method | Statewide/ Utility/ FCZ | Building Type | 0< X <=4 | 4< X <=8 | 8< X <=12 | 12< X <=16 | 16< X <=20 | 20<= X <24 | 24 Hrs/Day | Not Available | Total | ← Operating Hours Per Day
Floorspace-Based | Statewide | Office, Small | 0.922% | 37.04% | 52.76% | 5.01% | 1.177% | 0.5665% | 0.6799% | 1.841% | 100%
Annual Operating Hours By Planning Area & Forecast Zone
Calculation Method | Statewide/ Utility/ FCZ | Building Type | <=500 Hrs | 500 < Hrs <=1000 | 1000 < Hrs <=1500 | 1500 < Hrs <=2000 | 2000 < Hrs <=2500 | 2500 < Hrs <=3000 | 3000 < Hrs <=3500 | 3500 < Hrs <=4000 | 4000 < Hrs <=4500 | 4500 < Hrs <=5000 | 5000 < Hrs <=5500 | 5500 < Hrs <=6000 | 6500 < Hrs <=7000 | 7000 < Hrs <=7000 | 7500 < Hrs <=8000 | 8000< Hrs <=8500 | 8001 < Hrs <=8500 | 8500 < Hrs <8760 | 8760 Hours | Total | ← Annual Operating Hours
Floorspace-Based | Statewide | Office, Small | 0.06265% | 0.3069% | 1.574% | 7.177% | 53.64% | 19.27% | 8.738% | 2.484% | 1.993% | 0.6334% | 0.5853% | 0.5399% | 0.2139% | 0.2596% | 0.005075% | 0% | 0.03735% | 0.3457% | 2.132% | 100%
Occupnacy Schedules (existing prototypes extracted from the idf files (presented below)
| PNNL |  |  | DEER |  |  |  |  | CEC
Hour | m2/person | 18.5806 |  |  | Person/m2: 0.0538195521 | 18.5874 |  |  | Person/m2 :0.0538195521 |  | 18.5806
| PNNL (Core+ 3 Perimeter) | PNNL( 1 Perimeter) |  | DEER Normal day | DEER Saturday | DEER (Other day) |  |  | CEC Weekday | CEC Saturday | CEC Sunday
1 | 0 | 0 |  | 0 | 0 | 0 |  |  | 0 | 0 | 0
2 | 0 | 0 |  | 0 | 0 | 0 |  |  | 0 | 0 | 0
3 | 0 | 0 |  | 0 | 0 | 0 |  |  | 0 | 0 | 0
4 | 0 | 0 |  | 0 | 0 | 0 |  |  | 0 | 0 | 0
5 | 0 | 0 |  | 0 | 0 | 0 |  |  | 0 | 0 | 0
6 | 0 | 0 |  | 0 | 0 | 0 |  |  | 0 | 0 | 0
7 | 0.11 | 0.11 |  | 0.1 | 0.1 | 0.05 |  |  | 0.1 | 0.1 | 0.05
8 | 0.21 | 0.21 |  | 0.2 | 0.1 | 0.05 |  |  | 0.2 | 0.1 | 0.05
9 | 1 | 1 |  | 0.95 | 0.3 | 0.05 |  |  | 0.95 | 0.3 | 0.05
10 | 1 | 1 |  | 0.95 | 0.3 | 0.05 |  |  | 0.95 | 0.3 | 0.05
11 | 1 | 0 |  | 0.95 | 0.3 | 0.05 |  |  | 0.95 | 0.3 | 0.05
12 | 1 | 1 |  | 0.95 | 0.3 | 0.05 |  |  | 0.95 | 0.3 | 0.05
13 | 1 | 0 |  | 0.5 | 0.1 | 0.05 |  |  | 0.5 | 0.1 | 0.05
14 | 0.61 | 1 |  | 0.95 | 0.1 | 0.05 |  |  | 0.95 | 0.1 | 0.05
15 | 1 | 0 |  | 0.95 | 0.1 | 0.05 |  |  | 0.95 | 0.1 | 0.05
16 | 1 | 1 |  | 0.95 | 0.1 | 0.05 |  |  | 0.95 | 0.1 | 0.05
17 | 1 | 1 |  | 0.95 | 0.1 | 0.05 |  |  | 0.95 | 0.1 | 0.05
18 | 1 | 0.32 |  | 0.3 | 0.05 | 0.05 |  |  | 0.3 | 0.05 | 0.05
19 | 0.32 | 0.11 |  | 0.1 | 0.05 | 0 |  |  | 0.1 | 0.05 | 0
20 | 0.11 | 0.11 |  | 0.1 | 0 | 0 |  |  | 0.1 | 0 | 0
21 | 0.11 | 0.11 |  | 0.1 | 0 | 0 |  |  | 0.1 | 0 | 0
22 | 0.11 | 0.11 |  | 0.1 | 0 | 0 |  |  | 0.1 | 0 | 0
23 | 0.05 | 0.05 |  | 0.05 | 0 | 0 |  |  | 0.05 | 0 | 0
24 | 0 | 0 |  | 0.05 | 0 | 0 |  |  | 0 | 0 | 0
| 10.63 | 7.13 |  | 9.2 | 2 | 0.6 |  |  | 9.15 | 2 | 0.6
| 10 h entirely occupied | 17 |  | 9 h entirely occupied | 13 | 9 h entirely occupied
DEER 2024 (Old model rebuilt in E+)
DEERSmall Office idf: 07-2024
| Schedule:Compact, |  |  | Schedule:Compact, | [5 empty] | Schedule:Compact, | [5 empty] | Schedule:Compact, | [5 empty] | Schedule:Compact, |  | Schedule:Compact, | Schedule:Compact, | Schedule:Compact, | Schedule:Compact, | Schedule:Compact,
| Hall EL1 Core Spc (G.C5) Occupant Sch, !- Name |  |  | OfficeSmall EL1 North Perim Spc (G.N3) Occupant Sch, !- Name | [5 empty] | OfficeSmall EL1 East Perim Spc (G.E2) Occupant Sch, !- Name | [5 empty] | OfficeSmall EL1 South Perim Spc (G.S1) Occupant Sch, !- Name | [5 empty] | OfficeSmall EL1 West Perim Spc (G.W4) Occupant Sch, !- Name |  | Hall EL1 Core Spc (T.C15) Occupant Sch, !- Name | OfficeSmall EL1 East Perim Spc (T.E12) Occupant Sch, !- Name | OfficeSmall EL1 North Perim Spc (T.N13) Occupant Sch, !- Name | OfficeSmall EL1 South Perim Spc (T.S11) Occupant Sch, !- Name | OfficeSmall EL1 West Perim Spc (T.W14) Occupant Sch, !- Name
| Unit Interval, !- Schedule Type Limits Name |  |  | Unit Interval, !- Schedule Type Limits Name | [5 empty] | Unit Interval, !- Schedule Type Limits Name | [5 empty] | Unit Interval, !- Schedule Type Limits Name | [5 empty] | Unit Interval, !- Schedule Type Limits Name |  | Unit Interval, !- Schedule Type Limits Name | Unit Interval, !- Schedule Type Limits Name | Unit Interval, !- Schedule Type Limits Name | Unit Interval, !- Schedule Type Limits Name | Unit Interval, !- Schedule Type Limits Name
| Through: 12/31, !- Field 1 |  |  | Through: 12/31, !- Field 1 | [5 empty] | Through: 12/31, !- Field 1 | [5 empty] | Through: 12/31, !- Field 1 | [5 empty] | Through: 12/31, !- Field 1 |  | Through: 12/31, !- Field 1 | Through: 12/31, !- Field 1 | Through: 12/31, !- Field 1 | Through: 12/31, !- Field 1 | Through: 12/31, !- Field 1
| For: SummerDesignDay, !- Field 2 |  |  | For: SummerDesignDay, !- Field 2 | [5 empty] | For: SummerDesignDay, !- Field 2 | [5 empty] | For: SummerDesignDay, !- Field 2 | [5 empty] | For: SummerDesignDay, !- Field 2 |  | For: SummerDesignDay, !- Field 2 | For: SummerDesignDay, !- Field 2 | For: SummerDesignDay, !- Field 2 | For: SummerDesignDay, !- Field 2 | For: SummerDesignDay, !- Field 2
| Until: 24:00,1.0, !- Field 3 |  |  | Until: 24:00,1.0, !- Field 3 | [5 empty] | Until: 24:00,1.0, !- Field 3 |  |  | 0 | 0 |  | Until: 24:00,1.0, !- Field 3 | [5 empty] | Until: 24:00,1.0, !- Field 3 |  | Until: 24:00,1.0, !- Field 3 | Until: 24:00,1.0, !- Field 3 | Until: 24:00,1.0, !- Field 3 | Until: 24:00,1.0, !- Field 3 | Until: 24:00,1.0, !- Field 3
| For: WinterDesignDay, !- Field 5 |  |  | For: WinterDesignDay, !- Field 5 | [5 empty] | For: WinterDesignDay, !- Field 5 |  |  | 0 | 0 |  | For: WinterDesignDay, !- Field 5 | [5 empty] | For: WinterDesignDay, !- Field 5 |  | For: WinterDesignDay, !- Field 5 | For: WinterDesignDay, !- Field 5 | For: WinterDesignDay, !- Field 5 | For: WinterDesignDay, !- Field 5 | For: WinterDesignDay, !- Field 5
| Until: 24:00,0.0, !- Field 6 |  |  | Until: 24:00,0.0, !- Field 6 | [5 empty] | Until: 24:00,0.0, !- Field 6 |  |  | 0 | 0 |  | Until: 24:00,0.0, !- Field 6 | [5 empty] | Until: 24:00,0.0, !- Field 6 |  | Until: 24:00,0.0, !- Field 6 | Until: 24:00,0.0, !- Field 6 | Until: 24:00,0.0, !- Field 6 | Until: 24:00,0.0, !- Field 6 | Until: 24:00,0.0, !- Field 6
| For: Weekdays, !- Field 8 |  |  | For: Weekdays, !- Field 8 | [5 empty] | For: Weekdays, !- Field 8 |  |  | 0 | 0 |  | For: Weekdays, !- Field 8 | [5 empty] | For: Weekdays, !- Field 8 |  | For: Weekdays, !- Field 8 | For: Weekdays, !- Field 8 | For: Weekdays, !- Field 8 | For: Weekdays, !- Field 8 | For: Weekdays, !- Field 8
| Until: 06:00,0.0, !- Field 9 |  |  | Until: 06:00,0.0, !- Field 9 | [5 empty] | Until: 06:00,0.0, !- Field 9 |  |  | 0 | 0 |  | Until: 06:00,0.0, !- Field 9 | [5 empty] | Until: 06:00,0.0, !- Field 9 |  | Until: 06:00,0.0, !- Field 9 | Until: 06:00,0.0, !- Field 9 | Until: 06:00,0.0, !- Field 9 | Until: 06:00,0.0, !- Field 9 | Until: 06:00,0.0, !- Field 9
| Until: 07:00,0.10, !- Field 11 |  |  | Until: 07:00,0.10, !- Field 11 | [5 empty] | Until: 07:00,0.10, !- Field 11 |  |  | 0 | 0 |  | Until: 07:00,0.10, !- Field 11 | [5 empty] | Until: 07:00,0.10, !- Field 11 |  | Until: 07:00,0.10, !- Field 11 | Until: 07:00,0.10, !- Field 11 | Until: 07:00,0.10, !- Field 11 | Until: 07:00,0.10, !- Field 11 | Until: 07:00,0.10, !- Field 11
| Until: 08:00,0.20, !- Field 13 |  |  | Until: 08:00,0.20, !- Field 13 | [5 empty] | Until: 08:00,0.20, !- Field 13 |  |  | 0.1 | 0.1 |  | Until: 08:00,0.20, !- Field 13 | [5 empty] | Until: 08:00,0.20, !- Field 13 |  | Until: 08:00,0.20, !- Field 13 | Until: 08:00,0.20, !- Field 13 | Until: 08:00,0.20, !- Field 13 | Until: 08:00,0.20, !- Field 13 | Until: 08:00,0.20, !- Field 13
| Until: 12:00,0.95, !- Field 15 |  |  | Until: 12:00,0.95, !- Field 15 | [5 empty] | Until: 12:00,0.95, !- Field 15 |  |  | 0.2 | 0.1 |  | Until: 12:00,0.95, !- Field 15 | [5 empty] | Until: 12:00,0.95, !- Field 15 |  | Until: 12:00,0.95, !- Field 15 | Until: 12:00,0.95, !- Field 15 | Until: 12:00,0.95, !- Field 15 | Until: 12:00,0.95, !- Field 15 | Until: 12:00,0.95, !- Field 15
| Until: 13:00,0.50, !- Field 17 |  |  | Until: 13:00,0.50, !- Field 17 | [5 empty] | Until: 13:00,0.50, !- Field 17 |  |  | 0.95 | 0.3 |  | Until: 13:00,0.50, !- Field 17 | [5 empty] | Until: 13:00,0.50, !- Field 17 |  | Until: 13:00,0.50, !- Field 17 | Until: 13:00,0.50, !- Field 17 | Until: 13:00,0.50, !- Field 17 | Until: 13:00,0.50, !- Field 17 | Until: 13:00,0.50, !- Field 17
| Until: 17:00,0.95, !- Field 19 |  |  | Until: 17:00,0.95, !- Field 19 | [5 empty] | Until: 17:00,0.95, !- Field 19 |  |  | 0.95 | 0.3 |  | Until: 17:00,0.95, !- Field 19 | [5 empty] | Until: 17:00,0.95, !- Field 19 |  | Until: 17:00,0.95, !- Field 19 | Until: 17:00,0.95, !- Field 19 | Until: 17:00,0.95, !- Field 19 | Until: 17:00,0.95, !- Field 19 | Until: 17:00,0.95, !- Field 19
| Until: 18:00,0.30, !- Field 21 |  |  | Until: 18:00,0.30, !- Field 21 | [5 empty] | Until: 18:00,0.30, !- Field 21 |  |  | 0.95 | 0.3 |  | Until: 18:00,0.30, !- Field 21 | [5 empty] | Until: 18:00,0.30, !- Field 21 |  | Until: 18:00,0.30, !- Field 21 | Until: 18:00,0.30, !- Field 21 | Until: 18:00,0.30, !- Field 21 | Until: 18:00,0.30, !- Field 21 | Until: 18:00,0.30, !- Field 21
| Until: 22:00,0.10, !- Field 23 |  |  | Until: 22:00,0.10, !- Field 23 | [5 empty] | Until: 22:00,0.10, !- Field 23 |  |  | 0.95 | 0.3 |  | Until: 22:00,0.10, !- Field 23 | [5 empty] | Until: 22:00,0.10, !- Field 23 |  | Until: 22:00,0.10, !- Field 23 | Until: 22:00,0.10, !- Field 23 | Until: 22:00,0.10, !- Field 23 | Until: 22:00,0.10, !- Field 23 | Until: 22:00,0.10, !- Field 23
| Until: 24:00,0.05, !- Field 25 |  |  | Until: 24:00,0.05, !- Field 25 | [5 empty] | Until: 24:00,0.05, !- Field 25 |  |  | 0.5 | 0.1 |  | Until: 24:00,0.05, !- Field 25 | [5 empty] | Until: 24:00,0.05, !- Field 25 |  | Until: 24:00,0.05, !- Field 25 | Until: 24:00,0.05, !- Field 25 | Until: 24:00,0.05, !- Field 25 | Until: 24:00,0.05, !- Field 25 | Until: 24:00,0.05, !- Field 25
| For: Saturday, !- Field 27 |  |  | For: Saturday, !- Field 27 | [5 empty] | For: Saturday, !- Field 27 |  |  | 0.95 | 0.1 |  | For: Saturday, !- Field 27 | [5 empty] | For: Saturday, !- Field 27 |  | For: Saturday, !- Field 27 | For: Saturday, !- Field 27 | For: Saturday, !- Field 27 | For: Saturday, !- Field 27 | For: Saturday, !- Field 27
| Until: 06:00,0.0, !- Field 28 |  |  | Until: 06:00,0.0, !- Field 28 | [5 empty] | Until: 06:00,0.0, !- Field 28 |  |  | 0.95 | 0.1 |  | Until: 06:00,0.0, !- Field 28 | [5 empty] | Until: 06:00,0.0, !- Field 28 |  | Until: 06:00,0.0, !- Field 28 | Until: 06:00,0.0, !- Field 28 | Until: 06:00,0.0, !- Field 28 | Until: 06:00,0.0, !- Field 28 | Until: 06:00,0.0, !- Field 28
| Until: 08:00,0.10, !- Field 30 |  |  | Until: 08:00,0.10, !- Field 30 | [5 empty] | Until: 08:00,0.10, !- Field 30 |  |  | 0.95 | 0.1 |  | Until: 08:00,0.10, !- Field 30 | [5 empty] | Until: 08:00,0.10, !- Field 30 |  | Until: 08:00,0.10, !- Field 30 | Until: 08:00,0.10, !- Field 30 | Until: 08:00,0.10, !- Field 30 | Until: 08:00,0.10, !- Field 30 | Until: 08:00,0.10, !- Field 30
| Until: 12:00,0.30, !- Field 32 |  |  | Until: 12:00,0.30, !- Field 32 | [5 empty] | Until: 12:00,0.30, !- Field 32 |  |  | 0.95 | 0.1 |  | Until: 12:00,0.30, !- Field 32 | [5 empty] | Until: 12:00,0.30, !- Field 32 |  | Until: 12:00,0.30, !- Field 32 | Until: 12:00,0.30, !- Field 32 | Until: 12:00,0.30, !- Field 32 | Until: 12:00,0.30, !- Field 32 | Until: 12:00,0.30, !- Field 32
| Until: 17:00,0.10, !- Field 34 |  |  | Until: 17:00,0.10, !- Field 34 | [5 empty] | Until: 17:00,0.10, !- Field 34 |  |  | 0.3 | 0.5 |  | Until: 17:00,0.10, !- Field 34 | [5 empty] | Until: 17:00,0.10, !- Field 34 |  | Until: 17:00,0.10, !- Field 34 | Until: 17:00,0.10, !- Field 34 | Until: 17:00,0.10, !- Field 34 | Until: 17:00,0.10, !- Field 34 | Until: 17:00,0.10, !- Field 34
| Until: 19:00,0.05, !- Field 36 |  |  | Until: 19:00,0.05, !- Field 36 | [5 empty] | Until: 19:00,0.05, !- Field 36 |  |  | 0.1 | 0.5 |  | Until: 19:00,0.05, !- Field 36 | [5 empty] | Until: 19:00,0.05, !- Field 36 |  | Until: 19:00,0.05, !- Field 36 | Until: 19:00,0.05, !- Field 36 | Until: 19:00,0.05, !- Field 36 | Until: 19:00,0.05, !- Field 36 | Until: 19:00,0.05, !- Field 36
| Until: 24:00,0.0, !- Field 38 |  |  | Until: 24:00,0.0, !- Field 38 | [5 empty] | Until: 24:00,0.0, !- Field 38 |  |  | 0.1 | 0 |  | Until: 24:00,0.0, !- Field 38 | [5 empty] | Until: 24:00,0.0, !- Field 38 |  | Until: 24:00,0.0, !- Field 38 | Until: 24:00,0.0, !- Field 38 | Until: 24:00,0.0, !- Field 38 | Until: 24:00,0.0, !- Field 38 | Until: 24:00,0.0, !- Field 38
| For: AllOtherDays, !- Field 40 |  |  | For: AllOtherDays, !- Field 40 | [5 empty] | For: AllOtherDays, !- Field 40 |  |  | 0.1 | 0 |  | For: AllOtherDays, !- Field 40 | [5 empty] | For: AllOtherDays, !- Field 40 |  | For: AllOtherDays, !- Field 40 | For: AllOtherDays, !- Field 40 | For: AllOtherDays, !- Field 40 | For: AllOtherDays, !- Field 40 | For: AllOtherDays, !- Field 40
| Until: 06:00,0.0, !- Field 41 |  |  | Until: 06:00,0.0, !- Field 41 | [5 empty] | Until: 06:00,0.0, !- Field 41 |  |  | 0.1 | 0 |  | Until: 06:00,0.0, !- Field 41 | [5 empty] | Until: 06:00,0.0, !- Field 41 |  | Until: 06:00,0.0, !- Field 41 | Until: 06:00,0.0, !- Field 41 | Until: 06:00,0.0, !- Field 41 | Until: 06:00,0.0, !- Field 41 | Until: 06:00,0.0, !- Field 41
| Until: 18:00,0.05, !- Field 43 |  |  | Until: 18:00,0.05, !- Field 43 | [5 empty] | Until: 18:00,0.05, !- Field 43 |  |  | 0.05 | 0 |  | Until: 18:00,0.05, !- Field 43 | [5 empty] | Until: 18:00,0.05, !- Field 43 |  | Until: 18:00,0.05, !- Field 43 | Until: 18:00,0.05, !- Field 43 | Until: 18:00,0.05, !- Field 43 | Until: 18:00,0.05, !- Field 43 | Until: 18:00,0.05, !- Field 43
| Until: 24:00,0.0; !- Field 45 |  |  | Until: 24:00,0.0; !- Field 45 | [5 empty] | Until: 24:00,0.0; !- Field 45 |  |  | 0.05 | 0 |  | Until: 24:00,0.0; !- Field 45 | [5 empty] | Until: 24:00,0.0; !- Field 45 |  | Until: 24:00,0.0; !- Field 45 | Until: 24:00,0.0; !- Field 45 | Until: 24:00,0.0; !- Field 45 | Until: 24:00,0.0; !- Field 45 | Until: 24:00,0.0; !- Field 45
PNNL 2022
| PNNL Small Office |  |  | Schedule:Compact, |  | For only 1 perimeter zone
| Schedule:Compact, |  |  | BLDG_OCC_SCH_w_SB, !- Name
| BLDG_OCC_SCH_wo_SB, !- Name |  |  | Fraction, !- Schedule Type Limits Name
| Fraction, !- Schedule Type Limits Name |  |  | Through: 12/31, !- Field 1
| Through: 12/31, !- Field 1 |  |  | For: Weekdays, !- Field 2
| For: Weekdays, !- Field 2 |  |  | Until: 01:00,0, !- Field 3
| Until: 01:00,0, !- Field 3 |  |  | Until: 02:00,0, !- Field 5
| Until: 02:00,0, !- Field 5 |  |  | Until: 03:00,0, !- Field 7
| Until: 03:00,0, !- Field 7 |  |  | Until: 04:00,0, !- Field 9
| Until: 04:00,0, !- Field 9 |  |  | Until: 05:00,0, !- Field 11
| Until: 05:00,0, !- Field 11 |  |  | Until: 06:00,0, !- Field 13
| Until: 06:00,0, !- Field 13 |  |  | Until: 07:00,0.11, !- Field 15
| Until: 07:00,0.11, !- Field 15 |  |  | Until: 08:00,0.21, !- Field 17
| Until: 08:00,0.21, !- Field 17 |  |  | Until: 09:00,1, !- Field 19
| Until: 09:00,1, !- Field 19 |  |  | Until: 10:00,1, !- Field 21
| Until: 10:00,1, !- Field 21 |  |  | Until: 11:00,0, !- Field 23
| Until: 11:00,1, !- Field 23 |  |  | Until: 12:00,1, !- Field 25
| Until: 12:00,1, !- Field 25 |  |  | Until: 13:00,0, !- Field 27
| Until: 13:00,0.610394505402463, !- Field 27 |  |  | Until: 14:00,1, !- Field 29
| Until: 14:00,1, !- Field 29 |  |  | Until: 15:00,0, !- Field 31
| Until: 15:00,1, !- Field 31 |  |  | Until: 16:00,1, !- Field 33
| Until: 16:00,1, !- Field 33 |  |  | Until: 17:00,1, !- Field 35
| Until: 17:00,1, !- Field 35 |  |  | Until: 18:00,0.32, !- Field 37
| Until: 18:00,0.32, !- Field 37 |  |  | Until: 19:00,0.11, !- Field 39
| Until: 19:00,0.11, !- Field 39 |  |  | Until: 20:00,0.11, !- Field 41
| Until: 20:00,0.11, !- Field 41 |  |  | Until: 21:00,0.11, !- Field 43
| Until: 21:00,0.11, !- Field 43 |  |  | Until: 22:00,0.11, !- Field 45
| Until: 22:00,0.11, !- Field 45 |  |  | Until: 23:00,0.05, !- Field 47
| Until: 23:00,0.05, !- Field 47 |  |  | Until: 24:00,0, !- Field 49
| Until: 24:00,0, !- Field 49 |  |  | For: Weekends, !- Field 51
| For: Weekends, !- Field 51 |  |  | Until: 01:00,0, !- Field 52
| Until: 01:00,0, !- Field 52 |  |  | Until: 02:00,0, !- Field 54
| Until: 02:00,0, !- Field 54 |  |  | Until: 03:00,0, !- Field 56
| Until: 03:00,0, !- Field 56 |  |  | Until: 04:00,0, !- Field 58
| Until: 04:00,0, !- Field 58 |  |  | Until: 05:00,0, !- Field 60
| Until: 05:00,0, !- Field 60 |  |  | Until: 06:00,0, !- Field 62
| Until: 06:00,0, !- Field 62 |  |  | Until: 07:00,0, !- Field 64
| Until: 07:00,0, !- Field 64 |  |  | Until: 08:00,0, !- Field 66
| Until: 08:00,0, !- Field 66 |  |  | Until: 09:00,0, !- Field 68
| Until: 09:00,0, !- Field 68 |  |  | Until: 10:00,0, !- Field 70
| Until: 10:00,0, !- Field 70 |  |  | Until: 11:00,0, !- Field 72
| Until: 11:00,0, !- Field 72 |  |  | Until: 12:00,0, !- Field 74
| Until: 12:00,0, !- Field 74 |  |  | Until: 13:00,0, !- Field 76
| Until: 13:00,0, !- Field 76 |  |  | Until: 14:00,0, !- Field 78
| Until: 14:00,0, !- Field 78 |  |  | Until: 15:00,0, !- Field 80
| Until: 15:00,0, !- Field 80 |  |  | Until: 16:00,0, !- Field 82
| Until: 16:00,0, !- Field 82 |  |  | Until: 17:00,0, !- Field 84
| Until: 17:00,0, !- Field 84 |  |  | Until: 18:00,0, !- Field 86
| Until: 18:00,0, !- Field 86 |  |  | Until: 19:00,0, !- Field 88
| Until: 19:00,0, !- Field 88 |  |  | Until: 20:00,0, !- Field 90
| Until: 20:00,0, !- Field 90 |  |  | Until: 21:00,0, !- Field 92
| Until: 21:00,0, !- Field 92 |  |  | Until: 22:00,0, !- Field 94 | [6 empty] | Weekday | Saturday | Sunday
| Until: 22:00,0, !- Field 94 |  |  | Until: 23:00,0, !- Field 96 | [5 empty] | Occupancy Load | 13 hours | 2 | 0.6
| Until: 23:00,0, !- Field 96 |  |  | Until: 24:00,0, !- Field 98
| Until: 24:00,0, !- Field 98 |  |  | For: Holiday, !- Field 100
| For: Holiday, !- Field 100 |  |  | Until: 24:00,0.0, !- Field 101
| Until: 24:00,0.0, !- Field 101 |  |  | For: WinterDesignDay, !- Field 103 | [8 empty] | CEUS | [7 empty] | Entirely occupied
| For: WinterDesignDay, !- Field 103 |  |  | Until: 24:00,0.0, !- Field 104 | [8 empty] | Total Weighted Average Annual Operating Hours |  |  |  | Office, Small | 3286.2707 |  | DEER | 10
| Until: 24:00,0.0, !- Field 104 |  |  | For: SummerDesignDay, !- Field 106 | [8 empty] | Weighted Average Operating Hours Per Day |  |  |  | Office, Small | 9.0035 |  | CEC | 9
| For: SummerDesignDay, !- Field 106 |  |  | Until: 24:00,1.0, !- Field 107 | [8 empty] | Weighted average operating hours per working day |  |  |  | Office, Small | 13.1979 |  | PNNL | 9
| Until: 24:00,1.0, !- Field 107 |  |  | For: CustomDay1, !- Field 109
| For: CustomDay1, !- Field 109 |  |  | Until: 24:00,0.0, !- Field 110
| Until: 24:00,0.0, !- Field 110 |  |  | For: CustomDay2, !- Field 112
| For: CustomDay2, !- Field 112 |  |  | Until: 24:00,0.0; !- Field 113
Until: 24:00,0.0; !- Field 113
CBECC 2023
CEC: CBEC 2023
| Schedule:Day:Interval, |  | Schedule:Day:Interval, |  | Schedule:Day:Interval,
| OfficeOccupancyWD, !- Name |  | OfficeOccupancySat, !- Name |  | OfficeOccupancySun, !- Name
| Fraction, !- Schedule Type Limits Name |  | Fraction, !- Schedule Type Limits Name |  | Fraction, !- Schedule Type Limits Name |  |  |  |  | CEC
| No, !- Interpolate to Timestep |  | No, !- Interpolate to Timestep |  | No, !- Interpolate to Timestep
| 01:00, !- Time 1 |  | 01:00, !- Time 1 |  | 01:00, !- Time 1 |  |  |  | 1
| 0, !- Value Until Time 1 |  | 0, !- Value Until Time 1 |  | 0, !- Value Until Time 1 |  |  |  | 2
| 02:00, !- Time 2 |  | 02:00, !- Time 2 |  | 02:00, !- Time 2 |  |  |  | 3
| 0, !- Value Until Time 2 |  | 0, !- Value Until Time 2 |  | 0, !- Value Until Time 2 |  |  |  | 4
| 03:00, !- Time 3 |  | 03:00, !- Time 3 |  | 03:00, !- Time 3 |  |  |  | 5
| 0, !- Value Until Time 3 |  | 0, !- Value Until Time 3 |  | 0, !- Value Until Time 3 |  |  |  | 6
| 04:00, !- Time 4 |  | 04:00, !- Time 4 |  | 04:00, !- Time 4 |  |  |  | 7
| 0, !- Value Until Time 4 |  | 0, !- Value Until Time 4 |  | 0, !- Value Until Time 4 |  |  |  | 8
| 05:00, !- Time 5 |  | 05:00, !- Time 5 |  | 05:00, !- Time 5 |  |  |  | 9
| 0, !- Value Until Time 5 |  | 0, !- Value Until Time 5 |  | 0, !- Value Until Time 5 |  |  |  | 10
| 06:00, !- Time 6 |  | 06:00, !- Time 6 |  | 06:00, !- Time 6 |  |  |  | 11
| 0, !- Value Until Time 6 |  | 0, !- Value Until Time 6 |  | 0, !- Value Until Time 6 |  |  |  | 12
| 07:00, !- Time 7 |  | 07:00, !- Time 7 |  | 07:00, !- Time 7 |  |  |  | 13
| 0.1, !- Value Until Time 7 |  | 0.1, !- Value Until Time 7 |  | 0.05, !- Value Until Time 7 |  |  |  | 14
| 08:00, !- Time 8 |  | 08:00, !- Time 8 |  | 08:00, !- Time 8 |  |  |  | 15
| 0.2, !- Value Until Time 8 |  | 0.1, !- Value Until Time 8 |  | 0.05, !- Value Until Time 8 |  |  |  | 16
| 09:00, !- Time 9 |  | 09:00, !- Time 9 |  | 09:00, !- Time 9 |  |  |  | 17
| 0.95, !- Value Until Time 9 |  | 0.3, !- Value Until Time 9 |  | 0.05, !- Value Until Time 9 |  |  |  | 18
| 10:00, !- Time 10 |  | 10:00, !- Time 10 |  | 10:00, !- Time 10 |  |  |  | 19
| 0.95, !- Value Until Time 10 |  | 0.3, !- Value Until Time 10 |  | 0.05, !- Value Until Time 10 |  |  |  | 20
| 11:00, !- Time 11 |  | 11:00, !- Time 11 |  | 11:00, !- Time 11 |  |  |  | 21
| 0.95, !- Value Until Time 11 |  | 0.3, !- Value Until Time 11 |  | 0.05, !- Value Until Time 11 |  |  |  | 22
| 12:00, !- Time 12 |  | 12:00, !- Time 12 |  | 12:00, !- Time 12 |  |  |  | 23
| 0.95, !- Value Until Time 12 |  | 0.3, !- Value Until Time 12 |  | 0.05, !- Value Until Time 12 |  |  |  | 24
| 13:00, !- Time 13 |  | 13:00, !- Time 13 |  | 13:00, !- Time 13
| 0.5, !- Value Until Time 13 |  | 0.1, !- Value Until Time 13 |  | 0.05, !- Value Until Time 13
| 14:00, !- Time 14 |  | 14:00, !- Time 14 |  | 14:00, !- Time 14
| 0.95, !- Value Until Time 14 |  | 0.1, !- Value Until Time 14 |  | 0.05, !- Value Until Time 14
| 15:00, !- Time 15 |  | 15:00, !- Time 15 |  | 15:00, !- Time 15
| 0.95, !- Value Until Time 15 |  | 0.1, !- Value Until Time 15 |  | 0.05, !- Value Until Time 15
| 16:00, !- Time 16 |  | 16:00, !- Time 16 |  | 16:00, !- Time 16
| 0.95, !- Value Until Time 16 |  | 0.1, !- Value Until Time 16 |  | 0.05, !- Value Until Time 16
| 17:00, !- Time 17 |  | 17:00, !- Time 17 |  | 17:00, !- Time 17
| 0.95, !- Value Until Time 17 |  | 0.1, !- Value Until Time 17 |  | 0.05, !- Value Until Time 17
| 18:00, !- Time 18 |  | 18:00, !- Time 18 |  | 18:00, !- Time 18
| 0.3, !- Value Until Time 18 |  | 0.05, !- Value Until Time 18 |  | 0.05, !- Value Until Time 18
| 19:00, !- Time 19 |  | 19:00, !- Time 19 |  | 19:00, !- Time 19
| 0.1, !- Value Until Time 19 |  | 0.05, !- Value Until Time 19 |  | 0, !- Value Until Time 19
| 20:00, !- Time 20 |  | 20:00, !- Time 20 |  | 20:00, !- Time 20
| 0.1, !- Value Until Time 20 |  | 0, !- Value Until Time 20 |  | 0, !- Value Until Time 20
| 21:00, !- Time 21 |  | 21:00, !- Time 21 |  | 21:00, !- Time 21
| 0.1, !- Value Until Time 21 |  | 0, !- Value Until Time 21 |  | 0, !- Value Until Time 21
| 22:00, !- Time 22 |  | 22:00, !- Time 22 |  | 22:00, !- Time 22
| 0.1, !- Value Until Time 22 |  | 0, !- Value Until Time 22 |  | 0, !- Value Until Time 22
| 23:00, !- Time 23 |  | 23:00, !- Time 23 |  | 23:00, !- Time 23
| 0.05, !- Value Until Time 23 |  | 0, !- Value Until Time 23 |  | 0, !- Value Until Time 23
| 24:00, !- Time 24 |  | 24:00, !- Time 24 |  | 24:00, !- Time 24
| 0.05; !- Value Until Time 24 |  | 0; !- Value Until Time 24 |  | 0; !- Value Until Time 24

## Energy Usage
CalBEM Energy Consumption - RestaurantFastFood | [7 empty] | National Average (EnergyStar Portfolio Manager) |  |  |  | CEUS Energy Consumption - Restaurant
Prototype | CZ | CalBEM Electricity EUI (KBTU/ft²) | CalBEM Gas EUI (KBTU/ft²) | CalBEM Total EUI (KBTU/ft²) | New Construction Electricity EUI (KBTU/ft²) | New Construction Gas EUI (KBTU/ft²) | New Construction Total EUI (KBTU/ft²) | National Average | Acceptable Range (25% Higher) | Acceptable Range (25% Lower) | National Average Acceptable EUI Range | Prototype | CZ | Total Floorspace (Thousand of ft²) | CEUS 2022 Electricity EUI (kBtu/ft²) | CEUS 2022 Gas EUI (kBtu/ft²) | CEUS 2022 Total EUI (kBtu/ft²) | Acceptable Range (25% Higher) | Acceptable Range (25% Lower) | CEUS 2022 Acceptable EUI Range
RetailStripMall | 1 | 96.89 | 223.5698 | 320.4599 | 95.98 | 217.32 | 313.3 | 442.6 | 553.25 | 331.95 | 221.3 | Restaurant | 1 | 2670.248 | 140.2134 | 188.3968 | 328.6101 | 410.7627 | 246.4576 | 164.3051
| 2 | 127.4806 | 201.933 | 329.4136 | 119.46 | 190.73 | 310.19 | 442.6 | 553.25 | 331.95 | 221.3 |  | 2 | 4962.8202 | 115.4344 | 178.5959 | 294.0304 | 367.5379 | 220.5228 | 147.0152
| 3 | 114.2919 | 184.8696 | 299.1615 | 107.26 | 180.12 | 287.38 | 442.6 | 553.25 | 331.95 | 221.3 |  | 3 | 23016.1888 | 121.6825 | 177.6653 | 299.3479 | 374.1848 | 224.5109 | 149.6739
| 4 | 144.9432 | 193.9012 | 338.8444 | 133.89 | 181.83 | 315.72 | 442.6 | 553.25 | 331.95 | 221.3 |  | 4 | 11906.9501 | 121.6795 | 177.2298 | 298.9093 | 373.6366 | 224.1819 | 149.4546
| 5 | 116.3807 | 185.6828 | 302.0634 | 108.91 | 180.58 | 289.49 | 442.6 | 553.25 | 331.95 | 221.3 |  | 5 | 2232.1752 | 116.8971 | 182.68 | 299.577 | 374.4713 | 224.6828 | 149.7885
| 6 | 128.0448 | 158.0237 | 286.0686 | 118.41 | 156.17 | 274.58 | 442.6 | 553.25 | 331.95 | 221.3 |  | 6 | 19264.5577 | 114.3076 | 210.8626 | 325.1702 | 406.4628 | 243.8777 | 162.5851
| 7 | 127.6711 | 156.3823 | 284.0534 | 118.54 | 154.74 | 273.28 | 442.6 | 553.25 | 331.95 | 221.3 |  | 7 | 11474.8437 | 139.927 | 228.2706 | 368.1976 | 460.247 | 276.1482 | 184.0988
| 8 | 149.2795 | 159.7172 | 308.9967 | 137.7 | 155.83 | 293.53 | 442.6 | 553.25 | 331.95 | 221.3 |  | 8 | 29165.6468 | 124.0973 | 226.014 | 350.1113 | 437.6392 | 262.5835 | 175.0557
| 9 | 149.4567 | 164.12 | 313.5767 | 136.15 | 158.31 | 294.46 | 442.6 | 553.25 | 331.95 | 221.3 |  | 9 | 44906.6072 | 111.9489 | 217.8953 | 329.8442 | 412.3052 | 247.3831 | 164.9221
| 10 | 155.1844 | 165.1399 | 320.3243 | 142.73 | 158.66 | 301.39 | 442.6 | 553.25 | 331.95 | 221.3 |  | 10 | 24025.7033 | 129.0838 | 231.9237 | 361.0075 | 451.2594 | 270.7557 | 180.5038
| 11 | 159.7522 | 194.2541 | 354.0063 | 148.15 | 182.01 | 330.16 | 442.6 | 553.25 | 331.95 | 221.3 |  | 11 | 8514.5666 | 141.1332 | 172.3969 | 313.53 | 391.9126 | 235.1475 | 156.765
| 12 | 143.3895 | 193.0884 | 336.4779 | 133.27 | 182.68 | 315.95 | 442.6 | 553.25 | 331.95 | 221.3 |  | 12 | 37639.2204 | 145.5245 | 191.7377 | 337.2622 | 421.5777 | 252.9466 | 168.6311
| 13 | 158.5892 | 185.788 | 344.3772 | 147.5 | 176.73 | 324.23 | 442.6 | 553.25 | 331.95 | 221.3 |  | 13 | 12120.1215 | 147.9323 | 194.185 | 342.1173 | 427.6467 | 256.588 | 171.0587
| 14 | 156.1908 | 194.7926 | 350.9834 | 144.92 | 183.83 | 328.75 | 442.6 | 553.25 | 331.95 | 221.3 |  | 14 | 6251.7396 | 119.7658 | 215.3254 | 335.0912 | 418.864 | 251.3184 | 167.5456
| 15 | 198.6806 | 150.7776 | 349.4582 | 183.47 | 147.28 | 330.75 | 442.6 | 553.25 | 331.95 | 221.3 |  | 15 | 12622.5049 | 139.1963 | 260.7922 | 399.9885 | 499.9857 | 299.9914 | 199.9943
| 16 | 108.7374 | 237.4289 | 346.1663 | 103.98 | 224.69 | 328.67 | 442.6 | 553.25 | 331.95 | 221.3 |  | 16 | 23693.2853 | 127.4641 | 198.8373 | 326.3014 | 407.8767 | 244.726 | 163.1507
Ref: CEUS 2022 Report
And converted FZ level data to CZ level
Restaurants have only one category in CEUS data.
Background Data [To be deleted prior to publication]
| Screenshot of assumption for the national average in the EnergyStar Portfolio Manager website | [10 empty] | EIA 2018: | U.S. Energy Information Administration - EIA - Independent Statistics and Analysis
ENERGY STAR Portfolio Manager Upgrade

## Schedules
Schedules - RestaurantFastFood
Zone | Schedule Category | Schedule | Source | Type | Hour
[5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Dining | Restaurant | Occupancy | PNNL,ASHRAE 90.1, 2022 Fast Food Restaurant prototype (It has higher occupancy rate during morning compared to T24 2022 - Appendix 5.4B) | Weekday | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.4 | 0.4 | 0.4 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.8 | 0.8 | 0.8 | 0.5 | 0.35 | 0.2
|  |  |  | Saturday | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.4 | 0.2 | 0.45 | 0.5 | 0.5 | 0.35 | 0.3 | 0.3 | 0.3 | 0.7 | 0.9 | 0.7 | 0.65 | 0.55 | 0.35
|  |  |  | Sunday | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.3 | 0.2 | 0.25 | 0.35 | 0.55 | 0.65 | 0.7 | 0.35 | 0.2 | 0.2
Dining | Restaurant | Lights | T24 2022 - Appendix 5.4B, [Restaurant] Updated based on the equipment schedule from the plug load and schedule project with CEC | Weekday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.3 | 0.67 | 0.73 | 0.75 | 0.85 | 0.85 | 0.85 | 0.83 | 0.72 | 0.65 | 0.67 | 0.75 | 0.85 | 0.85 | 0.85 | 0.75 | 0.57 | 0.3
|  |  |  | Saturday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.3 | 0.67 | 0.73 | 0.75 | 0.85 | 0.85 | 0.85 | 0.83 | 0.72 | 0.65 | 0.67 | 0.75 | 0.85 | 0.85 | 0.85 | 0.75 | 0.57 | 0.3
|  |  |  | Sunday | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.67 | 0.73 | 0.75 | 0.85 | 0.85 | 0.85 | 0.83 | 0.72 | 0.65 | 0.67 | 0.75 | 0.85 | 0.85 | 0.85 | 0.75 | 0.57 | 0.3
Dining | Restaurant | ElecEquipment | Plug load and schedules project with CEC, 2025 | Weekday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.3 | 0.72 | 0.78 | 0.8 | 0.9 | 0.9 | 0.9 | 0.88 | 0.77 | 0.7 | 0.72 | 0.8 | 0.9 | 0.9 | 0.9 | 0.8 | 0.62 | 0.3
|  |  |  | Saturday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.3 | 0.72 | 0.78 | 0.8 | 0.9 | 0.9 | 0.9 | 0.88 | 0.77 | 0.7 | 0.72 | 0.8 | 0.9 | 0.9 | 0.9 | 0.8 | 0.62 | 0.3
|  |  |  | Sunday | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.72 | 0.78 | 0.8 | 0.9 | 0.9 | 0.9 | 0.88 | 0.77 | 0.7 | 0.72 | 0.8 | 0.9 | 0.9 | 0.9 | 0.8 | 0.62 | 0.3
Dining | Restaurant | HVACAvail | T24 2022 - Appendix 5.4B , [Restaurant] Updated based on the adopted PNNL occupancy | Weekday | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Saturday | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Sunday | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Dining | Restaurant | ServiceHotWater | T24 2022 - Appendix 5.4B, [Restaurant] Updated based on the adopted PNNL occupancy | Weekday | 0.2 | 0 | 0 | 0 | 0 | 0.6 | 0.6 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25
|  |  |  | Saturday | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3
|  |  |  | Sunday | 0.25 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2
Dining | Restaurant | Infiltration | T24 2022 - Appendix 5.4B, [Restaurant] Updated based on the adopted PNNL occupancy | Weekday | 0.25 | 0 | 0 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  |  | Saturday | 0.25 | 0 | 0 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  |  | Sunday | 0.25 | 0 | 0 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Dining | Restaurant | Refrigeration | T24 2022 - Appendix 5.4B, [Restaurant] | Weekday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Saturday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Sunday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
Dining | Restaurant | HtgSetpt | T24 2022 - Appendix 5.4B, [Restaurant] | Weekday | 70 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
|  |  |  | Saturday | 70 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
|  |  |  | Sunday | 70 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
Dining | Restaurant | ClgSetpt | T24 2022 - Appendix 5.4B, [Restaurant] | Weekday | 75 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
|  |  |  | Saturday | 75 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
|  |  |  | Sunday | 75 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
Kitchen
Kitchen | Kitchen | occupancy | PNNL,ASHRAE 90.1, 2022 Fast Food Restaurant prototype (It has higher occupancy rate during morning compared to T24 2022 - Appendix 5.4B) | Weekday | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.4 | 0.4 | 0.4 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.8 | 0.8 | 0.8 | 0.5 | 0.35 | 0.2
|  |  |  | Saturday | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.4 | 0.2 | 0.45 | 0.5 | 0.5 | 0.35 | 0.3 | 0.3 | 0.3 | 0.7 | 0.9 | 0.7 | 0.65 | 0.55 | 0.35
|  |  |  | Sunday | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.3 | 0.2 | 0.25 | 0.35 | 0.55 | 0.65 | 0.7 | 0.35 | 0.2 | 0.2
Kitchen | Kitchen | Lights | T24 2022 - Appendix 5.4B, [Restaurant] Updated based on the equipment schedule from the plug load and schedule project with CEC | Weekday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.3 | 0.67 | 0.73 | 0.75 | 0.85 | 0.85 | 0.85 | 0.83 | 0.72 | 0.65 | 0.67 | 0.75 | 0.85 | 0.85 | 0.85 | 0.75 | 0.57 | 0.3
|  |  |  | Saturday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.3 | 0.67 | 0.73 | 0.75 | 0.85 | 0.85 | 0.85 | 0.83 | 0.72 | 0.65 | 0.67 | 0.75 | 0.85 | 0.85 | 0.85 | 0.75 | 0.57 | 0.3
|  |  |  | Sunday | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.67 | 0.73 | 0.75 | 0.85 | 0.85 | 0.85 | 0.83 | 0.72 | 0.65 | 0.67 | 0.75 | 0.85 | 0.85 | 0.85 | 0.75 | 0.57 | 0.3
Kitchen | Kitchen | ElecEquipment | Plug load and schedules project with CEC, 2025 | Weekday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.3 | 0.72 | 0.78 | 0.8 | 0.9 | 0.9 | 0.9 | 0.88 | 0.77 | 0.7 | 0.72 | 0.8 | 0.9 | 0.9 | 0.9 | 0.8 | 0.62 | 0.3
|  |  |  | Saturday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.3 | 0.72 | 0.78 | 0.8 | 0.9 | 0.9 | 0.9 | 0.88 | 0.77 | 0.7 | 0.72 | 0.8 | 0.9 | 0.9 | 0.9 | 0.8 | 0.62 | 0.3
|  |  |  | Sunday | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.72 | 0.78 | 0.8 | 0.9 | 0.9 | 0.9 | 0.88 | 0.77 | 0.7 | 0.72 | 0.8 | 0.9 | 0.9 | 0.9 | 0.8 | 0.62 | 0.3
Kitchen | Kitchen | HVACAvail | T24 2022 - Appendix 5.4B , [Restaurant] Updated based on the adopted PNNL occupancy | Weekday | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Saturday | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Sunday | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Kitchen | Kitchen | ServiceHotWater | T24 2022 - Appendix 5.4B, [Restaurant] Updated based on the adopted PNNL occupancy | Weekday | 0.2 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0.3 | 0.3 | 0.3 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.2
|  |  |  | Saturday | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0.3 | 0.3 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.2
|  |  |  | Sunday | 0.25 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0.3 | 0.3 | 0.3 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2
Kitchen | Kitchen | Infiltration | T24 2022 - Appendix 5.4B, [Restaurant] Updated based on the adopted PNNL occupancy | Weekday | 0.25 | 0 | 0 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  |  | Saturday | 0.25 | 0 | 0 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  |  | Sunday | 0.25 | 0 | 0 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Kitchen | Kitchen | ExhaustHoodEqualOrLessThan5000cfm | T24 2022 - Appendix 5.4B, [Restaurant] Updated based on the adopted PNNL occupancy | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
Kitchen | Kitchen | ExhaustHoodGreaterThan 5000cfm | T24 2022 - Appendix 5.4B, [Restaurant] Updated based on the adopted PNNL occupancy | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 0.5 | 1 | 0.5 | 1 | 0.5 | 1 | 0.5 | 1 | 0.5 | 1 | 0.5 | 1 | 0.5 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 0.5 | 1 | 0.5 | 1 | 0.5 | 1 | 0.5 | 1 | 0.5 | 1 | 0.5 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 0.5 | 1 | 0.5 | 1 | 0.5 | 1 | 0.5 | 1 | 0.5 | 1 | 0.5 | 0 | 0 | 0 | 0 | 0
Kitchen | Kitchen | Refrigeration | T24 2022 - Appendix 5.4B, [Restaurant] | Weekday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Saturday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Sunday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
Kitchen | Kitchen | GasEquipment | T24 2022 - Appendix 5.4B, [Restaurant] Updated based on the equipment schedule from the plug load and schedule project with CEC | Weekday | 0.5 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.75 | 0.75 | 0.75 | 0.9 | 0.9 | 0.9 | 0.9 | 0.75 | 0.5 | 0.5
|  |  |  | Saturday | 0.5 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.75 | 0.75 | 0.75 | 0.9 | 0.9 | 0.9 | 0.9 | 0.75 | 0.75 | 0.5
|  |  |  | Sunday | 0.5 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.75 | 0.75 | 0.75 | 0.9 | 0.9 | 0.9 | 0.9 | 0.75 | 0.5 | 0.5
Kitchen | Kitchen | HtgSetpt | Thermostat Setpoints of PNNL 09.1, 2022 Restaurant prototype and HVAC availability schedule of CEC Restaurant prototype | Weekday | 66 | 60 | 60 | 60 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66
|  |  |  | Saturday | 66 | 60 | 60 | 60 | 60 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66
|  |  |  | Sunday | 66 | 60 | 60 | 60 | 60 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66
Kitchen | Kitchen | ClgSetpt | Thermostat Setpoints of PNNL 09.1, 2022 Restaurant prototype and HVAC availability schedule of CEC Restaurant prototype | Weekday | 79 | 86 | 86 | 86 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79
|  |  |  | Saturday | 79 | 86 | 86 | 86 | 86 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79
|  |  |  | Sunday | 79 | 86 | 86 | 86 | 86 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79
Other
| Building | ExtLightingNonMotionCtrl |  | Weekday | bar: Hour 1 to Hour 24
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
| Building | ExtLightingMotionCtrl |  | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Dining | Building | DiningAreaPeopleActivityLevel | Based on Activity level schedules in CEC Prototypes and assumed spaces for Basement | Weekday | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2
|  |  |  | Saturday | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2
|  |  |  | Sunday | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2
Kitchen | Building | KitchenPeopleActivityLevel | Based on Activity level schedules in CEC Prototypes and assumed spaces for Basement | Weekday | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8
|  |  |  | Saturday | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8
|  |  |  | Sunday | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8
Background Data [To be deleted prior to publication] | bar: Hour 1 to Hour 2
Background Data [To be deleted prior to publication] | bar: Hour 1 to Hour 2
| Occupancy | T24 2022 | Kitchen | Weekday | 0.15 | 0.15 | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.8 | 0.8 | 0.8 | 0.5 | 0.35 | 0.2
|  | ComNET |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.75 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.75 | 0.25 | 0.25 | 0.75 | 0.9 | 0.9 | 0.9 | 0.9 | 0.75 | 0.25
|  | Plug load and schedules project |  |  | Hour 1: No match
|  | CPUC |  |  | 0.15 | 0.15 | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.8 | 0.8 | 0.8 | 0.5 | 0.35 | 0.2
|  | PNNL90.1 2022 |  |  | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.4 | 0.4 | 0.4 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.8 | 0.8 | 0.8 | 0.5 | 0.35 | 0.2
|  | Proposed |  |  | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.4 | 0.4 | 0.4 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.8 | 0.8 | 0.8 | 0.5 | 0.35 | 0.2
Occupancy - Kitchen - Weekday
| COMNET/Building_Space_Specific_Loads/dining__cafeteria_fast_food/kitchen/space_specific_schedules.json at master · pnnl/COMNET · GitHub |  |  |  | Hour 14: COMNET/Building_Space_Specific_Loads/dining__cafeteria_fast_food/dining_cafeteria_fast_food/space_specific_schedules.json at master · pnnl/COMNET · GitHub
| Equipment | Proposed | All zones | Weekday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.3 | 0.72 | 0.78 | 0.8 | 0.9 | 0.9 | 0.9 | 0.88 | 0.77 | 0.7 | 0.72 | 0.8 | 0.9 | 0.9 | 0.9 | 0.8 | 0.62 | 0.3
| Equipment | Proposed | All zones | Saturday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.3 | 0.72 | 0.78 | 0.8 | 0.9 | 0.9 | 0.9 | 0.88 | 0.77 | 0.7 | 0.72 | 0.8 | 0.9 | 0.9 | 0.9 | 0.8 | 0.62 | 0.3
| Equipment | Proposed | All zones | Sunday | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.72 | 0.78 | 0.8 | 0.9 | 0.9 | 0.9 | 0.88 | 0.77 | 0.7 | 0.72 | 0.8 | 0.9 | 0.9 | 0.9 | 0.8 | 0.62 | 0.3
| Occupancy | Proposed | All zones | Weekday | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.4 | 0.4 | 0.4 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.8 | 0.8 | 0.8 | 0.5 | 0.35 | 0.2
| Occupancy | Proposed | All zones | Saturday | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.4 | 0.2 | 0.45 | 0.5 | 0.5 | 0.35 | 0.3 | 0.3 | 0.3 | 0.7 | 0.9 | 0.7 | 0.65 | 0.55 | 0.35
| Occupancy | Proposed | All zones | Sunday | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.3 | 0.2 | 0.25 | 0.35 | 0.55 | 0.65 | 0.7 | 0.35 | 0.2 | 0.2
| Lighting | Proposed | All zones | Weekday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.3 | 0.67 | 0.73 | 0.75 | 0.85 | 0.85 | 0.85 | 0.83 | 0.72 | 0.65 | 0.67 | 0.75 | 0.85 | 0.85 | 0.85 | 0.75 | 0.57 | 0.3
| Lighting | Proposed | All zones | Saturday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.3 | 0.67 | 0.73 | 0.75 | 0.85 | 0.85 | 0.85 | 0.83 | 0.72 | 0.65 | 0.67 | 0.75 | 0.85 | 0.85 | 0.85 | 0.75 | 0.57 | 0.3
| Lighting | Proposed | All zones | Sunday | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.67 | 0.73 | 0.75 | 0.85 | 0.85 | 0.85 | 0.83 | 0.72 | 0.65 | 0.67 | 0.75 | 0.85 | 0.85 | 0.85 | 0.75 | 0.57 | 0.3
| Equipment | T24 2022 | All zones | Weekday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.4 | 0.4 | 0.6 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
| Equipment | T24 2022 | All zones | Saturday | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
| Equipment | T24 2022 | All zones | Sunday | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3
| Occupancy | T24 2022 | All zones | Weekday | 0.15 | 0.15 | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.8 | 0.8 | 0.8 | 0.5 | 0.35 | 0.2
| Occupancy | T24 2022 | All zones | Saturday | 0.3 | 0.25 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.2 | 0.45 | 0.5 | 0.5 | 0.35 | 0.3 | 0.3 | 0.3 | 0.7 | 0.9 | 0.7 | 0.65 | 0.55 | 0.35
| Occupancy | T24 2022 | All zones | Sunday | 0.2 | 0.2 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.25 | 0.25 | 0.15 | 0.2 | 0.25 | 0.35 | 0.55 | 0.65 | 0.7 | 0.35 | 0.2 | 0.2
| Lighting | T24 2022 | All zones | Weekday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.35 | 0.35 | 0.55 | 0.55 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.45 | 0.3
| Lighting | T24 2022 | All zones | Saturday | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.55 | 0.55 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.45 | 0.3
| Lighting | T24 2022 | All zones | Sunday | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.45 | 0.45 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.45 | 0.3
| Equipment | Plug load and schedules project | All zones | Weekday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.3 | 0.72 | 0.78 | 0.8 | 0.9 | 0.9 | 0.9 | 0.88 | 0.77 | 0.7 | 0.72 | 0.8 | 0.9 | 0.9 | 0.9 | 0.8 | 0.62 | 0.3
| Equipment | Plug load and schedules project | All zones | Saturday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.3 | 0.72 | 0.78 | 0.8 | 0.9 | 0.9 | 0.9 | 0.88 | 0.77 | 0.7 | 0.72 | 0.8 | 0.9 | 0.9 | 0.9 | 0.8 | 0.62 | 0.3
| Equipment | Plug load and schedules project | All zones | Sunday | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.72 | 0.78 | 0.8 | 0.9 | 0.9 | 0.9 | 0.88 | 0.77 | 0.7 | 0.72 | 0.8 | 0.9 | 0.9 | 0.9 | 0.8 | 0.62 | 0.3
| Occupancy | ComNET | Kitchen | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.75 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.75 | 0.25 | 0.25 | 0.75 | 0.9 | 0.9 | 0.9 | 0.9 | 0.75 | 0.25
| Occupancy | ComNET | Kitchen | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.75 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.75 | 0.25 | 0.25 | 0.75 | 0.9 | 0.9 | 0.9 | 0.9 | 0.75 | 0.25
| Occupancy | ComNET | Kitchen | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.75 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.75 | 0.25 | 0.25 | 0.75 | 0.9 | 0.9 | 0.9 | 0.9 | 0.75 | 0.25
| Equipment | ComNET | Kitchen | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.33
| Equipment | ComNET | Kitchen | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.33
| Equipment | ComNET | Kitchen | Sunday | 0.05, | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.33
| lighting | ComNET | Kitchen | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
| lighting | ComNET | Kitchen | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
| lighting | ComNET | Kitchen | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
| Occupancy | ComNET | Dining | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.9 | 0.9 | 0.5 | 0.25 | 0.25 | 0.25 | 0.5 | 0.9 | 0.9 | 0.9 | 0.5 | 0
| Occupancy | ComNET | Dining | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.9 | 0.9 | 0.5 | 0.25 | 0.25 | 0.25 | 0.5 | 0.9 | 0.9 | 0.9 | 0.5 | 0
| Occupancy | ComNET | Dining | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.9 | 0.9 | 0.5 | 0.25 | 0.25 | 0.25 | 0.5 | 0.9 | 0.9 | 0.9 | 0.5 | 0
| Equipment | ComNET | Dining | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.34
| Equipment | ComNET | Dining | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.34
| Equipment | ComNET | Dining | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.34
| lighting | ComNET | Dining | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0
| lighting | ComNET | Dining | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0
| lighting | ComNET | Dining | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0
| Equipment | PNNL90.1 2022 | All zones | Weekday | 0.029967 | 0.019901 | 0.029852 | 0.019901 | 0.049754 | 0.11987 | 0.12986 | 0.14984 | 0.1798 | 0.20977 | 0.25972 | 0.28969 | 0.26971 | 0.24973 | 0.22975 | 0.22975 | 0.25972 | 0.25972 | 0.23974 | 0.21976 | 0.19978 | 0.1798 | 0.089902 | 0.029967
| Equipment | PNNL90.1 2022 | All zones | Saturday | 0.029967 | 0.019901 | 0.029852 | 0.019901 | 0.049754 | 0.11941 | 0.12986 | 0.14984 | 0.1798 | 0.20977 | 0.25972 | 0.28969 | 0.26971 | 0.24973 | 0.22975 | 0.22975 | 0.25972 | 0.25972 | 0.23974 | 0.21976 | 0.19978 | 0.1798 | 0.089902 | 0.029967
| Equipment | PNNL90.1 2022 | All zones | Sunday | 0.029967 | 0.019901 | 0.029852 | 0.019901 | 0.049754 | 0.11941 | 0.12986 | 0.14984 | 0.1798 | 0.20977 | 0.25972 | 0.28969 | 0.26971 | 0.24973 | 0.22975 | 0.22975 | 0.25972 | 0.25972 | 0.23974 | 0.21976 | 0.19978 | 0.1798 | 0.089902 | 0.029967
| Occupancy | PNNL90.1 2022 | All zones | Weekday | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.4 | 0.4 | 0.4 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.8 | 0.8 | 0.8 | 0.5 | 0.35 | 0.2
| Occupancy | PNNL90.1 2022 | All zones | Saturday | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.4 | 0.2 | 0.45 | 0.5 | 0.5 | 0.35 | 0.3 | 0.3 | 0.3 | 0.7 | 0.9 | 0.7 | 0.65 | 0.55 | 0.35
| Occupancy | PNNL90.1 2022 | All zones | Sunday | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.3 | 0.2 | 0.25 | 0.35 | 0.55 | 0.65 | 0.7 | 0.35 | 0.2 | 0.2
| lighting | PNNL90.1 2022 | All zones | Weekday | 0.13686 | 0.13686 | 0.13686 | 0.13686 | 0.13686 | 0.18248 | 0.36496 | 0.36496 | 0.54743 | 0.54743 | 0.82115 | 0.82115 | 0.82115 | 0.82115 | 0.82115 | 0.82115 | 0.82115 | 0.82115 | 0.82115 | 0.82115 | 0.82115 | 0.82115 | 0.4562 | 0.27372
| lighting | PNNL90.1 2022 | All zones | Saturday | 0.18248 | 0.13686 | 0.13686 | 0.13686 | 0.13686 | 0.13686 | 0.27372 | 0.27372 | 0.54743 | 0.54743 | 0.72991 | 0.72991 | 0.72991 | 0.72991 | 0.72991 | 0.72991 | 0.72991 | 0.82115 | 0.82115 | 0.82115 | 0.82115 | 0.82115 | 0.4562 | 0.27372
| lighting | PNNL90.1 2022 | All zones | Sunday | 0.18248 | 0.13686 | 0.13686 | 0.13686 | 0.13686 | 0.13686 | 0.27372 | 0.27372 | 0.4562 | 0.4562 | 0.63867 | 0.63867 | 0.63867 | 0.63867 | 0.63867 | 0.63867 | 0.54743 | 0.54743 | 0.54743 | 0.54743 | 0.54743 | 0.54743 | 0.4562 | 0.27372
| Equipment | CPUC | Dining | Weekday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.4 | 0.4 | 0.6 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
| Equipment | CPUC | Dining | Saturday | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
| Equipment | CPUC | Dining | Sunday | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3
| Occupancy | CPUC | Dining | Weekday | 0.15 | 0.15 | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.8 | 0.8 | 0.8 | 0.5 | 0.35 | 0.2
| Occupancy | CPUC | Dining | Saturday | 0.3 | 0.25 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.2 | 0.45 | 0.5 | 0.5 | 0.35 | 0.3 | 0.3 | 0.3 | 0.7 | 0.9 | 0.7 | 0.65 | 0.55 | 0.35
| Occupancy | CPUC | Dining | Sunday | 0.2 | 0.2 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.25 | 0.25 | 0.15 | 0.2 | 0.25 | 0.35 | 0.55 | 0.65 | 0.7 | 0.35 | 0.2 | 0.2
| lighting | CPUC | Dining | Weekday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.35 | 0.35 | 0.55 | 0.55 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.45 | 0.3
| lighting | CPUC | Dining | Saturday | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.55 | 0.55 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.45 | 0.3
| lighting | CPUC | Dining | Sunday | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.45 | 0.45 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.45 | 0.3
| Equipment | CPUC | Kitchen | Weekday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.4 | 0.4 | 0.6 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
| Equipment | CPUC | Kitchen | Saturday | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
| Equipment | CPUC | Kitchen | Sunday | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3
| Occupancy | CPUC | Kitchen | Weekday | 0.15 | 0.15 | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.8 | 0.8 | 0.8 | 0.5 | 0.35 | 0.2
| Occupancy | CPUC | Kitchen | Saturday | 0.3 | 0.25 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.2 | 0.45 | 0.5 | 0.5 | 0.35 | 0.3 | 0.3 | 0.3 | 0.7 | 0.9 | 0.7 | 0.65 | 0.55 | 0.35
| Occupancy | CPUC | Kitchen | Sunday | 0.2 | 0.2 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.25 | 0.25 | 0.15 | 0.2 | 0.25 | 0.35 | 0.55 | 0.65 | 0.7 | 0.35 | 0.2 | 0.2
| lighting | CPUC | Kitchen | Weekday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.35 | 0.35 | 0.55 | 0.55 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.45 | 0.3
| lighting | CPUC | Kitchen | Saturday | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.55 | 0.55 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.45 | 0.3
| lighting | CPUC | Kitchen | Sunday | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.45 | 0.45 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.45 | 0.3
| RestaurantFastFood Equipment | T24 2022 - Appendix 5.4B | All zones | Weekday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.4 | 0.4 | 0.6 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
|  |  |  | Saturday | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
|  |  |  | Sunday | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3
| RestaurantFastFood Occupancy | T24 2022 - Appendix 5.4B | All zones | Weekday | 0.15 | 0.15 | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.8 | 0.8 | 0.8 | 0.5 | 0.35 | 0.2
|  |  |  | Saturday | 0.3 | 0.25 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.2 | 0.45 | 0.5 | 0.5 | 0.35 | 0.3 | 0.3 | 0.3 | 0.7 | 0.9 | 0.7 | 0.65 | 0.55 | 0.35
|  |  |  | Sunday | 0.2 | 0.2 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.25 | 0.25 | 0.15 | 0.2 | 0.25 | 0.35 | 0.55 | 0.65 | 0.7 | 0.35 | 0.2 | 0.2
| RestaurantFastFoodLighting | T24 2022 - Appendix 5.4B | All zones | Weekday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.35 | 0.35 | 0.55 | 0.55 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.45 | 0.3
|  |  |  | Saturday | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.55 | 0.55 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.45 | 0.3
|  |  |  | Sunday | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.45 | 0.45 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.45 | 0.3
| RestaurantFastFood HVAC availability | T24 2022 - Appendix 5.4B | All zones | Weekday | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Saturday | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Sunday | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| RestaurantFastFood Service Hot Water | T24 2022 - Appendix 5.4B | Kitchen | Weekday | 0.2 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25
|  |  |  | Saturday | 0.2 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3
|  |  |  | Sunday | 0.25 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2
| RestaurantFastFood Infiltration | T24 2022 - Appendix 5.4B | All zones | Weekday | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  |  | Saturday | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  |  | Sunday | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
| Exhaust Hood Equal Or Less Than 5000cfm | T24 2022 - Appendix 5.4B | Kitchen | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
| Exhaust Hood Greater Than 5000cfm | T24 2022 - Appendix 5.4B | Kitchen | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | 1 | 0.5 | 1 | 0.5 | 1 | 0.5 | 1 | 0.5 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 0.5 | 1 | 0.5 | 1 | 0.5 | 1 | 0.5 | 1 | 0.5 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.5 | 1 | 0.5 | 1 | 0.5 | 1 | 0.5 | 1 | 0.5 | 0 | 0 | 0 | 0 | 0
| Refrigeration | T24 2022 - Appendix 5.4B | Kitchen | Weekday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Saturday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Sunday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
| Gas Equipment | T24 2022 - Appendix 5.4B | Kitchen | Weekday | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.75 | 0.75 | 0.75 | 0.9 | 0.9 | 0.9 | 0.9 | 0.75 | 0.5 | 0.5
|  |  |  | Saturday | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.75 | 0.75 | 0.75 | 0.9 | 0.9 | 0.9 | 0.9 | 0.75 | 0.75 | 0.5
|  |  |  | Sunday | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.75 | 0.75 | 0.75 | 0.9 | 0.9 | 0.9 | 0.9 | 0.75 | 0.5 | 0.5
;
Note on E240: Yousefi, Fatemeh: Saturday updated schedule proposed by the CEC project is similar to weekday schedule.
Note on C242: Yousefi, Fatemeh: (Dining_cafeteria_fast_food)
Note on C245: Yousefi, Fatemeh: (Dining_cafeteria_fast_food)
Note on C248: Yousefi, Fatemeh: (Dining_cafeteria_fast_food)
Note on C251: Yousefi, Fatemeh: (Dining_cafeteria_fast_food)
Note on C254: Yousefi, Fatemeh: (Dining_cafeteria_fast_food)
Note on C257: Yousefi, Fatemeh: (Dining_cafeteria_fast_food)

## Weights
% of Floor Area per CZ and Vintage Bin - Restaurant | [7 empty] | % of Floor Area per CZ and Vintage Bin - Restaurant
Prototype | CZ | Vintage Bin | [5 empty] | Prototype | Vintage Bin | CZ
|  | Pre-1978 | 1978-1997 | 1998-2007 | 2008-2018 | Not available |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
Restaurant | 1 | 32.39% | 30.26% | 13.06% | 10.08% | 14.21% | 100% | Restaurant | Pre-1978 | 0.8633% | 2.349% | 10.03% | 5.28% | 0.8409% | 8.82% | 4.229% | 14.45% | 21.67% | 5.094% | 2.788% | 11.23% | 3.128% | 2.006% | 1.901% | 5.329% | 100%
| 2 | 47.22% | 28.14% | 7.544% | 5.14% | 11.96% | 100% |  | 1978-1997 | 0.8807% | 1.528% | 6.698% | 3.458% | 0.6681% | 7.234% | 5.195% | 8.671% | 15.81% | 11.71% | 2.606% | 12.57% | 4.03% | 2.495% | 6.253% | 10.2% | 100%
| 3 | 43.58% | 26.66% | 11.16% | 4.712% | 13.88% | 100% |  | 1998-2007 | 1.071% | 1.154% | 7.9% | 3.87% | 1.1% | 4.049% | 3.194% | 6.653% | 8.403% | 11.25% | 4.502% | 20.21% | 5.478% | 2.731% | 5.444% | 13% | 100%
| 4 | 44.34% | 26.6% | 10.57% | 4.59% | 13.9% | 100% |  | 2008-2018 | 1.504% | 1.431% | 6.069% | 3.059% | 0.6461% | 3.993% | 3.652% | 6.959% | 7.532% | 10.61% | 4.418% | 20.68% | 8.129% | 2.409% | 6.177% | 12.73% | 100%
| 5 | 37.74% | 27.46% | 16.06% | 5.181% | 13.56% | 100% |  | Not available | 1.184% | 1.859% | 9.985% | 5.173% | 0.9447% | 5.565% | 2.416% | 10.45% | 14.38% | 8.062% | 3.33% | 14.22% | 6.332% | 1.978% | 6.387% | 7.735% | 100%
| 6 | 45.8% | 34.41% | 6.838% | 3.705% | 9.246% | 100% |  | Total | 0.9729% | 1.815% | 8.4% | 4.346% | 0.8133% | 7.029% | 4.18% | 10.64% | 16.36% | 8.741% | 3.1% | 13.71% | 4.409% | 2.278% | 4.579% | 8.631% | 100%
| 7 | 36.93% | 41.55% | 9.07% | 5.698% | 6.75% | 100%
| 8 | 49.59% | 27.25% | 7.424% | 4.266% | 11.47% | 100%
| 9 | 48.34% | 32.3% | 6.096% | 3.002% | 10.26% | 100%
| 10 | 21.27% | 44.77% | 15.28% | 7.917% | 10.77% | 100%
| 11 | 32.82% | 28.1% | 17.24% | 9.294% | 12.54% | 100%
| 12 | 29.89% | 30.66% | 17.5% | 9.838% | 12.11% | 100%
| 13 | 25.9% | 30.55% | 14.75% | 12.02% | 16.77% | 100%
| 14 | 32.13% | 36.6% | 14.23% | 6.896% | 10.14% | 100%
| 15 | 15.16% | 45.65% | 14.11% | 8.797% | 16.29% | 100%
| 16 | 22.54% | 39.5% | 17.88% | 9.618% | 10.47% | 100%
| Statewide | 39.89% | 32.25% | 10.98% | 5.629% | 11.25% | 100%
Ref: CEUS 2022 dataset
And converted FZ level data to CZ level
Restaurants have only one category in CEUS data.
Background Data [To be deleted prior to publication]

## EV Charger (hidden)
EV Charger - RestaurantFastFood
TBD

## PV (hidden)
PV - RestaurantFastFood
TBD

## Data (hidden)
Space Function | Electric Equipment Load Intensity | Electric Equipment Load Intensity | LPD
Aging Eye/Low-vision (Corridor Area) |  |  | 2013 | 2016 | 2019 | 2025
Aging Eye/Low-vision (Dining)
Aging Eye/Low-vision (Lobby, Main Entry)
Aging Eye/Low-vision (Lounge/Waiting Area)
Aging Eye/Low-vision (Multipurpose Room)
Aging Eye/Low-vision (Religious Worship Area)
Aging Eye/Low-vision (Restroom)
Aging Eye/Low-vision (Stairwell)
Audience Seating Area
Auditorium Area
Auto Repair / Maintenance Area
Barber, Beauty Salon, Spa Area
Civic Meeting Place Area
Classroom, Lecture, Training, Vocational Areas
Concourse and Atria Area
Convention, Conference, Multipurpose and Meeting Area
Copy Room
Corridor Area
Dining Area (Bar/Lounge and Fine Dining)
Dining Area (Cafeteria/Fast Food)
Dining Area (Family and Leisure)
Electrical, Mechanical, Telephone Rooms
Exercise/Fitness Center and Gymnasium Areas
Financial Transaction Area
Healthcare Facility and Hospitals (Exam/Treatment Room)
Healthcare Facility and Hospitals (Imaging Room)
Healthcare Facility and Hospitals (Medical Supply Room)
Healthcare Facility and Hospitals (Nursery)
Healthcare Facility and Hospitals (Nurse's Station)
Healthcare Facility and Hospitals (Operating Room)
Healthcare Facility and Hospitals (Patient Room)
Healthcare Facility and Hospitals (Physical Therapy Room)
Healthcare Facility and Hospitals (Recovery Room)
Hotel Function Area
Kitchen/Food Preparation Area
Kitchenette or Residential Kitchen
Laboratory, Scientific
Laundry Area
Library (Reading Area)
Library (Stacks Area)
Lobby, Main Entry
Locker Room
Lounge, Breakroom, or Waiting Area
Manufacturing, Commercial & Industrial Work Area (Low Bay)
Manufacturing, Commercial & Industrial Work Area (High Bay)
Manufacturing, Commercial & Industrial Work Area (Precision)
Museum Area (Exhibition/Display)
Museum Area (Restoration Room)
Office Area (>250 square feet)
Office Area (<250 square feet)
Parking Garage Area (Parking Zone and Ramps)
Parking Garage Area (Daylight Adaptation Zones)
Pharmacy Area
Retail Sales Area (Grocery Sales)
Retail Sales Area (Retail Merchandise Sales)
Retail Sales Area (Fitting Room)
Religious Worship Area
Restrooms
Stairwell
Storage, Commercial/Industrial (Warehouse)
Storage, Commercial/Industrial (Refrigerated)
Storage, Commercial/Industrial (Shipping & Handling)
Storage (General)
Sports Arena - Playing Area (> 5,000 Spectators)
Sports Arena - Playing Area (2,000 - 5,000 Spectators)
Sports Arena - Playing Area (< 2,000 Spectators)
Sports Arena - Playing Area (Recreational)
Theater Area (Motion Picture)
Theater Area (Performance)
Transportation Function (Baggage Area)
Transportation Function (Ticketing Area)
Videoconferencing Studio
High-Rise Residential Living Spaces
Hotel/Motel Guest Room
All other
Attic
Reception Area
Elevator
Plenum
IT Room (EPD 12)
Computer Room (EPD 20)
Server Room (EPD 45)