## Notes
Data Sources
Dataset | Dodge 2023
Prototype | CEC prototype (CBECC 2022.3.1) | https://bees.noresco.com/software2022.html
| TRC Multifamily Prototypes study (2019) | https://title24stakeholders.com/wp-content/uploads/2019/06/SCE-MFModeling_MultifamilyPrototypesReport_2019-06-07_clean.pdf
Codes | Title 24, part 6 (1986, 2001, 2007, 2013, 2022, 2025)
ASHRAE 90.1 (2022)
ASHRAE Handbook of Fundamentals (Ch. 15 Tables 4 and 10)
CFR Title 10 (2010, 2024)
Others | 2019 Outdoor Lighting CASE Report | https://title24stakeholders.com/wp-content/uploads/2016/10/T24-2019-CASE-Study-Results-Report-Outdoor-Sources_Final_with-Attachments.pdf
| PNNL 20405, 2011 | https://www.pnnl.gov/main/publications/external/technical_reports/PNNL-20405.pdf
| 2024 CASE Report: A Comprehensive, High Efficiency Solution for Water Heating in Multifamily Buildings | https://www.energy.ca.gov/sites/default/files/2024-06/CEC-500-2024-054.pdf
| 2022 CASE Report: Multifamily Domestic Hot Water Distribution | https://title24stakeholders.com/wp-content/uploads/2020/09/2022_T24_Final-CASE-Report-MF-DHW-Dist.pdf
| Maguire & Roberts 2020 (NREL/CP-5500-71633): Deriving Simulation Parameters for Storage-Type Water Heaters Using Ratings Data Produced from the Uniform Energy Factor Test Procedure | https://docs.nrel.gov/docs/fy21osti/71633.pdf
Construction Rate
Notes

## Prototype
NORESCO, Updated September 2026
ApartmentMidRise
Characteristic | Value | Data Sources
Building Type | Mid-Rise Apartment
Building Category | Nonresidential
Version | v2-0
Vintages | 4 Vintages: Pre-1978 , 1978-1997 ,1998-2007 , 2008-2018 New Construction (2019+) | Following the vintage‑bin analysis performed for the nonresidential prototypes. A summary of the findings is presented in the following paper, with a link provided in the Notes tab: Yousefi, F., Athalye, R. (2025). “Determining Vintage Bins for Prototype Development: An Analysis of California Commercial Buildings.” ASHRAE Annual Conference.
Shape |  | CEC Prototype model TRC Multifamily Prototypes study (2019) https://title24stakeholders.com/wp-content/uploads/2019/06/SCE-MFModeling_MultifamilyPrototypesReport_2019-06-07_clean.pdf
Total Floor Area (ft2) | 141013.76 | CEC Prototype model TRC Multifamily Prototypes study (2019)
Aspect Ratio | 1.1613
Number of Floors | 5 above-ground floors including one underground parking garage (180 ft x 155 ft)
Roof type | Flat roof
WWR (above grade) | South: 22.0%, East: 22.0%, North: 22.0%, West: 22.0% Total 22.0%
Window dimensions | 5 * 3
Shading Geometry | -
Floor to floor height (feet) | Residential: 10 Non-residential: 10 Parking: 15
Floor to ceiling height (feet) | Residential: 9 Non-residential: 10 Parking: 14
Glazing sill height (feet) | 3.1 ft (in first floor), 2.95 ft. (in upper floors)
Number of dwelling units | 88 | 22 per residential floor × 4 floors. Mix per floor from TRC/plans: 2 studio, 10 one-bed, 8 two-bed, 2 three-bed.
Above grade wall area (ft²) | 42304.13
Gross wall area (ft²) | 51685.04
Roof area (ft²) | 27902.72
Underground Gross Wall Area (ft²) | 9380.91

## Zones
Proposed Layout - ApartmentMidRise
Building | Space/Thermal Zone | Space Type [Primarily from: T24, 2022 Appendix 5.4A] - See Notes column | Res/NR | Schedule Category | No. of Dwelling Units | Dwelling Unit Type | Thermal Zone (HVAC Zone) | Conditioned [Y/N] | Area Fraction | Area (ft²) | Volume (ft³) | Multipliers | People | People (persons/1,000 ft²) | Notes | Spaces and Zoning layout
ApartmentMidRise | F1 BUSINESS CENTER | Convention, Conference, Multipurpose and Meeting Area | NR | ResidentialCommon | NA | NA | AHU1 | Y | 0.0025532 | 360.04 | 3600.53 | 1 | 24.0039 | 66.67 | Dwellings: occupants/unit — ACM 2025 §6.5.4 Max(Nbr+1, 2) Parking garage: 0 (unoccupied for internal loads; App 5.4A 5/1000 not used) Other nonresidential: persons/1,000 ft² — App 5.4A / Table 120.1-A
ApartmentMidRise | F1 CORRIDOR | Corridor Area | NR | ResidentialCommon | NA | NA | AHU2 | Y | 0.013617 | 1920.19 | 19202.81 | 1 | 19.2019 | 10
ApartmentMidRise | F1 FITNESS CENTER | Exercise/Fitness Center and Gymnasium Areas | NR | ResidentialCommon | NA | NA | AHU3 | Y | 0.006383 | 900.09 | 9001.32 | 1 | 18.0018 | 20
ApartmentMidRise | F1 LEASING OFFICE | Office Area (>250 square feet) | NR | ResidentialCommon | NA | NA | AHU4 | Y | 0.0024468 | 345.03 | 3450.51 | 1 | 3.4503 | 10
ApartmentMidRise | F1 LOUNGE | Lobby, Main Entry | NR | ResidentialCommon | NA | NA | AHU5 | Y | 0.0074468 | 1050.1 | 10501.54 | 1 | 70.0417 | 66.7
ApartmentMidRise | F1 MECHANICAL ROOM | Electrical, Mechanical, Telephone Rooms | NR | Ancillary | NA | NA | AHU6 | Y | 0.0030638 | 432.04 | 4320.63 | 1 | 1.2961 | 3
ApartmentMidRise | F1 RETAIL N-NW | Retail Sales Area (Retail Merchandise Sales) | NR | Retail | NA | NA | AHU7 | Y | 0.042447 | 5985.58 | 59858.76 | 1 | 99.7597 | 16.6667
ApartmentMidRise | F1 RETAIL NE | Retail Sales Area (Retail Merchandise Sales) | NR | Retail | NA | NA | AHU8 | Y | 0.030638 | 4320.42 | 43206.32 | 1 | 72.007 | 16.6667
ApartmentMidRise | F1 RETAIL SE | Retail Sales Area (Retail Merchandise Sales) | NR | Retail | NA | NA | AHU9 | Y | 0.020426 | 2880.28 | 28804.22 | 1 | 48.0047 | 16.6667
ApartmentMidRise | F1 RETAIL SW | Retail Sales Area (Retail Merchandise Sales) | NR | Retail | NA | NA | AHU10 | Y | 0.031404 | 4428.43 | 44286.48 | 1 | 73.8072 | 16.6667
ApartmentMidRise | F2-4 1-BED CORE EAST | Residential Living Spaces | Res | ResidentialLiving | 6 | 1-Bed Type | AHU11 | Y | 0.030638 | 1440.14 | 14402.11 | 3 | 12 | 2
ApartmentMidRise | F2-4 1-BED CORE N | Residential Living Spaces | Res | ResidentialLiving | 3 | 1-Bed Type | AHU12 | Y | 0.015319 | 720.07 | 7201.05 | 3 | 6 | 2
ApartmentMidRise | F2-4 1-BED CORE WEST | Residential Living Spaces | Res | ResidentialLiving | 6 | 1-Bed Type | AHU13 | Y | 0.030638 | 1440.14 | 14402.11 | 3 | 12 | 2
ApartmentMidRise | F2-4 1-BED NORTH | Residential Living Spaces | Res | ResidentialLiving | 15 | 1-Bed Type | AHU14 | Y | 0.079149 | 3720.36 | 37205.45 | 3 | 30 | 2
ApartmentMidRise | F2-4 2-BED CORE NE-NW | Residential Living Spaces | Res | ResidentialLiving | 6 | 2-Bed Type | AHU15 | Y | 0.045957 | 2160.21 | 21603.16 | 3 | 18 | 3
ApartmentMidRise | F2-4 2-BED EAST | Residential Living Spaces | Res | ResidentialLiving | 9 | 2-Bed Type | AHU16 | Y | 0.068936 | 3240.32 | 32404.74 | 3 | 27 | 3
ApartmentMidRise | F2-4 2-BED WEST | Residential Living Spaces | Res | ResidentialLiving | 9 | 2-Bed Type | AHU17 | Y | 0.068936 | 3240.32 | 32404.74 | 3 | 27 | 3
ApartmentMidRise | F2-4 3-BED NE | Residential Living Spaces | Res | ResidentialLiving | 3 | 3-Bed Type | AHU18 | Y | 0.03 | 1410.14 | 14102.06 | 3 | 12 | 4
ApartmentMidRise | F2-4 3-BED NW | Residential Living Spaces | Res | ResidentialLiving | 3 | 3-Bed Type | AHU19 | Y | 0.03 | 1410.14 | 14102.06 | 3 | 12 | 4
ApartmentMidRise | F2-4 CORRIDOR | Corridor Area | NR | ResidentialCommon | NA | NA | AHU20 | Y | 0.054894 | 2580.25 | 25803.78 | 3 | 77.4075 | 10
ApartmentMidRise | F2-4 LAUNDRY | Laundry Area | NR | ResidentialCommon | NA | NA | AHU21 | Y | 0.0038298 | 180.02 | 1800.26 | 3 | 5.4006 | 10
ApartmentMidRise | F2-4 STUDIO SE | Residential Living Spaces | Res | ResidentialLiving | 3 | Studio Type | AHU22 | Y | 0.011489 | 540.05 | 5400.79 | 3 | 6 | 2
ApartmentMidRise | F2-4 STUDIO SW | Residential Living Spaces | Res | ResidentialLiving | 3 | Studio Type | AHU23 | Y | 0.011489 | 540.05 | 5400.79 | 3 | 6 | 2
ApartmentMidRise | F5 1-BED CORE EAST | Residential Living Spaces | Res | ResidentialLiving | 2 | 1-Bed Type | AHU24 | Y | 0.010213 | 1440.14 | 14402.11 | 1 | 4 | 2
ApartmentMidRise | F5 1-BED CORE N | Residential Living Spaces | Res | ResidentialLiving | 1 | 1-Bed Type | AHU25 | Y | 0.0051064 | 720.07 | 7201.05 | 1 | 2 | 2
ApartmentMidRise | F5 1-BED CORE WEST | Residential Living Spaces | Res | ResidentialLiving | 2 | 1-Bed Type | AHU26 | Y | 0.010213 | 1440.14 | 14402.11 | 1 | 4 | 2
ApartmentMidRise | F5 1-BED NORTH | Residential Living Spaces | Res | ResidentialLiving | 5 | 1-Bed Type | AHU27 | Y | 0.026383 | 3720.36 | 37205.45 | 1 | 10 | 2
ApartmentMidRise | F5 2-BED CORE NE-NW | Residential Living Spaces | Res | ResidentialLiving | 2 | 2-Bed Type | AHU28 | Y | 0.015319 | 2160.21 | 21603.16 | 1 | 6 | 3
ApartmentMidRise | F5 2-BED EAST | Residential Living Spaces | Res | ResidentialLiving | 3 | 2-Bed Type | AHU29 | Y | 0.022979 | 3240.32 | 32404.74 | 1 | 9 | 3
ApartmentMidRise | F5 2-BED WEST | Residential Living Spaces | Res | ResidentialLiving | 3 | 2-Bed Type | AHU30 | Y | 0.022979 | 3240.32 | 32404.74 | 1 | 9 | 3
ApartmentMidRise | F5 3-BED NE | Residential Living Spaces | Res | ResidentialLiving | 1 | 3-Bed Type | AHU31 | Y | 0.01 | 1410.14 | 14102.06 | 1 | 4 | 4
ApartmentMidRise | F5 3-BED NW | Residential Living Spaces | Res | ResidentialLiving | 1 | 3-Bed Type | AHU32 | Y | 0.01 | 1410.14 | 14102.06 | 1 | 4 | 4
ApartmentMidRise | F5 CORRIDOR | Corridor Area | NR | ResidentialCommon | NA | NA | AHU33 | Y | 0.018298 | 2580.25 | 25803.78 | 1 | 25.8025 | 10
ApartmentMidRise | F5 LAUNDRY | Laundry Area | NR | ResidentialCommon | NA | NA | AHU34 | Y | 0.0012766 | 180.02 | 1800.26 | 1 | 1.8002 | 10
ApartmentMidRise | F5 STUDIO SE | Residential Living Spaces | Res | ResidentialLiving | 1 | Studio Type | AHU35 | Y | 0.0038298 | 540.05 | 5400.79 | 1 | 2 | 2
ApartmentMidRise | F5 STUDIO SW | Residential Living Spaces | Res | ResidentialLiving | 1 | Studio Type | AHU36 | Y | 0.0038298 | 540.05 | 5400.79 | 1 | 2 | 2
ApartmentMidRise | PARKING GARAGE | Parking Garage Area (Parking Zone and Ramps) | NR | ResidentialCommon | NA | NA | none | N | 0.19787 | 27902.72 | 390657.19 | 1 | 0 | 0
Total (1 Building) | Total (37 Spaces) | Total (11 Space Types) |  |  | Total (88 Dwelling Units) | Total (4 Dwelling Unit Types) | Total (37 Thermal Zones) | Total (36 Conditioned Zones, 1 Unconditioned Zones) | 100% | 141013.76 | 1069356.51 |  | 763.985
N
N

## Envelope
Envelope - ApartmentMidRise
Element | Prototype | Assembly Type | Construction | Thermal Properties | Vintage | Selected T24 | Notes | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
External Wall (Floor 1) | ApartmentMidRise | ExtWall_MassHeavy_Nonres | Heavy mass wall: 8-in cast-in-place concrete wall + insulation + air/water barrier + exterior cladding + gypsum board Insulation only where the vintage U-factor requires | U-factor IP | Pre 1978 | N/A | Using: 1)ASHRAE 90.1‑2022, Table A3.1‑1: R‑0 wall (U = 0.74 for concrete); using U = 5.523 for stucco, U = 1.746 for gypsum board, and U=1.54 for Air - Metal Wall Framing 2) and a 7.7% cumulative wall renovation rate through 2028, based on the average annual rate from CBECS 2003 and 2012 projected over 48 years. | 0.35457 | 0.36304 | 0.36304 | 0.36304 | 0.36304 | 0.36304 | 0.36304 | 0.36304 | 0.36304 | 0.36304 | 0.34926 | 0.35457 | 0.35133 | 0.34926 | 0.34926 | 0.34741
[5 empty] | 1978-1997 | 1992 | Same as 1992. No direct regulation was found in 1986 for concrete walls. Also, T24, 1986, Table 2-53B and Equation 2-53E presents U-factors more than the previous vintage (for wall density of >81 lb/ft² & Degree day<3000). | 0.36 | 0.36304 | 0.36304 | 0.36304 | 0.36304 | 0.36304 | 0.36304 | 0.36304 | 0.36304 | 0.36304 | 0.36304 | 0.36304 | 0.36304 | 0.36304 | 0.36304 | 0.36
[5 empty] | 1998-2007 | 2001 | Table 1-H Mass HC≥15 (2001). CZ groups 1&16 / 3-5 / 6-9 / 2&10-13 / 14-15. | 0.36 | 0.36304 | 0.36304 | 0.36304 | 0.36304 | 0.36304 | 0.36304 | 0.36304 | 0.36304 | 0.36304 | 0.36304 | 0.36304 | 0.36304 | 0.36304 | 0.36304 | 0.36
[5 empty] | 2008-2018 | 2013 | Table 140.3-B Walls — Mass, Heavy (2013) | 0.253 | 0.36304 | 0.36304 | 0.36304 | 0.36304 | 0.36304 | 0.36304 | 0.36304 | 0.36304 | 0.36304 | 0.18 | 0.25 | 0.21 | 0.18 | 0.18 | 0.16
[5 empty] | Existing |  | Weighted average of all 4 vintages | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 2019+ | 2025 | Table 140.3-B Walls - Mass, Heavy (2025) | 0.211 | 0.36304 | 0.36304 | 0.36304 | 0.36304 | 0.36304 | 0.36304 | 0.36304 | 0.36304 | 0.36304 | 0.16 | 0.21 | 0.18 | 0.16 | 0.16 | 0.15
External Wall (Floors 2-5) | ApartmentMidRise | ExtWall_WoodFramed_Res | Wood framed walls: Wood frame + insulation + Gypsum board | U-factor IP | Pre 1978 | N/A | Using ASHRAE 90.1, 2022 Table A3.4.3.1, 3.5", R-1.5 and a 7.7% cumulative wall renovation rate through 2028, based on the average annual rate from CBECS 2003 and 2012 projected over 48 years. | 0.19099 | 0.19099 | 0.19099 | 0.19099 | 0.19099 | 0.19099 | 0.19099 | 0.19099 | 0.19099 | 0.19099 | 0.18968 | 0.19099 | 0.19099 | 0.18968 | 0.18968 | 0.18968
[5 empty] | 1978-1997 | 1986 | Title 24 1986 Table 2-53 BB, wall density less than 25 | 0.095 | 0.095 | 0.095 | 0.095 | 0.095 | 0.095 | 0.095 | 0.095 | 0.095 | 0.095 | 0.095 | 0.095 | 0.095 | 0.095 | 0.095 | 0.095
[5 empty] | 1998-2007 | 2001 | TABLE 1-I wood frame (2001 high-rise residential). CZ1 and CZ16 = 0.063. | 0.063 | 0.084 | 0.092 | 0.092 | 0.092 | 0.092 | 0.092 | 0.092 | 0.092 | 0.084 | 0.084 | 0.084 | 0.084 | 0.084 | 0.084 | 0.063
[5 empty] | 2008-2018 | 2013 | TABLE 140.3-C Wood-framed and Other (2013 high-rise residential). Not 140.3-B and not Mass, Heavy (F2-5 construction is wood). | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.042 | 0.059 | 0.059 | 0.042 | 0.042 | 0.042
[5 empty] | Existing |  | Weighted average of all 4 vintages | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 2019+ | 2025 | TABLE 170.2-A framed (wood, metal) and other — >1-hr fire rating | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.065 | 0.065 | 0.059 | 0.059 | 0.059 | 0.051 | 0.059 | 0.059 | 0.051 | 0.051 | 0.051
Roof | ApartmentMidRise | FlatRoof_WoodFramedAndOther_Res | wood deck roof: Roof membrane or shingles + roof insulation + wood decking/sheathing + wood framing | U-factor IP | Pre 1978 | N/A | Considering 30 years for roof/ insulation replacement. | 0.037 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037
[5 empty] | 1978-1997 | N/A |  | 0.037 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037
[5 empty] | 1998-2007 | 2001 | TABLE 1-I | 0.037 | 0.037 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037
[5 empty] | 2008-2018 | 2013 | TABLE 140.3-C | 0.034 | 0.028 | 0.039 | 0.028 | 0.039 | 0.039 | 0.039 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028
[5 empty] | Existing |  | Weighted average of all 4 vintages | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 2019+ | 2025 | TABLE 170.2-A ENVELOPE COMPONENT PACKAGE – Multifamily Standard Building Design | 0.028 | 0.028 | 0.034 | 0.028 | 0.034 | 0.034 | 0.039 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028
Windows_Dwelling Units (Floors 2-5) | ApartmentMidRise | FixedAndOperableWindow_Res | 100% single pane for Pre-1978 and 1978-1997 (as-built). Title 24 fenestration U/SHGC starts at 1998-2007 (2001 Tables 1-H / 1-I). | U factor | Pre 1978 | N/A | ASHRAE Handbook of Fundamentals Ch. 15 Table 4: U 1.12 (fixed metal) / 1.23 (operable). Weighted with Envelope $C$56 operable fraction. No 2013 double-pane blend. | 1.1475 | 1.1475 | 1.1475 | 1.1475 | 1.1475 | 1.1475 | 1.1475 | 1.1475 | 1.1475 | 1.1475 | 1.1475 | 1.1475 | 1.1475 | 1.1475 | 1.1475 | 1.1475
[5 empty] | 1978-1997 | N/A |  | 1.1475 | 1.1475 | 1.1475 | 1.1475 | 1.1475 | 1.1475 | 1.1475 | 1.1475 | 1.1475 | 1.1475 | 1.1475 | 1.1475 | 1.1475 | 1.1475 | 1.1475 | 1.1475
|  |  | Double pane |  | 1998-2007 | 2001 | Table 1-I | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49
[5 empty] | 2008-2018 | 2013 | Table 140.3-C | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385
[5 empty] | Existing |  | Weighted average of all 4 vintages | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 2019+ | 2025 | TABLE 170.2-A All Other Fenestration (not fixed/operable blend) | 0.28 | 0.3 | 0.28 | 0.28 | 0.28 | 0.34 | 0.34 | 0.3 | 0.3 | 0.3 | 0.28 | 0.3 | 0.28 | 0.28 | 0.28 | 0.28
|  |  | 100% single pane for Pre-1978 and 1978-1997 (as-built). Title 24 fenestration U/SHGC starts at 1998-2007 (2001 Tables 1-H / 1-I). | SHGC | Pre 1978 | N/A | ASHRAE Handbook of Fundamentals Ch. 15 Table 10: SHGC 0.79 (fixed) / 0.78 (operable). Weighted with Envelope $C$56. No 2013 double-pane blend. | 0.7875 | 0.7875 | 0.7875 | 0.7875 | 0.7875 | 0.7875 | 0.7875 | 0.7875 | 0.7875 | 0.7875 | 0.7875 | 0.7875 | 0.7875 | 0.7875 | 0.7875 | 0.7875
[5 empty] | 1978-1997 | N/A |  | 0.7875 | 0.7875 | 0.7875 | 0.7875 | 0.7875 | 0.7875 | 0.7875 | 0.7875 | 0.7875 | 0.7875 | 0.7875 | 0.7875 | 0.7875 | 0.7875 | 0.7875 | 0.7875
|  |  | Double pane |  | 1998-2007 | 2001 | TABLE 1-I 21-30% WWR (prototype 22%). Non-north row 116; CZ1 uses north (row 117) per Table 1-I note. | 0.36 | 0.4 | 0.61 | 0.61 | 0.61 | 0.61 | 0.61 | 0.61 | 0.61 | 0.4 | 0.4 | 0.4 | 0.4 | 0.43 | 0.43 | 0.47
[5 empty] | 2008-2018 | 2013 | Table 140.3-C | 0.2425 | 0.2425 | 0.2425 | 0.2425 | 0.2425 | 0.2425 | 0.2425 | 0.2425 | 0.2425 | 0.2425 | 0.2425 | 0.2425 | 0.2425 | 0.2425 | 0.2425 | 0.2425
[5 empty] | Existing |  | Weighted average of all 4 vintages | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 2019+ | 2025 | TABLE 170.2-A All Other Fenestration RSHGC (NR in CZ1, 3, 5, 16), for those excluded climate zones, an SHGC of 0.6 was assumed (greater than other CZs) | 0.6 | 0.23 | 0.6 | 0.23 | 0.6 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.6
Windows_Nonres (Floor 1) | ApartmentMidRise | FixedWindow_NonRes | 100% single pane for Pre-1978 and 1978-1997 (as-built). Title 24 fenestration U/SHGC starts at 1998-2007 (2001 Tables 1-H / 1-I). | U factor | Pre 1978 | N/A | ASHRAE Handbook of Fundamentals Ch. 15 Table 4: U-1.12 (100% fixed metal, Nonres). No 2013 double-pane blend. | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12
[5 empty] | 1978-1997 | N/A |  | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12
|  |  | Double pane |  | 1998-2007 | 2001 | Table 1-H window U-factor (2001). CZ3-9 = 0.81; other CZs = 0.49. Values from Envelope row 85. | 0.49 | 0.49 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36
[5 empty] | Existing |  | Weighted average of all 4 vintages | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.34 | 0.36 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.36
|  |  | 100% single pane for Pre-1978 and 1978-1997 (as-built). Title 24 fenestration U/SHGC starts at 1998-2007 (2001 Tables 1-H / 1-I). | SHGC | Pre 1978 | N/A | ASHRAE Handbook of Fundamentals Ch. 15 Table 10: SHGC 0.79 (100% fixed, Nonres). No 2013 double-pane blend. | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79
[5 empty] | 1978-1997 | N/A |  | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79
|  |  | Double pane |  | 1998-2007 | 2001 | Table 1-H 21-30% WWR (prototype 22%). Non-north row 120; CZ1 uses north (row 121) per Table 1-H note. | 0.43 | 0.47 | 0.61 | 0.61 | 0.61 | 0.61 | 0.61 | 0.61 | 0.61 | 0.47 | 0.47 | 0.47 | 0.47 | 0.47 | 0.47 | 0.47
[5 empty] | 2008-2018 | 2013 | Table 140.3-B (100% fixed, 0% operable) | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
[5 empty] | Existing |  | Weighted average of all 4 vintages | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 2019+ | 2025 | Table 140.3-B (100% fixed, 0% operable) | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.22 | 0.25 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.25
* Based on PNNL scorecard assumption.
Infiltration
|  |  | Building | Zones | Vintage | Source | Res/NR | ACH50
|  | Infiltration | ApartmentMidRise |  | Pre 1978 | DOE reference buildings (pre/post 1980 | All | 3.97
1978-1997
1998-2007
2008-2018
[5 empty] | Existing |  | Same as all the vintages | 3.97
[5 empty] | 2019+ | 2027 Nonresidential and Multifamily ACM, §6.6 / §6.6.1 | Res | 2.3
[5 empty] | 2019+ |  | NR | 7
Multifamily infiltration is modeled differently compared to other nonresidential models. Specifically, according to 2025 Nonresidentail and Multifamily ACM, infiltration is modeled per ACH 50 metrics.
-
Pre-1978 exterior wall U value calculation:
External Wall (Floor 1) | ApartmentMidRise | ExtWall_MassHeavy_Nonres | 8-in cast-in-place concrete wall + insulation + air/water barrier + exterior cladding + gypsum board Insulation only where the vintage U-factor requires it; Pre-1978 is uninsulated (Appendix A R-0). | U-factor IP | Pre 1978 | N/A | ASHRAE 90.1‑2022, Table A3.1‑1: R‑0 wall (U = 0.74 for concrete); using U = 5.523 for stucco, U = 1.746 for gypsum board, and U=1.54 for Air - Metal Wall Framing | 0.36304 | 0.36304 | 0.36304 | 0.36304 | 0.36304 | 0.36304 | 0.36304 | 0.36304 | 0.36304 | 0.36304 | 0.36304 | 0.36304 | 0.36304 | 0.36304 | 0.36304 | 0.36304
[7 empty] | T24, 2008 (U value): Heavy mass Nonres | 0.253 | 0.36304 | 0.36304 | 0.36304 | 0.36304 | 0.36304 | 0.36304 | 0.36304 | 0.36304 | 0.36304 | 0.184 | 0.253 | 0.211 | 0.184 | 0.184 | 0.16
[7 empty] | Renovation rate since 1980 | 7.7%
External Wall (Floors 2-5) | ApartmentMidRise | ExtWall_WoodFramed_Res | Wood-frame walls + insulation + Gypsum board | U-factor IP | Pre 1978 | N/A | ASHRAE 90.1, 2022 Table A3.4.3.1, 3.5", R-0 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292
[7 empty] | T24 ( 2008) Wood framed Res | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.042 | 0.059 | 0.059 | 0.042 | 0.042 | 0.042
[7 empty] | ASHRAE 90.1, 2022 Table A3.4.3.1, 3.5", R-1.5 | 0.202 | 0.202 | 0.202 | 0.202 | 0.202 | 0.202 | 0.202 | 0.202 | 0.202 | 0.202 | 0.202 | 0.202 | 0.202 | 0.202 | 0.202 | 0.202
[7 empty] | Renovation rate since 1980 | 7.7%
Background Data [To be deleted prior to publication]
External Wall (Floor 1) | ApartmentMidRise | ExtWall_MassHeavy_Nonres | 8-in cast-in-place concrete wall + insulation + air/water barrier + exterior cladding + gypsum board Insulation only where the vintage U-factor requires it; Pre-1978 is uninsulated (Appendix A R-0). | U-factor IP | Pre 1978 | N/A | 90.1 Table A3.1-1, 8 in. NWC 145 pcf solid, No Framing R-0: U-0.740. using U = 5.523 for stucco and U = 1.746 for gypsum board. | 0.47503 | 0.47503 | 0.47503 | 0.47503 | 0.47503 | 0.47503 | 0.47503 | 0.47503 | 0.47503 | 0.47503 | 0.47503 | 0.47503 | 0.47503 | 0.47503 | 0.47503 | 0.47503
[5 empty] | 1978-1997 | 1992 | Same as 1992. No direct regulation was found in 1986 for concrete walls. Also, T24, 1986, Table 2-53B and Equation 2-53E presents U-factors more than the previous vintage (for wall density of >81 lb/ft² & Degree day<3000). | 0.36 | 0.65 | 0.65 | 0.65 | 0.65 | 0.69 | 0.69 | 0.69 | 0.69 | 0.69 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | 0.36
External Wall (Floors 2-5) | ApartmentMidRise | ExtWall_WoodFramed_Res | Wood-frame walls + insulation + Gypsum board | U-factor IP | Pre 1978 | N/A | ASHRAE 90.1 Table A3.4.3.1, 3.5", R-0 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292
[5 empty] | 1978-1997 | 1986 | Title 24 1986 Table 2-53 BB, wall density less than 25 | 0.095 | 0.095 | 0.095 | 0.095 | 0.095 | 0.095 | 0.095 | 0.095 | 0.095 | 0.095 | 0.095 | 0.095 | 0.095 | 0.095 | 0.095 | 0.095
Percentage of operable to fix windows |  | 25% |  |  |  |  | Operable fraction weights older-vintage window U/SHGC only. Natural ventilation is not modeled. Dwelling outdoor air is mechanical Eq 160.2-B.
|  |  |  | Existing stock infiltration assumptions | Perimeter | 846 |  | ft
[5 empty] | Area | 22620 |  | ft2
Stories = 5 → total height = 50 ft (10 ft/floor)
Wall area = 846 × 50 = 42,300 ft² (= 3,929.80 m²)
Roof area = 22,620 ft² (= 2,101.47 m²)
Exterior area (walls + roof) = 64,920 ft² (= 6,031.27 m²)
Volume (with updated footprint): 22,620 × 50 = 1,131,000 ft³ (= 32,026.35 m³)
[5 empty] | Q=0.001133×6,031.27=6.833 m3/s (≈ 14,479 cfm) |  |  | Reference: DOE Commercial Reference Building: Flow per Exterior Surface Area {m3/s-m2}
[5 empty] | ACH (natural/operational) | ACH=Q×3600​/V |  | Walls + roof: 0.768 h−1
[5 empty] | ACH₅₀ (at 50 Pa) | ACH50​=ACHnat​*(50/4​)^0.65 |  | 3.97 h−1
Windows_Dwelling Units | Mid-Rise Apartment | Fixed Windows | U factor |  | Pre 1978 | N/A
[5 empty] | 1978-1997 | 1984
[5 empty] | 1998-2007 | 2001 |  |  | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49
[5 empty] | 2008-2018 | 2013 |  |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36
[5 empty] | 2019+ | 2025 |  |  | 0.28 | 0.3 | 0.28 | 0.28 | 0.28 | 0.34 | 0.34 | 0.3 | 0.3 | 0.3 | 0.28 | 0.3 | 0.28 | 0.28 | 0.28 | 0.28
|  |  | SHGC |  | Pre 1978 | N/A
[5 empty] | 1978-1997 | 1984
[5 empty] | 1998-2007 | 2001 |  | TABLE 1-I (50% north with WWR 20-30% + 50% non north with WWR 30-40% ) | 0.385 | 0.33 | 0.435 | 0.435 | 0.435 | 0.46 | 0.46 | 0.46 | 0.46 | 0.33 | 0.33 | 0.33 | 0.33 | 0.345 | 0.345 | 0.385
[5 empty] | 2008-2018 | 2013 |  |  | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
[5 empty] | 2019+ | 2025 |  |  | 0.63 | 0.23 | 0.63 | 0.23 | 0.63 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.63
Windows_ Nonres |  |  | U factor |  | Pre 1978 | N/A
[5 empty] | 1978-1997 | 1984
[5 empty] | 1998-2007 | 2001 |  |  | 0.49 | 0.49 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49
[5 empty] | 2008-2018 | 2013 |  |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36
[5 empty] | 2019+ | 2025 |  |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.34 | 0.36 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.36
|  |  | SHGC |  | Pre 1978 | N/A
[5 empty] | 1978-1997 | 1984
[5 empty] | 1998-2007 | 2001 |  |  | 0.45 | 0.39 | 0.51 | 0.51 | 0.51 | 0.475 | 0.475 | 0.475 | 0.475 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.45
[5 empty] | 2008-2018 | 2013 |  |  | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
[5 empty] | 2019+ | 2025 |  |  | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.22 | 0.25 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.25
Windows_Dwelling Units |  | Operable Windows | U factor |  | Pre 1978 | N/A
[5 empty] | 1978-1997 | 1984
[5 empty] | 1998-2007 | 2001 |  |  | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49
[5 empty] | 2008-2018 | 2013 |  |  | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46
[5 empty] | 2019+ | 2025 |  |  | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46
|  |  | SHGC |  | Pre 1978 | N/A
[5 empty] | 1978-1997 | 1984
[5 empty] | 1998-2007 | 2001 |  | TABLE 1-I (50% north with WWR 20-30% + 50% non north with WWR 30-40%) | 0.385 | 0.33 | 0.435 | 0.435 | 0.435 | 0.46 | 0.46 | 0.46 | 0.46 | 0.33 | 0.33 | 0.33 | 0.33 | 0.345 | 0.345 | 0.385
[5 empty] | 2008-2018 | 2013 |  |  | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22
[5 empty] | 2019+ | 2025 |  |  | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22
Windows_ Nonres |  |  | U factor |  | Pre 1978 | N/A
[5 empty] | 1978-1997 | 1984
[5 empty] | 1998-2007 | 2001 |  | TABLE 1-H (50% north with WWR 20-30% + 50% non north with WWR 30-40% ) | 0.49 | 0.49 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49
[5 empty] | 2008-2018 | 2013 |  |  | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46
[5 empty] | 2019+ | 2025 |  |  | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46
|  |  | SHGC |  | Pre 1978 | N/A
[5 empty] | 1978-1997 | 1984
[5 empty] | 1998-2007 | 2001 |  | TABLE 1-H (50% north with WWR 20-30% + 50% non north with WWR 30-40% ) | 0.45 | 0.39 | 0.51 | 0.51 | 0.51 | 0.475 | 0.475 | 0.475 | 0.475 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.45
[5 empty] | 2008-2018 | 2013 |  |  | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22
[5 empty] | 2019+ | 2025 |  |  | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22
High-rise/Hotel | 2001 | Windows | North | 20-30% WWR | RSHGC | 2001 |  | TABLE 1-I | 0.47 | 0.4 | 0.61 | 0.61 | 0.61 | 0.61 | 0.61 | 0.61 | 0.61 | 0.4 | 0.4 | 0.4 | 0.4 | 0.43 | 0.43 | 0.47
High-rise/Hotel | 2001 | Windows | NonNorth | 20-30% WWR | RSHGC | 2001 |  | TABLE 1-I | 0.36 | 0.31 | 0.31 | 0.31 | 0.31 | 0.36 | 0.36 | 0.36 | 0.36 | 0.31 | 0.31 | 0.31 | 0.31 | 0.26 | 0.26 | 0.36
High-rise/Hotel | 2001 | Windows | NonNorth | 30-40% WWR | RSHGC | 2001 |  | TABLE 1-I | 0.3 | 0.26 | 0.26 | 0.26 | 0.26 | 0.31 | 0.31 | 0.31 | 0.31 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.3
Nonres | 2001 | Windows | North | 20-30% WWR | RSHGC | 2001 |  | TABLE 1-H | 0.47 | 0.47 | 0.61 | 0.61 | 0.61 | 0.61 | 0.61 | 0.61 | 0.61 | 0.47 | 0.47 | 0.47 | 0.47 | 0.47 | 0.47 | 0.47
Nonres | 2001 | Windows | NonNorth | 20-30% WWR | RSHGC | 2001 |  | TABLE 1-H | 0.43 | 0.36 | 0.41 | 0.41 | 0.41 | 0.39 | 0.39 | 0.39 | 0.39 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.43
Nonres | 2001 | Windows | NonNorth | 30-40% WWR | RSHGC | 2001 |  | TABLE 1-H | 0.43 | 0.31 | 0.41 | 0.41 | 0.41 | 0.34 | 0.34 | 0.34 | 0.34 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.43
Guest room |  |  |  |  | SHGC | 2001 |  | 45% of north+10% of east and west + 45% of west | 0.3825 | 0.328 | 0.4225 | 0.4225 | 0.4225 | 0.45 | 0.45 | 0.45 | 0.45 | 0.328 | 0.328 | 0.328 | 0.328 | 0.3365 | 0.3365 | 0.3825
Guest room |  |  |  |  | SHGC | 2001 |  | 45% of north+10% of east and west + 45% of west | 0.448 | 0.387 | 0.5 | 0.5 | 0.5 | 0.4665 | 0.4665 | 0.4665 | 0.4665 | 0.387 | 0.387 | 0.387 | 0.387 | 0.387 | 0.387 | 0.448

## HVAC System
HVAC system - ApartmentMidRise
Vintage | Space Type | Heating | Cooling | Air Distribution | Source
Existing | Residential Tenant and common | SZAC (Furnace) | SZAC (DX) | CAV | ResStock 2022 & T24 (2008, 2013)
| Non-Residential Tenant (Retail) | PVAV (Gas Boiler & hot water reheat) | PVAV (DX) | VAV | ResStock 2022 & T24 (2008, 2013)
New Construction | Residential Tenant and common | SZHP (DX) | SZHP (DX) | CAV | T24 2025 | ACM 2025 Table 26: dwelling units (>3 habitable floors) SZHP CAV, no economizer; CZ2-15 electric-resistance supplemental heat; CZ1/16 gas furnace supplemental. Common areas are a separate Table 26 row (economizer language differs). Tenant vs common not split into two HVAC rows this pass.
| Non-Residential Tenant (Retail) | PVAV (Gas Boiler & hot water reheat) | PVAV (DX) | VAV
*Based on NR ACM 2025 - Table 26
Efficiency of HVAC system (Efficiency is capacity-dependent. The following table provides a general estimate of system efficiency based on preliminary simulations in one climate zone, or assuming cooling load based on rule of thumb)
Vintage | Upgrade/Installed year | Heating | Cooling | Source
Pre 1978 | 2008 | Efficiency 80% (78% AFUE) | EER=9 (<65,000 Btu/h) RES SEER: 13 | T24, 2008 / 10 CFR Part 430, §430.32(c)(2)
1978-1997
1998-2007
2008-2018 | 2013 | Efficiency 80% (78% AFUE) | EER=9 (<65,000 Btu/h) RES: SEER 13 (<65k) | CFR Energy 2010:Title 10- Table 9
New Construction | 2025 | RES: HSPF2:7.5 For SZHPDF: Furnace efficiency: 80% | SEER2: 14.3 | Title 20, 2023 Table E-6
|  | Non-Res: For ≥65k and <135k Btu/h: 11.0 EER and 14.1 IEER Heating (gas boiler) efficiency is not listed and was not invented. Retail NC system remains PVAV with gas boiler (row 6). | 11.0 EER, 14.1 IEER Dual Fuel: 10.8 EER, 13.9 IEER | Title 24, 2025 able 110.2 footnote a
Fan power
Vintage | Approach | System | Total Static Pressure (TSP) (in w.c.) | Fan Efficiency [ACM 2025] | Motor Efficiency | Fan Power Index (W/cfm) | Data Source
Existing | PNNL 90.1-2011, TSP | SZAC CAV, residential tenant and common | 1.33 | 0.65 | ASHRAE 90.1, 2004, Table 10.8 * |  | Fan power formula: PNNL 20405, 2010, section 5.2.2.5 TSP and fan efficiency: PNNL 20405, 2010, Table 5.11, 90.1-04ac values Motor and drive efficiency: ASHRAE 90.1, 2004, Table 10.8 | PNNL 20405, 2010, Table 5.11
|  | VAV, retail supply fans | 5.58
Brake horsepower (bhp) = (Supply cfm × TSP in w.c.) / (6356 × fan efficiency)
Fan power (w/cfm) = (bhp × 746) / ( supply cfm × motor efficiency )
New Construction | ACM 2025 | SZHP, residential tenant and common — indoor-unit fan | TSP = fan power × motor efficiency × fan efficiency × 6356 / 746 | 0.65 | 2025 ACM Table 12 ** | 0.35 | w/cfm: [T24, 2025, Section 140.4(a)3 D] Motor efficiency: [ACM 2025, Table 12]
|  | PVAV, retail (System 5), by supply cfm | TSP = fan power × motor efficiency × fan efficiency × 6356 / 746 |  |  | 0.978 <=5,000; 1.022 <=10,000; 0.964 >10,000 | Fan power index: [ACM 2025, Table 13] Motor efficiency: [ACM 2025, Table 12]
* According to PNNL 20405 section 5.2.2.5, the full-load efficiency of the motor serving the fan is taken from ASHRAE 90.1, 2004, Table 10.8, based on motor nameplate and assuming enclosed motors operating at 1,800 rotations per minute (rpm) Motor nameplate size (bhp) = brake horsepower (bhp) × 1.1 ( using a 10% oversizing factor)
** The full‑load efficiency of the motor serving the fan is taken from ACM 2025 Table 12 based on the motor nameplate horsepower. Brake horsepower (bhp) = (Supply cfm from sizing run × fan power in W/cfm) / 746. Note: 0.35 W/cfm is the indoor-unit fan (T24 2025 §140.4(a)3 D), same allowance as OfficeMedium VRF and Hotel Large four-pipe fan coil. Not an ACM Table 13 system index. Note: HVAC system is PVAV, not System 6. ACM System 5 >10,000 cfm = 0.964 (Hotel Small). >5,000–10,000 cfm = 1.022. At or below 5,000 cfm = 0.978.

## Thermostat
Thermostat Setpoints - ApartmentMidRise : ResidentialLiving
Setpoint | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16 | Source
Heating Setpoint (F) | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | T24 2025 - Appendix 5.4B
Heating Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Cooling Setpoint (F) | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | T24 2025 - Appendix 5.4B
Cooling Setback (F) | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78
Thermostat Setpoints - ApartmentMidRise :Retail
Setpoint | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16 | Source
Heating Setpoint (F) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | T24 2022 - Appendix 5.4B
Heating Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Cooling Setpoint (F) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
Cooling Setback (F) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
Thermostat Setpoints - ApartmentMidRise : ResidentialCommon
Heating Setpoint (F) | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | T24 2025 Appendix 5.4B ResidentialCommon
Heating Setback (F) | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68
Cooling Setpoint (F) | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78
Cooling Setback (F) | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78
Thermostat Setpoints: Ancillary
Heating Setpoint (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Heating Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Cooling Setpoint (F) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
Cooling Setback (F) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
One App 5.4B ResidentialLiving profile (68°F occupied / 60°F hours 1–6 and 23–24). ACM 2025 does not publish a multi-unit thermostat diversity set for this prototype. Stochastic or deep-setback mixes were not added.

## Ventilation
Outdoor Airflow Rate - ApartmentMidRise
Space Thermal Zone | Number of People | Floor Area (ft2) | cfm/person (T24, 2025, Equation 120.1-F and Table 120.1-A) | cfm (whole-dwelling continuous mechanical ventilation rate) Res: Equation 160.2-B | cfm/ft² (T24, 2025, Equation 120.1-F and Table 120.1-A) | Required Exhaust Rate-CFM/ft²- (T24, 2025, Table 120.1-B – Minimum Exhaust Rates) | Total cfm Driven by People | Total cfm Driven by Area | Total cfm Driven by Exhaust | Total cfm | Note
F1 BUSINESS CENTER | 24.0039 | 360.04 | 15 |  | 0.15 |  | 360.058 | 54.006 |  | 360.058
F1 CORRIDOR | 19.2019 | 1920.19 | 15 |  | 0.15 |  | 288.0285 | 288.0285 |  | 288.0285
F1 FITNESS CENTER | 18.0018 | 900.09 | 15 |  | 0.15 |  | 270.027 | 135.0135 |  | 270.027
F1 LEASING OFFICE | 3.4503 | 345.03 | 15 |  | 0.15 |  | 51.7545 | 51.7545 |  | 51.7545
F1 LOUNGE | 70.0417 | 1050.1 | 15 |  | 0.15 |  | 1050.625 | 157.515 |  | 1050.625
F1 MECHANICAL ROOM | 1.2961 | 432.04 | 15 |  | 0.15 |  | 19.4418 | 64.806 |  | 64.806
F1 RETAIL N-NW | 99.7597 | 5985.58 | 15 |  | 0.2 |  | 1496.395 | 1197.116 |  | 1496.395 | Retail merchandise: Table 120.1-A / App 5.4C Retail-Sales Ra = 0.20 cfm/ft².
F1 RETAIL NE | 72.007 | 4320.42 | 15 |  | 0.2 |  | 1080.105 | 864.084 |  | 1080.105
F1 RETAIL SE | 48.0047 | 2880.28 | 15 |  | 0.2 |  | 720.07 | 576.056 |  | 720.07
F1 RETAIL SW | 73.8072 | 4428.43 | 15 |  | 0.2 |  | 1107.1075 | 885.686 |  | 1107.1075
F2-4 1-BED CORE EAST | 12 | 1440.14 | NA | 219.6126 |  |  |  | 219.6126 | 219.6126 | 219.6126 | Eq 160.2-B: 0.03×CFA_total + 7.5×N_units×(N_br+1). Studio N_br=0. CFA_total = zone area × floor multiplier. Natural ventilation is not modeled (operable fraction Envelope C56 is fenestration weighting only).
F2-4 1-BED CORE N | 6 | 720.07 | NA | 109.8063 |  |  |  | 109.8063 | 109.8063 | 109.8063 | Balanced IAQ fan - only applies to new construction
F2-4 1-BED CORE WEST | 12 | 1440.14 | NA | 219.6126 |  |  |  | 219.6126 | 219.6126 | 219.6126 | Balanced IAQ fan - only applies to new construction
F2-4 1-BED NORTH | 30 | 3720.36 | NA | 559.8324 |  |  |  | 559.8324 | 559.8324 | 559.8324 | Balanced IAQ fan - only applies to new construction
F2-4 2-BED CORE NE-NW | 18 | 2160.21 | NA | 329.4189 |  |  |  | 329.4189 | 329.4189 | 329.4189 | Balanced IAQ fan - only applies to new construction
F2-4 2-BED EAST | 27 | 3240.32 | NA | 494.1288 |  |  |  | 494.1288 | 494.1288 | 494.1288 | Balanced IAQ fan - only applies to new construction
F2-4 2-BED WEST | 27 | 3240.32 | NA | 494.1288 |  |  |  | 494.1288 | 494.1288 | 494.1288 | Balanced IAQ fan - only applies to new construction
F2-4 3-BED NE | 12 | 1410.14 | NA | 216.9126 |  |  |  | 216.9126 | 216.9126 | 216.9126 | Balanced IAQ fan - only applies to new construction
F2-4 3-BED NW | 12 | 1410.14 | NA | 216.9126 |  |  |  | 216.9126 | 216.9126 | 216.9126 | Balanced IAQ fan - only applies to new construction
F2-4 CORRIDOR | 77.4075 | 2580.25 | 15 |  | 0.15 |  | 1161.1125 | 387.0375 |  | 1161.1125
F2-4 LAUNDRY | 5.4006 | 180.02 | 15 |  | 0.15 |  | 81.009 | 27.003 |  | 81.009
F2-4 STUDIO SE | 6 | 540.05 | NA | 71.1045 |  |  |  | 71.1045 | 71.1045 | 71.1045 | Balanced IAQ fan - only applies to new construction
F2-4 STUDIO SW | 6 | 540.05 | NA | 71.1045 |  |  |  | 71.1045 | 71.1045 | 71.1045 | Balanced IAQ fan - only applies to new construction
F5 1-BED CORE EAST | 4 | 1440.14 | NA | 73.2042 |  |  |  | 73.2042 | 73.2042 | 73.2042 | Balanced IAQ fan - only applies to new construction
F5 1-BED CORE N | 2 | 720.07 | NA | 36.6021 |  |  |  | 36.6021 | 36.6021 | 36.6021 | Balanced IAQ fan - only applies to new construction
F5 1-BED CORE WEST | 4 | 1440.14 | NA | 73.2042 |  |  |  | 73.2042 | 73.2042 | 73.2042 | Balanced IAQ fan - only applies to new construction
F5 1-BED NORTH | 10 | 3720.36 | NA | 186.6108 |  |  |  | 186.6108 | 186.6108 | 186.6108 | Balanced IAQ fan - only applies to new construction
F5 2-BED CORE NE-NW | 6 | 2160.21 | NA | 109.8063 |  |  |  | 109.8063 | 109.8063 | 109.8063 | Balanced IAQ fan - only applies to new construction
F5 2-BED EAST | 9 | 3240.32 | NA | 164.7096 |  |  |  | 164.7096 | 164.7096 | 164.7096 | Balanced IAQ fan - only applies to new construction
F5 2-BED WEST | 9 | 3240.32 | NA | 164.7096 |  |  |  | 164.7096 | 164.7096 | 164.7096 | Balanced IAQ fan - only applies to new construction
F5 3-BED NE | 4 | 1410.14 | NA | 72.3042 |  |  |  | 72.3042 | 72.3042 | 72.3042 | Balanced IAQ fan - only applies to new construction
F5 3-BED NW | 4 | 1410.14 | NA | 72.3042 |  |  |  | 72.3042 | 72.3042 | 72.3042 | Balanced IAQ fan - only applies to new construction
F5 CORRIDOR | 25.8025 | 2580.25 | 15 |  | 0.15 |  | 387.0375 | 387.0375 |  | 387.0375
F5 LAUNDRY | 1.8002 | 180.02 | 15 |  | 0.15 |  | 27.003 | 27.003 |  | 27.003
F5 STUDIO SE | 2 | 540.05 | NA | 23.7015 |  |  |  | 23.7015 | 23.7015 | 23.7015 | Balanced IAQ fan - only applies to new construction
F5 STUDIO SW | 2 | 540.05 | NA | 23.7015 |  |  |  | 23.7015 | 23.7015 | 23.7015 | Balanced IAQ fan - only applies to new construction
PARKING GARAGE | 0 | 27902.72 | 0 |  | 0 | 0.75 | 0 | 0 | 20927.04 | 20927.04 | Parking garage: Table 120.1-B exhaust 0.75 cfm/ft² only. Person and area OA removed (App 5.4C Exhaust - Parking garages).

## Water Heater
Water Heater - ApartmentMidRise
Vintage | WH Type | Efficiency | Number of WH | Tank volume (gal) | Tank loss | Source | Note
Existing | Gas consumer storage (in-unit) | 0.8 | 88 | See Existing in-unit CZ table, col F (gal/unit); building = 88 x F | 0.653 | C3 is recovery efficiency (input = capacity / RE). F3 is the 10 CFR 430.32 high-draw UEF for the CZ tank size (col F). CZ columns: G = standby loss %/hr = I / (0.0834 × F); I = tank UA (Btu/h·°F) from the Maguire & Roberts 2020 UEF-to-UA method, used for both off-cycle and on-cycle losses; J is the unit. In SI, UA (W/K) = I × 0.527527 (B140). Not Title 20 Table F-4 and not the DEER commercial HPWH value 4.37. | D3 = 88 in-unit water heaters, one per apartment (dwelling units only, not a central plant). All 88 are the same unit in every CZ: 30 gal / 30,000 Btu/h gas storage (Existing) and 200,000 Btu/h instantaneous (NC), because the smallest catalog size already covers the 3-bed peak. Only the hot water draw differs: 48 studio/1-bed (2 people, 0.36 gal/h), 32 two-bed (3 people, 0.54 gal/h), 8 three-bed (4 people, 0.72 gal/h). The common/retail area adds 1 commercial gas storage heater (Common CZ table), so the building has 89 water heaters.
New Construction | Gas consumer instantaneous (in-unit) | 0.81 | 88 | 0 | n/a
* Individual dwelling-unit water heaters (not central §170.2(d)3 storage + recirculation + solar). 88 units. Existing = consumer storage catalog. NC = ACM §6.11.2 instantaneous. Retail/laundry/amenities = one commercial plant (NR catalog + 75 gal/h minimum).
Peak Hot Water Consumption
Space | Plant (In-unit dwelling vs Common commercial) | Total Area (ft²) | Number of People | Hot Water Usage Specification (gal/hr per person) [T24, 2022, Appendix 5.4A , sheet: "2022 SpaceFuncData-Input"] | Peak Hot Water Usage (gal/hr) | Peak Hot Water Usage (gal/min) | Notes
F1 BUSINESS CENTER | Common | 360.04 | 24.0039 | 0.18 | 4.3207 | 0.072012 | In-unit = dwelling DHW (consumer heater in each apartment). Common = retail/laundry/amenity DHW on a separate commercial plant. Dwelling gal/h-person is 0.18 throughout. Corridor 0, lounge/office 0.09, laundry 0.578 per Jason APTM58 / school App 5.4A kitchen-locker rate.
F1 CORRIDOR | Common | 1920.19 | 19.2019 | 0 | 0 | 0
F1 FITNESS CENTER | Common | 900.09 | 18.0018 | 0.18 | 3.2403 | 0.054005
F1 LEASING OFFICE | Common | 345.03 | 3.4503 | 0.09 | 0.31053 | 0.0051754
F1 LOUNGE | Common | 1050.1 | 70.0417 | 0.09 | 6.3038 | 0.10506
F1 MECHANICAL ROOM | Common | 432.04 | 1.2961 | 0 | 0 | 0
F1 RETAIL N-NW | Common | 5985.58 | 99.7597 | 0.18 | 17.9567 | 0.29928
F1 RETAIL NE | Common | 4320.42 | 72.007 | 0.18 | 12.9613 | 0.21602
F1 RETAIL SE | Common | 2880.28 | 48.0047 | 0.18 | 8.6408 | 0.14401
F1 RETAIL SW | Common | 4428.43 | 73.8072 | 0.18 | 13.2853 | 0.22142
F2-4 1-BED CORE EAST | In-unit | 4320.42 | 12 | 0.18 | 2.16 | 0.036
F2-4 1-BED CORE N | In-unit | 2160.21 | 6 | 0.18 | 1.08 | 0.018
F2-4 1-BED CORE WEST | In-unit | 4320.42 | 12 | 0.18 | 2.16 | 0.036
F2-4 1-BED NORTH | In-unit | 11161.08 | 30 | 0.18 | 5.4 | 0.09
F2-4 2-BED CORE NE-NW | In-unit | 6480.63 | 18 | 0.18 | 3.24 | 0.054
F2-4 2-BED EAST | In-unit | 9720.96 | 27 | 0.18 | 4.86 | 0.081
F2-4 2-BED WEST | In-unit | 9720.96 | 27 | 0.18 | 4.86 | 0.081
F2-4 3-BED NE | In-unit | 4230.42 | 12 | 0.18 | 2.16 | 0.036
F2-4 3-BED NW | In-unit | 4230.42 | 12 | 0.18 | 2.16 | 0.036
F2-4 CORRIDOR | Common | 7740.75 | 77.4075 | 0 | 0 | 0
F2-4 LAUNDRY | Common | 540.06 | 5.4006 | 0.578 | 3.1215 | 0.052026
F2-4 STUDIO SE | In-unit | 1620.15 | 6 | 0.18 | 1.08 | 0.018
F2-4 STUDIO SW | In-unit | 1620.15 | 6 | 0.18 | 1.08 | 0.018
F5 1-BED CORE EAST | In-unit | 1440.14 | 4 | 0.18 | 0.72 | 0.012
F5 1-BED CORE N | In-unit | 720.07 | 2 | 0.18 | 0.36 | 0.006
F5 1-BED CORE WEST | In-unit | 1440.14 | 4 | 0.18 | 0.72 | 0.012
F5 1-BED NORTH | In-unit | 3720.36 | 10 | 0.18 | 1.8 | 0.03
F5 2-BED CORE NE-NW | In-unit | 2160.21 | 6 | 0.18 | 1.08 | 0.018
F5 2-BED EAST | In-unit | 3240.32 | 9 | 0.18 | 1.62 | 0.027
F5 2-BED WEST | In-unit | 3240.32 | 9 | 0.18 | 1.62 | 0.027
F5 3-BED NE | In-unit | 1410.14 | 4 | 0.18 | 0.72 | 0.012
F5 3-BED NW | In-unit | 1410.14 | 4 | 0.18 | 0.72 | 0.012
F5 CORRIDOR | Common | 2580.25 | 25.8025 | 0 | 0 | 0
F5 LAUNDRY | Common | 180.02 | 1.8002 | 0.578 | 1.0405 | 0.017342
F5 STUDIO SE | In-unit | 540.05 | 2 | 0.18 | 0.36 | 0.006
F5 STUDIO SW | In-unit | 540.05 | 2 | 0.18 | 0.36 | 0.006
PARKING GARAGE | Common | 27902.72 | 0 | 0 | 0 | 0
Total | In-unit peak, one dwelling (gal/h) |  |  |  | 0.72 |  | Largest apartment only (3-bed, 0.72 gal/h). Not the sum of all apartments. No 75 gal/h minimum on in-unit heaters.
Total | Common / retail (commercial plant gal/h) |  |  |  | 75 |  | ACM 2025 §5.9.2 minimum peak 75 gal/h applied only if common DHW > 0.
Number of dwelling units | 88 | Prototype A18 / Zones E
Peak gal/h per dwelling unit | 0.72
NC input per dwelling (Btu/h) | 200000 | ACM §6.11.2 consumer instantaneous
NC prototype total input (Btu/h) | 17600000
Design supply temperature (°F) | 135 | T24 2022 Appendix 5.4B
WH system factor | 0.6 | 2025 ACM §5.9.2 Rated Capacity
Water mass conversion (lb/gal) | 8.2877 | 2025 ACM §5.9.2 Rated Capacity
Reheat multiplier | 0.4 | 2025 ACM §5.9.2 Storage Volume
Climate Zone Water Heater Sizing — Existing in-unit consumer storage (per dwelling)
Climate Zone | Minimum Monthly Mains Temp (°F) [T24 2022 - Appendix 5.4B] | Heat Output (Btu/hr) [ACM, 2025, 5.9.2: Rated capacity section] | WH Capacity (Btu/hr) [ACM, 2025, 5.9.2: Rated capacity section] | Required Energy Input (Btu/hr) | Storage Volume (gal) | Standby Loss (%/hr) [= I ÷ (0.0834 × F); UA per Maguire & Roberts 2020. Not Title 20 Table F-4] |  | Off/On Cycle Loss Coefficient to Ambient Temp |  | Source/Note
CZ01 | 47.9 | 519.7382 | 311.8429 | 30000 | 30 | 3.3814 | %/hr | 8.4602 | Btu/h·°F | I is tank UA (Btu/h·°F) from the Maguire & Roberts 2020 UEF-to-UA method at consumer UEF test conditions (inputs in rows 134–140). G = I ÷ (0.0834 × F) %/hr. The same UA applies to off-cycle and on-cycle losses. In SI, UA (W/K) = I × 0.527527 (B140). Not the DEER commercial HPWH UA 4.37 and not Title 20 Table F-4.
CZ02 | 50.8 | 502.4335 | 301.4601 | 30000 | 30 | 3.3814 | %/hr | 8.4602 | Btu/h·°F
CZ03 | 52.2 | 494.0795 | 296.4477 | 30000 | 30 | 3.3814 | %/hr | 8.4602 | Btu/h·°F
CZ04 | 52.7 | 491.096 | 294.6576 | 30000 | 30 | 3.3814 | %/hr | 8.4602 | Btu/h·°F
CZ05 | 51.6 | 497.6598 | 298.5959 | 30000 | 30 | 3.3814 | %/hr | 8.4602 | Btu/h·°F
CZ06 | 56.8 | 466.6307 | 279.9784 | 30000 | 30 | 3.3814 | %/hr | 8.4602 | Btu/h·°F
CZ07 | 58.4 | 457.0832 | 274.2499 | 30000 | 30 | 3.3814 | %/hr | 8.4602 | Btu/h·°F
CZ08 | 58.4 | 457.0832 | 274.2499 | 30000 | 30 | 3.3814 | %/hr | 8.4602 | Btu/h·°F
CZ09 | 57.6 | 461.8569 | 277.1142 | 30000 | 30 | 3.3814 | %/hr | 8.4602 | Btu/h·°F
CZ10 | 57.1 | 464.8405 | 278.9043 | 30000 | 30 | 3.3814 | %/hr | 8.4602 | Btu/h·°F
CZ11 | 50.5 | 504.2237 | 302.5342 | 30000 | 30 | 3.3814 | %/hr | 8.4602 | Btu/h·°F
CZ12 | 51.4 | 498.8532 | 299.3119 | 30000 | 30 | 3.3814 | %/hr | 8.4602 | Btu/h·°F
CZ13 | 51.7 | 497.0631 | 298.2379 | 30000 | 30 | 3.3814 | %/hr | 8.4602 | Btu/h·°F
CZ14 | 50.1 | 506.6105 | 303.9663 | 30000 | 30 | 3.3814 | %/hr | 8.4602 | Btu/h·°F
CZ15 | 63.2 | 428.4409 | 257.0646 | 30000 | 30 | 3.3814 | %/hr | 8.4602 | Btu/h·°F
CZ16 | 41.4 | 558.5247 | 335.1148 | 30000 | 30 | 3.3814 | %/hr | 8.4602 | Btu/h·°F
Climate Zone Water Heater Sizing — New Construction in-unit consumer instantaneous (per dwelling)
Climate Zone | Minimum Monthly Mains Temp (°F) [T24 2022 - Appendix 5.4B] | Heat Output (Btu/hr) [ACM, 2025, 5.9.2: Rated capacity section] | WH Capacity (Btu/hr) [ACM, 2025, 5.9.2: Rated capacity section] | Required Energy Input (Btu/hr) | Storage Volume (gal) | Standby Loss (%/hr) [No storage tank. Not Title 20 Table F-4] |  | Off/On Cycle Loss Coefficient to Ambient Temp |  | Source/Note
CZ01 | 47.9 | 519.7382 | 311.8429 | 200000 | 0 | 0 | %/hr | 0 | Btu/h·°F | ACM §6.11.2 consumer instantaneous: no storage tank (F = 0 gal), so standby loss (G) and tank UA (I) are 0 for both off-cycle and on-cycle losses. G uses the same formula as the Existing table and returns 0 when there is no tank. UEF 0.81 is in C4.
CZ02 | 50.8 | 502.4335 | 301.4601 | 200000 | 0 | 0 | %/hr | 0 | Btu/h·°F
CZ03 | 52.2 | 494.0795 | 296.4477 | 200000 | 0 | 0 | %/hr | 0 | Btu/h·°F
CZ04 | 52.7 | 491.096 | 294.6576 | 200000 | 0 | 0 | %/hr | 0 | Btu/h·°F
CZ05 | 51.6 | 497.6598 | 298.5959 | 200000 | 0 | 0 | %/hr | 0 | Btu/h·°F
CZ06 | 56.8 | 466.6307 | 279.9784 | 200000 | 0 | 0 | %/hr | 0 | Btu/h·°F
CZ07 | 58.4 | 457.0832 | 274.2499 | 200000 | 0 | 0 | %/hr | 0 | Btu/h·°F
CZ08 | 58.4 | 457.0832 | 274.2499 | 200000 | 0 | 0 | %/hr | 0 | Btu/h·°F
CZ09 | 57.6 | 461.8569 | 277.1142 | 200000 | 0 | 0 | %/hr | 0 | Btu/h·°F
CZ10 | 57.1 | 464.8405 | 278.9043 | 200000 | 0 | 0 | %/hr | 0 | Btu/h·°F
CZ11 | 50.5 | 504.2237 | 302.5342 | 200000 | 0 | 0 | %/hr | 0 | Btu/h·°F
CZ12 | 51.4 | 498.8532 | 299.3119 | 200000 | 0 | 0 | %/hr | 0 | Btu/h·°F
CZ13 | 51.7 | 497.0631 | 298.2379 | 200000 | 0 | 0 | %/hr | 0 | Btu/h·°F
CZ14 | 50.1 | 506.6105 | 303.9663 | 200000 | 0 | 0 | %/hr | 0 | Btu/h·°F
CZ15 | 63.2 | 428.4409 | 257.0646 | 200000 | 0 | 0 | %/hr | 0 | Btu/h·°F
CZ16 | 41.4 | 558.5247 | 335.1148 | 200000 | 0 | 0 | %/hr | 0 | Btu/h·°F
Climate Zone Water Heater Sizing and Loss Coefficients — Common / retail commercial plant
Climate Zone | Minimum Monthly Mains Temp (°F) [T24 2022 - Appendix 5.4B] | Heat Output (Btu/hr) [ACM, 2025, 5.9.2: Rated capacity section] | WH Capacity (Btu/hr) [ACM, 2025, 5.9.2: Rated capacity section] | Required Energy Input (Btu/hr) | Storage Volume (gal) | Standby Loss [Title 20, §1605.1 Table F-4; Appendix B: Water Heating Calculation Method] |  | Off/On Cycle Loss Coefficient to Ambient Temp |  | Source/Note
CZ01 | 47.9 | 54139.4002 | 32483.6401 | 60000 | 80 | 1058.8699 | Btu/hr | 15.1267 | Btu/h·°F | G is the Title 20 §1605.1 Table F-4 standby loss (Btu/h); I = G ÷ 70 (Btu/h·°F); J is the unit. In SI, UA (W/K) = I × 0.527527 (B140).
CZ02 | 50.8 | 52336.8255 | 31402.0953 | 60000 | 80 | 1058.8699 | Btu/hr | 15.1267 | Btu/h·°F
CZ03 | 52.2 | 51466.617 | 30879.9702 | 60000 | 80 | 1058.8699 | Btu/hr | 15.1267 | Btu/h·°F
CZ04 | 52.7 | 51155.8282 | 30693.4969 | 60000 | 80 | 1058.8699 | Btu/hr | 15.1267 | Btu/h·°F
CZ05 | 51.6 | 51839.5635 | 31103.7381 | 60000 | 80 | 1058.8699 | Btu/hr | 15.1267 | Btu/h·°F
CZ06 | 56.8 | 48607.3605 | 29164.4163 | 60000 | 80 | 1058.8699 | Btu/hr | 15.1267 | Btu/h·°F
CZ07 | 58.4 | 47612.8365 | 28567.7019 | 60000 | 80 | 1058.8699 | Btu/hr | 15.1267 | Btu/h·°F
CZ08 | 58.4 | 47612.8365 | 28567.7019 | 60000 | 80 | 1058.8699 | Btu/hr | 15.1267 | Btu/h·°F
CZ09 | 57.6 | 48110.0985 | 28866.0591 | 60000 | 80 | 1058.8699 | Btu/hr | 15.1267 | Btu/h·°F
CZ10 | 57.1 | 48420.8872 | 29052.5323 | 60000 | 80 | 1058.8699 | Btu/hr | 15.1267 | Btu/h·°F
CZ11 | 50.5 | 52523.2987 | 31513.9792 | 60000 | 80 | 1058.8699 | Btu/hr | 15.1267 | Btu/h·°F
CZ12 | 51.4 | 51963.879 | 31178.3274 | 60000 | 80 | 1058.8699 | Btu/hr | 15.1267 | Btu/h·°F
CZ13 | 51.7 | 51777.4057 | 31066.4434 | 60000 | 80 | 1058.8699 | Btu/hr | 15.1267 | Btu/h·°F
CZ14 | 50.1 | 52771.9297 | 31663.1578 | 60000 | 80 | 1058.8699 | Btu/hr | 15.1267 | Btu/h·°F
CZ15 | 63.2 | 44629.2645 | 26777.5587 | 60000 | 80 | 1058.8699 | Btu/hr | 15.1267 | Btu/h·°F
CZ16 | 41.4 | 58179.654 | 34907.7924 | 60000 | 80 | 1058.8699 | Btu/hr | 15.1267 | Btu/h·°F
Market data
Consumer gas input (Btu/h) | Input source | NC instantaneous (Btu/h) | NC source | Consumer gas tank (gal) | Tank source | NC tank (gal) | NC tank source | Commercial gas input (Btu/h) | Comm. input source | Commercial gas tank (gal) | Comm. tank source
30000 | Title 20 consumer (≤75 kBtu/h); ENERGY STAR/AHRI common ratings | 200000 | ACM §6.11.2 / 10 CFR 430.32 instantaneous high draw | 30 | Title 20 consumer storage ≥20 and ≤75 gal typical certified sizes | 0 | ACM §6.11.2 tank volume = 0 | 60000 | Grainger / ENERGY STAR Commercial (NR revised-tab catalog) | 80 | Grainger / ENERGY STAR Commercial
32000 | Title 20 consumer (≤75 kBtu/h); ENERGY STAR/AHRI common ratings |  |  | 40 | Title 20 consumer storage ≥20 and ≤75 gal typical certified sizes |  |  | 75000 | Grainger / ENERGY STAR Commercial (NR revised-tab catalog) | 100 | Grainger / ENERGY STAR Commercial
34000 | Title 20 consumer (≤75 kBtu/h); ENERGY STAR/AHRI common ratings |  |  | 50 | Title 20 consumer storage ≥20 and ≤75 gal typical certified sizes |  |  | 100000 | Grainger / ENERGY STAR Commercial (NR revised-tab catalog) | 119 | Grainger / ENERGY STAR Commercial
36000 | Title 20 consumer (≤75 kBtu/h); ENERGY STAR/AHRI common ratings |  |  | 60 | Title 20 consumer storage ≥20 and ≤75 gal typical certified sizes |  |  | 125000 | Grainger / ENERGY STAR Commercial (NR revised-tab catalog) | 120 | Grainger / ENERGY STAR Commercial
38000 | Title 20 consumer (≤75 kBtu/h); ENERGY STAR/AHRI common ratings |  |  | 75 | Title 20 consumer storage ≥20 and ≤75 gal typical certified sizes |  |  | 150000 | Grainger / ENERGY STAR Commercial (NR revised-tab catalog) | 125 | Grainger / ENERGY STAR Commercial
40000 | Title 20 consumer (≤75 kBtu/h); ENERGY STAR/AHRI common ratings | [6 empty] | 199000 | Grainger / ENERGY STAR Commercial (NR revised-tab catalog)
50000 | Title 20 consumer (≤75 kBtu/h); ENERGY STAR/AHRI common ratings | [6 empty] | 250000 | Grainger / ENERGY STAR Commercial (NR revised-tab catalog)
65000 | Title 20 consumer (≤75 kBtu/h); ENERGY STAR/AHRI common ratings | [6 empty] | 300000 | Grainger / ENERGY STAR Commercial (NR revised-tab catalog)
75000 | Title 20 consumer (≤75 kBtu/h); ENERGY STAR/AHRI common ratings | [6 empty] | 399000 | Grainger / ENERGY STAR Commercial (NR revised-tab catalog)
[8 empty] | 500000 | Grainger / ENERGY STAR Commercial (NR revised-tab catalog)
Residential lists exclude commercial boilers (>75 kBtu/h storage), 119 gal commercial HPWH, and the 75 gal/h plant floor. Commercial lists are only for the common/retail plant. E/F pick the next size at or above the ACM calculated value (XLOOKUP match_mode 1).
UEF → UA inputs (Maguire & Roberts 2020)
UEF high-draw daily volume (gal) | 84 | 10 CFR 430 App E high-usage bin
UEF tank setpoint (°F) | 125 | 10 CFR 430 App E / Maguire 2020
UEF inlet temp (°F) | 58 | 10 CFR 430 App E / Maguire 2020
UEF ambient temp (°F) | 67.5 | 10 CFR 430 App E / Maguire 2020
Water density (lb/gal) | 8.2938 | Water property constant for the UEF-to-UA calculation
Water cp (Btu/lb·°F) | 1.0007 | Water property constant for the UEF-to-UA calculation
Btu/h·°F to W/K | 0.52753 | 1 Btu/h·°F = 0.527527 W/K
Background Data [To be deleted prior to publication]
2024 CASE Report: A Comprehensive, High Efficiency Solution for Water Heating in Multifamily Buildings | https://www.energy.ca.gov/sites/default/files/2024-06/CEC-500-2024-054.pdf | 50% central water heating
2022 CASE Report: Multifamily Domestic Hot Water Distribution | https://title24stakeholders.com/wp-content/uploads/2020/09/2022_T24_Final-CASE-Report-MF-DHW-Dist.pdf | 100% central water heating

## Interior Lights
Interior Lighting - ApartmentMidRise
Space Type | New Construction |  |  | Existing
| LPD (W/ft²) | Additional LPD for Portable Lighting (W/ft²) | Source | LPD (W/ft²) | Additional LPD for Portable Lighting (W/ft²) | Source
Convention, Conference, Multipurpose and Meeting Area | 0.75 | 0.125 | T24, 2025, Table 170.2-M (Area category method). Retail merchandise: Table 140.6-C. Additional LPD (C): Table 140.6-C decorative/portable — meeting 0.25, office 0.20, lobby 0.25, retail decorative 0.35. Wall-display W/ft not used (no perimeter takeoff). | 1.2 | 0.2 | T24, 2016, Table 140.6 C (Area category method) Additional LPD (F): 2016 Table 140.6-C footnote 7 decorative 0.20 W/ft² on meeting, office, lobby, and retail.
Corridor Area | 0.4 |  |  | 0.6
Exercise/Fitness Center and Gymnasium Areas | 0.5 |  |  | 1
Office Area (>250 square feet) | 0.6 | 0.1 |  | 0.75 | 0.2
Lobby, Main Entry | 0.7 | 0.125 |  | 0.95 | 0.2
Electrical, Mechanical, Telephone Rooms | 0.4 |  |  | 0.55
Retail Sales Area (Retail Merchandise Sales) | 0.95 | 0.175 |  | 1.2 | 0.2
Laundry Area | 0.45 |  |  | 0.7
Parking Garage Area (Parking Zone and Ramps) | 0.15109 |  |  | 0.16611
Residential Living Spaces | 0.79 |  | CEC 2025 Single-Family ACM Appendix E - Table 2 and 8 | 0.79 |  | CEC 2016 Single-Family ACM Section 2.2.12
*Annual kWh=100+0.1775×CFA (ft²)(Eq. 1)
Daylight-adaptation zone width (ft) | 24
Daylight-adaptation zone depth (ft) — Table 140.6-C / 170.2-M note 2 maximum | 66
Parking LPD is area-weighted with Zones J39: general parking + one two-way entry (24 ft) × 66 ft at daylight-adaptation LPD (NC 1.00 / 2016 0.60).

## Equipment
Equipment - ApartmentMidRise
Vintage | Space Type | Plug load Power Density (W/ft2) | Source
New Construction/Existing | Convention, Conference, Multipurpose and Meeting Area | 1 | Plug load and schedules project with CEC, 2025 Retail Sales RecptPwrDens from T24 2025 Appendix 5.4A (1.0 W/ft²).
| Corridor Area | 0
| Exercise/Fitness Center and Gymnasium Areas | 0.5
| Office Area (>250 square feet) | 1.5
| Lobby, Main Entry | 0.5
| Electrical, Mechanical, Telephone Rooms | 3
| Retail Sales Area (Retail Merchandise Sales) | 1
| Laundry Area | 3
| Parking Garage Area (Parking Zone and Ramps) | 0
| Residential Living Spaces | 0.5 | Plug load and schedules project with CBECC-COM, 2019
Elevator
Vintage | Class | Number of elevators (ne) | Cab Lighting Power Limit (W/ft2) | Fan Power Limit (W/CFM) | Cab Ventilation Fan & Lighting Shutoff | Design Motor Load (W) | Fan Load (W) | Lighting Load (W) | Total (W) | Note
Existing | F/G | 1 | 1.14 | 0.33 | When stopped and unoccupied with doors closed for over 15 minutes, cab interior lighting and ventilation shall be de-energized until required for operation. | 9527.68 | 82.5 | 34.09 | 9644.27 | Design load is calculated according to ISO 25745-2 method using Class F/G. Cab lighting and fan requirements are based on ASHRAE 90.1 2013.
New Construction | E | 1 | 0.6 | 0.33 | When the elevator cab is stopped and unoccupied with doors closed for over 15 minutes, the cab interior lighting and ventilation fans shall be switched off until elevator cab operation resumes. | 5259.96 | 82.5 | 17.94 | 5360.4 | Design load is calculated according to ISO 25745-2 method using Class E. Cab lighting and fan requirements are based on T24 2025 §120.6 (f).
Mid-Rise Apartment Elevator Calculations
Symbol | Definition | Value | Units | Source
E | Annual energy consumption of the elevator - Existing | 19300.7 | kWh/year | Calculated
| Annual energy consumption of the elevator - New Construction | 10655.36 | kWh/year | Calculated
C1 | Running-energy coefficient | 3.65 for Class E; 5.47 for Class F | Coefficient | ISO 25745-2 Table 7
C2 | Idle/standby coefficient | 800 for Class E; 1,600 for Class F | Coefficient | ISO 25745-2 Table 7
Q | Rated load of elevator | 1361 | kg | Assumed for all prototypes
Elevator Size | Cab floor area | 29.9 | ft^2 | W=6.781 ft, L=4.406 ft; assumed based on representative manufacturer
CFM | Cab fan airflow | 250 | cfm | Assumed for multifamily and commercial prototypes
cat | Usage category | 3 | - | ISO 25745-2 Table A.1
d | Operating days per year | 360 | days/year | ISO 25745-2 Table A.1
nf | Number of floors | 5 | floors | Prototype assumptions
h | Floor-to-floor height | 3.05 | m | Prototype assumptions
v | Elevator lift speed | 1.6 | m/s | ISO 25745-2 Table A.1
nd | Number of trips per day | 300 | trips/day | ISO 25745-2 Table A.1
S_pct | Percent of average travel distance | 0.49 | % | ISO 25745-2 Table 2
a | Acceleration | 1 | m/s^2 | Annex B of ISO 25745-2
j | Jerk | 1.25 | m/s^3 | Annex B of ISO 25745-2
td | Door time | 8 | seconds | Annex B of ISO 25745-2
S_av | Average distance traveled per trip | 7.47 | m/trip | Calculated (nf * h * S_pct)
t_av | Average trip time | 15.07 | seconds/trip | Calculated (S_av/v + v/a + a/j + td)
t_nr | Time not running per day | 22.74 | hours/day | Calculated (24 - nd * t_av)
Standby Hours | Annual standby hours | 8307.89 | hours/year | Calculated (24*(365-d)+t_nr*d)
Total light level | Total light level | 40 | lm/ft2 | PNNL Prototypes
EFLH | Equivalent full load hours | 2025.75 | hours | Calculated using the elevator schedule

## Ext Lighting
Exterior Lighting - ApartmentMidRise
Motion Controlled Luminaires (W) | Non-motion Controlled Luminaires (W) | Total (W) | Source
2259.9691 | 1367.7096 | 3627.6788 | T24, 2022 & 2025 2019 Outdoor Lighting CASE report PNNL 90.1-2010 TSD
Exterior Lighting - ApartmentMidRise
Items (Assume LZ2) | Assumptions [2019 Outdoor Lighting CASE Report & PNNL 90.1-2010 TSD] |  | Unit | Lighting Power Allowance [T24, 2025, Table 140.7-A & 140.7-B] | Unit | Exterior Lighting Power (W)
IWA (Initial Wage Allowance) |  |  |  | 200 | (W) | 200
Parking area | 400 ft² for every parking space 1.5 parking spaces per living unit for residential 1 parking space per 360 ft² of gross building area | 84136.3911 | (ft²) | 0.019 | (W/ft²) | 1598.5914
Building Entrance | 5 building entrances: 1 residential lobby + 4 first-floor retail storefronts (Zones). Was 3 from 1 per 10,000 ft² footprint. | 5 | (count) | 15 | (W/ea) | 75
Hardscape Ornamental Light | 0.1 ft² per ft² of gross building area for hardscape ornamental light | 14101.376 | (ft²) | 0.007 | (W/ft²) | 98.7096
Building façade | 0.1 W per ft² of facade area Façade Area = Perimeter × 0.5 × 30 ft (30 ft is the max height that is lit) * The 0.5 factor assumes that only half of the perimeter walls are lit. -Formula is developed based on the 2019 Outdoor Lighting CASE report | 12690 | (ft²) | 0.1 | (W/ft²) | 1269
Non-sales canopy | 0.1 ft² per ft² of one floor. LZ2 non-sales canopy 0.137 W/ft² (Table 140.7-B). Sales canopy would be 0.470 W/ft². | 2820.2752 | (ft²) | 0.137 | (W/ft²) | 386.3777
Motion controlled Luminaires | [5 empty] | 2259.9691
Non-motion-controlled Luminaires | [5 empty] | 1367.7096
Total | [5 empty] | 3627.6788
Perimeter (ft) | 846
Total floor area (ft²) | 141013.76
Floors (above floor) | 5
Number of dwelling units | 88

## Schedules
Schedules - ApartmentMidRise
Zone | Schedule Category | Schedule | Source | Day | Hour
[5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Living Area | ResidentialLiving | Occupancy | T24 2022 - Appendix 5.4B [ResidentialLiving] | Weekday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.8 | 0.9 | 0.9
|  |  |  | Saturday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.8 | 0.9 | 0.9
|  |  |  | Sunday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.8 | 0.9 | 0.9
Living Area | ResidentialLiving | Lights | T24 2022 - Appendix 5.4B [ResidentialLiving] | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.45 | 0.45 | 0.45 | 0.45 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3
|  |  |  | Saturday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.45 | 0.45 | 0.45 | 0.45 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3
|  |  |  | Sunday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.45 | 0.45 | 0.45 | 0.45 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3
Living Area | ResidentialLiving | ElecEquipment | T24 2022 - Appendix 5.4B [ResidentialLiving] | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.45 | 0.45 | 0.45 | 0.45 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3
|  |  |  | Saturday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.45 | 0.45 | 0.45 | 0.45 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3
|  |  |  | Sunday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.45 | 0.45 | 0.45 | 0.45 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3
Living Area | ResidentialLiving | HVACAvail | T24 2022 - Appendix 5.4B [ResidentialLiving] | Weekday | bar: Hour 1 to Hour 24
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
Living Area | ResidentialLiving | ServiceHotWater | T24 2022 - Appendix 5.4B [ResidentialLiving] | Weekday | 0.131 | 0.075 | 0.084 | 0.103 | 0.187 | 0.411 | 0.832 | 1 | 0.832 | 0.617 | 0.486 | 0.355 | 0.336 | 0.308 | 0.299 | 0.243 | 0.393 | 0.449 | 0.486 | 0.439 | 0.393 | 0.364 | 0.336 | 0.206
|  |  |  | Saturday | 0.217 | 0.12 | 0.108 | 0.096 | 0.181 | 0.277 | 0.313 | 0.566 | 0.928 | 1 | 0.892 | 0.735 | 0.614 | 0.518 | 0.47 | 0.47 | 0.627 | 0.699 | 0.675 | 0.627 | 0.566 | 0.53 | 0.482 | 0.337
|  |  |  | Sunday | 0.217 | 0.12 | 0.108 | 0.096 | 0.181 | 0.277 | 0.313 | 0.566 | 0.928 | 1 | 0.892 | 0.735 | 0.614 | 0.518 | 0.47 | 0.47 | 0.627 | 0.699 | 0.675 | 0.627 | 0.566 | 0.53 | 0.482 | 0.337
Living Area | ResidentialLiving | GasEquipment | T24 2022 - Appendix 5.4B [ResidentialLiving] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0
Living Area | ResidentialLiving | HtgSetpt | T24 2022 - Appendix 5.4B [ResidentialLiving] | Weekday | 60 | 60 | 60 | 60 | 60 | 60 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 60 | 60
|  |  |  | Saturday | 60 | 60 | 60 | 60 | 60 | 60 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 60 | 60
|  |  |  | Sunday | 60 | 60 | 60 | 60 | 60 | 60 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 60 | 60
Living Area | ResidentialLiving | ClgSetpt | T24 2022 - Appendix 5.4B [ResidentialLiving] | Weekday | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78
|  |  |  | Saturday | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78
|  |  |  | Sunday | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78
Living Area | ResidentialLiving | Infiltration | T24 2022 - Appendix 5.4B [ResidentialLiving] | Weekday | bar: Hour 1 to Hour 24
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
Living Area | ResidentialLiving | Refrigeration | T24 2022 - Appendix 5.4B [ResidentialLiving] | Weekday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Saturday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Sunday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
Common Use Area
Common Use Area | ResidentialCommon | Occupancy | T24 2022 - Appendix 5.4B [ResidentialCommon] | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.45 | 0.45 | 0.45 | 0.45 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3
|  |  |  | Saturday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.45 | 0.45 | 0.45 | 0.45 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3
|  |  |  | Sunday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.45 | 0.45 | 0.45 | 0.45 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3
Common Use Area | ResidentialCommon | Lights | T24 2022 - Appendix 5.4B [ResidentialCommon] | Weekday | bar: Hour 1 to Hour 24
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
Common Use Area | ResidentialCommon | ElecEquipment | T24 2022 - Appendix 5.4B [ResidentialCommon] | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.45 | 0.45 | 0.45 | 0.45 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3
|  |  |  | Saturday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.45 | 0.45 | 0.45 | 0.45 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3
|  |  |  | Sunday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.45 | 0.45 | 0.45 | 0.45 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3
Common Use Area | ResidentialCommon | ServiceHotWater | T24 2022 - Appendix 5.4B [ResidentialCommon] | Weekday | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.8 | 0.7 | 0.5 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.6 | 0.7 | 0.7 | 0.4 | 0.25 | 0.2 | 0.2 | 0.05 | 0.05
|  |  |  | Saturday | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.8 | 0.7 | 0.5 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.6 | 0.7 | 0.7 | 0.4 | 0.25 | 0.2 | 0.2 | 0.05 | 0.05
|  |  |  | Sunday | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.8 | 0.7 | 0.5 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.6 | 0.7 | 0.7 | 0.4 | 0.25 | 0.2 | 0.2 | 0.05 | 0.05
Common Use Area | ResidentialCommon | GasEquipment | T24 2022 - Appendix 5.4B [ResidentialCommon] | Weekday | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.5 | 0.1 | 0.1 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.5 | 0.1 | 0.1 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.5 | 0.1 | 0.1 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0 | 0 | 0 | 0
Common Use Area | ResidentialCommon | HVACAvail | T24 2022 - Appendix 5.4B [ResidentialCommon] | Weekday | bar: Hour 1 to Hour 24
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
Common Use Area | ResidentialCommon | HtgSetpt | T24 2022 - Appendix 5.4B [ResidentialCommon] | Weekday | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68
|  |  |  | Saturday | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68
|  |  |  | Sunday | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68
Common Use Area | ResidentialCommon | ClgSetpt | T24 2022 - Appendix 5.4B [ResidentialCommon] | Weekday | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78
|  |  |  | Saturday | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78
|  |  |  | Sunday | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78
Common Use Area | ResidentialCommon | Infiltration | T24 2022 - Appendix 5.4B [ResidentialCommon] | Weekday | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  |  | Saturday | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  |  | Sunday | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Common Use Area | ResidentialCommon | Refrigeration | T24 2022 - Appendix 5.4B [ResidentialCommon] | Weekday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Saturday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Sunday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
Retail
Retail | Retail | Occupancy | T24 2022 - Appendix 5.4B [Retail] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0
Retail | Retail | Lights | T24 2022 - Appendix 5.4B [Retail] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.55 | 0.55 | 0.5 | 0.2 | 0.05 | 0.05
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.55 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.4 | 0.4 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Retail | Retail | ElecEquipment | Plug load and schedules project with CEC, 2025 | Weekday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.4 | 0.4 | 0.4
|  |  |  | Saturday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.4 | 0.4
|  |  |  | Sunday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
Retail | Retail | HVACAvail | T24 2022 - Appendix 5.4B [Retail] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
Retail | Retail | ServiceHotWater | T24 2022 - Appendix 5.4B [Retail] | Weekday | 0.04 | 0.05 | 0.05 | 0.04 | 0.04 | 0.04 | 0.04 | 0.15 | 0.23 | 0.32 | 0.41 | 0.57 | 0.62 | 0.61 | 0.5 | 0.45 | 0.46 | 0.47 | 0.42 | 0.34 | 0.33 | 0.23 | 0.13 | 0.08
|  |  |  | Saturday | 0.11 | 0.1 | 0.08 | 0.06 | 0.06 | 0.06 | 0.07 | 0.2 | 0.24 | 0.27 | 0.42 | 0.54 | 0.59 | 0.6 | 0.49 | 0.48 | 0.47 | 0.46 | 0.44 | 0.36 | 0.29 | 0.22 | 0.16 | 0.13
|  |  |  | Sunday | 0.07 | 0.07 | 0.07 | 0.06 | 0.06 | 0.06 | 0.07 | 0.1 | 0.12 | 0.14 | 0.29 | 0.31 | 0.36 | 0.36 | 0.34 | 0.35 | 0.37 | 0.34 | 0.25 | 0.27 | 0.21 | 0.16 | 0.1 | 0.06
Retail | Retail | Infiltration | T24 2022 - Appendix 5.4B [Retail] | Weekday | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1
|  |  |  | Saturday | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1
|  |  |  | Sunday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1
Retail | Retail | Refrigeration | T24 2022 - Appendix 5.4B [Retail] | Weekday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Saturday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Sunday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
Retail | Retail | HtgSetpt | T24 2022 - Appendix 5.4B [Retail] | Weekday | 60 | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 60 | 60 | 60
|  |  |  | Saturday | 60 | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 60 | 60
|  |  |  | Sunday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 60 | 60 | 60 | 60 | 60
Retail | Retail | ClgSetpt | T24 2022 - Appendix 5.4B [Retail] | Weekday | 85 | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 85 | 85 | 85
|  |  |  | Saturday | 85 | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 85 | 85
|  |  |  | Sunday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 85 | 85 | 85 | 85 | 85
Other | [28 empty] | EFLH
| Building | Elevator | T24 2022 - Appendix 5.4B, [LivingResidential] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.69 | 0.43 | 0.37 | 0.43 | 0.58 | 0.48 | 0.37 | 0.37 | 0.46 | 0.62 | 0.2 | 0.12 | 0.04 | 0.04 | 0 | 0 | 2025.75
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.69 | 0.43 | 0.37 | 0.43 | 0.58 | 0.48 | 0.37 | 0.37 | 0.46 | 0.62 | 0.2 | 0.12 | 0.04 | 0.04 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.69 | 0.43 | 0.37 | 0.43 | 0.58 | 0.48 | 0.37 | 0.37 | 0.46 | 0.62 | 0.2 | 0.12 | 0.04 | 0.04 | 0 | 0
| Building | ExtLightingNonMotionCtrl |  | Weekday | bar: Hour 1 to Hour 24
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
| Building | ExtLightingMotionCtrl |  | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Residential | Building | ResidentialSpcPeopleActivityLevel | Based on Activity level schedules in CEC Prototypes | Weekday | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 130 | 130 | 130 | 130 | 140 | 140 | 140 | 140 | 140 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110
|  |  |  | Saturday | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 130 | 130 | 130 | 130 | 140 | 140 | 140 | 140 | 140 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110
|  |  |  | Sunday | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 130 | 130 | 130 | 130 | 140 | 140 | 140 | 140 | 140 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110
Retail | Building | RetailSalePeopleActivityLevel | Based on Activity level schedules in CEC Prototypes | Weekday | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
|  |  |  | Saturday | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
|  |  |  | Sunday | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
MeetingRm | Building | MeetingAreaPeopleActivityLevel | Based on Activity level schedules in CEC Prototypes | Weekday | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2
|  |  |  | Saturday | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2
|  |  |  | Sunday | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2
Office Area (>250 square feet) | Building | FunctionalAreaPeopleActivityLevel | Based on Activity level schedules in CEC Prototypes | Weekday | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
|  |  |  | Saturday | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
|  |  |  | Sunday | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
Corridor, ExcerciseArea, Lobby, MechanicalRM, Stair, Lounge | Building | CommonAreaPeopleActivityLevel | Based on Activity level schedules in CEC Prototypes | Weekday | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5
|  |  |  | Saturday | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5
|  |  |  | Sunday | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5
Ancillary
Mechanical room | Ancillary | Occupancy | T24 2022 - Appendix 5.4B [ResidentialCommon] | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.45 | 0.45 | 0.45 | 0.45 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3
|  |  |  | Saturday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.45 | 0.45 | 0.45 | 0.45 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3
|  |  |  | Sunday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.45 | 0.45 | 0.45 | 0.45 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3
Mechanical room | Ancillary | Lights | T24 2022 - Appendix 5.4B [ResidentialLiving lights profile; ResidentialCommon 1.0 not used for the mechanical room] | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.45 | 0.45 | 0.45 | 0.45 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3
|  |  |  | Saturday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.45 | 0.45 | 0.45 | 0.45 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3
|  |  |  | Sunday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.45 | 0.45 | 0.45 | 0.45 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3
Mechanical room | Ancillary | ElecEquipment | T24 2022 - Appendix 5.4B [ResidentialCommon] | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.45 | 0.45 | 0.45 | 0.45 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3
|  |  |  | Saturday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.45 | 0.45 | 0.45 | 0.45 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3
|  |  |  | Sunday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.45 | 0.45 | 0.45 | 0.45 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3
Mechanical room | Ancillary | ServiceHotWater | T24 2022 - Appendix 5.4B [ResidentialCommon] | Weekday | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.8 | 0.7 | 0.5 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.6 | 0.7 | 0.7 | 0.4 | 0.25 | 0.2 | 0.2 | 0.05 | 0.05
|  |  |  | Saturday | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.8 | 0.7 | 0.5 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.6 | 0.7 | 0.7 | 0.4 | 0.25 | 0.2 | 0.2 | 0.05 | 0.05
|  |  |  | Sunday | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.8 | 0.7 | 0.5 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.6 | 0.7 | 0.7 | 0.4 | 0.25 | 0.2 | 0.2 | 0.05 | 0.05
Mechanical room | Ancillary | HVACAvail | T24 2022 - Appendix 5.4B [ResidentialCommon] | Weekday | bar: Hour 1 to Hour 24
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
Mechanical room | Ancillary | HtgSetpt | T24 2022 - Appendix 5.4B [ResidentialCommon] | Weekday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  |  | Saturday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  |  | Sunday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Mechanical room | Ancillary | ClgSetpt | T24 2022 - Appendix 5.4B [ResidentialCommon] | Weekday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
|  |  |  | Saturday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
|  |  |  | Sunday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
Mechanical room | Ancillary | Infiltration | T24 2022 - Appendix 5.4B [ResidentialCommon] | Weekday | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  |  | Saturday | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  |  | Sunday | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25

## Energy Usage
Energy Consumption - ApartmentMidRise
Prototype | CZ | Total Floorspace (Thousand of ft2) | Electric Energy Intensity (kWh/ft2) | Annual Gas Intensity (kBTU/ft2)
ApartmentMidRise | 1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
Background Data [To be deleted prior to publication]

## Weights
% of Floor Area per CZ and Vintage Bin - ApartmentMidRise
Prototype | CZ | Vintage Bin
|  | Pre-1978 | 1978-1997 | 1998-2007 | 2008-2018 | Not available
ApartmentMidRise | 1 | [5 empty] | 0%
| 2 | [5 empty] | 0%
| 3 | [5 empty] | 0%
| 4 | [5 empty] | 0%
| 5 | [5 empty] | 0%
| 6 | [5 empty] | 0%
| 7 | [5 empty] | 0%
| 8 | [5 empty] | 0%
| 9 | [5 empty] | 0%
| 10 | [5 empty] | 0%
| 11 | [5 empty] | 0%
| 12 | [5 empty] | 0%
| 13 | [5 empty] | 0%
| 14 | [5 empty] | 0%
| 15 | [5 empty] | 0%
| 16 | [5 empty] | 0%
| Statewide | [5 empty] | 0%
Background Data [To be deleted prior to publication]

## PV (hidden)
PV - ApartmentMidRise
TBD

## EV Charger (hidden)
EV Charger - ApartmentMidRise
TBD
Background Data [To be deleted prior to publication]

## Data (hidden)
Space Function | Electric Equipment Load Intensity | Electric Equipment Load Intensity | LPD
Aging Eye/Low-vision (Corridor Area) |  |  | 2013 | 2016 | 2019 | 2025
Aging Eye/Low-vision (Dining)
Aging Eye/Low-vision (Lobby, Main Entry)
Aging Eye/Low-vision (Lounge/Waiting Area)
Aging Eye/Low-vision (Multipurpose Room)
Aging Eye/Low-vision (Religious Worship Area)
Aging Eye/Low-vision (Restroom)
Aging Eye/Low-vision (Stairwell)
Audience Seating Area
Auditorium Area
Auto Repair / Maintenance Area
Barber, Beauty Salon, Spa Area
Civic Meeting Place Area
Classroom, Lecture, Training, Vocational Areas
Concourse and Atria Area
Convention, Conference, Multipurpose and Meeting Area
Copy Room
Corridor Area
Dining Area (Bar/Lounge and Fine Dining)
Dining Area (Cafeteria/Fast Food)
Dining Area (Family and Leisure)
Electrical, Mechanical, Telephone Rooms
Exercise/Fitness Center and Gymnasium Areas
Financial Transaction Area
Healthcare Facility and Hospitals (Exam/Treatment Room)
Healthcare Facility and Hospitals (Imaging Room)
Healthcare Facility and Hospitals (Medical Supply Room)
Healthcare Facility and Hospitals (Nursery)
Healthcare Facility and Hospitals (Nurse's Station)
Healthcare Facility and Hospitals (Operating Room)
Healthcare Facility and Hospitals (Patient Room)
Healthcare Facility and Hospitals (Physical Therapy Room)
Healthcare Facility and Hospitals (Recovery Room)
Hotel Function Area
Kitchen/Food Preparation Area
Kitchenette or Residential Kitchen
Laboratory, Scientific
Laundry Area
Library (Reading Area)
Library (Stacks Area)
Lobby, Main Entry
Locker Room
Lounge, Breakroom, or Waiting Area
Manufacturing, Commercial & Industrial Work Area (Low Bay)
Manufacturing, Commercial & Industrial Work Area (High Bay)
Manufacturing, Commercial & Industrial Work Area (Precision)
Museum Area (Exhibition/Display)
Museum Area (Restoration Room)
Office Area (>250 square feet)
Office Area (<250 square feet)
Parking Garage Area (Parking Zone and Ramps)
Parking Garage Area (Daylight Adaptation Zones)
Pharmacy Area
Retail Sales Area (Grocery Sales)
Retail Sales Area (Retail Merchandise Sales)
Retail Sales Area (Fitting Room)
Religious Worship Area
Restrooms
Stairwell
Storage, Commercial/Industrial (Warehouse)
Storage, Commercial/Industrial (Refrigerated)
Storage, Commercial/Industrial (Shipping & Handling)
Storage (General)
Sports Arena - Playing Area (> 5,000 Spectators)
Sports Arena - Playing Area (2,000 - 5,000 Spectators)
Sports Arena - Playing Area (< 2,000 Spectators)
Sports Arena - Playing Area (Recreational)
Theater Area (Motion Picture)
Theater Area (Performance)
Transportation Function (Baggage Area)
Transportation Function (Ticketing Area)
Videoconferencing Studio
High-Rise Residential Living Spaces
Hotel/Motel Guest Room
All other
Attic
Reception Area
Elevator
Plenum
IT Room (EPD 12)
Computer Room (EPD 20)
Server Room (EPD 45)