## Notes
Data Sources
Dataset | Dodge 2023
| Commercial End-Use Survey (CEUS) 2022 | https://www.energy.ca.gov/publications/2023/2022-california-commercial-end-use-survey-ceus-final-report
Lawrence Berkeley National Laboratory (LBNL) / U.S. Department of Energy (DOE), 2019
Prototype | California Energy Commission (CEC) Laboratory prototype (CBECC 2022.3.1) | https://bees.noresco.com/software2022.html
| Database for Energy Efficient Resources (DEER) Manufacturing-BioTech prototype (June 2024) | https://github.com/sound-data/DEER-Prototypes-EnergyPlus
Codes | Title 24, part 6, referred to as T24 (1984, 1992,1998, 2001, 2005, 2008, 2013, 2016,2019, 2022, 2025) | https://www.energy.ca.gov/publications/2025/2025-building-energy-efficiency-standards-residential-and-nonresidential | 2025
|  | https://codes.iccsafe.org/codes/united-states/california | 2010+
| American Society of Heating, Refrigerating and Air-Conditioning Engineers (ASHRAE) 90.1 (2022) | https://www.ashrae.org/technical-resources/standards-and-guidelines/read-only-versions-of-ashrae-standards
| Code of Federal Regulations (CFR) Title 10 (2008, 2010) | https://www.govinfo.gov/content/pkg/FR-2009-03-23/pdf/FR-2009-03-23.pdf
| CFR Title 10 (2025) | https://www.ecfr.gov/current/title-10
Other | Alternative Calculation Method (ACM) (2022) | https://www.energy.ca.gov/publications/2022/2022-nonresidential-and-multifamily-alternative-calculation-method-reference
| Nonres ACM 2022, Appendix 5.4A and Appendix 5.4B | https://www.energy.ca.gov/publications/2022/2022-nonresidential-and-multifamily-alternative-calculation-method-reference
| 2022 Reduced infiltration Codes and Standards Enhancement (CASE) report | https://title24stakeholders.com/wp-content/uploads/2020/10/2022-T24-Final-CASE-Report_Reduce-Infiltration.pdf
| 2019 Outdoor Lighting CASE Report | https://title24stakeholders.com/wp-content/uploads/2016/10/T24-2019-CASE-Study-Results-Report-Outdoor-Sources_Final_with-Attachments.pdf
| 2019 High Efficiency Fume Hoods in Laboratory Spaces CASE Report | https://title24stakeholders.com/wp-content/uploads/2017/09/2019-T24-CASE-Report_Fume-Hoods_Final_September-2017.pdf?
| PNNL 20405, 2011 | https://www.pnnl.gov/main/publications/external/technical_reports/PNNL-20405.pdf
| Air leakage Memo, NORESCO, 2025 | Infiltration_rate_report_14May2025-Short-Version.docx
| Proposed Updates to Equipment Power Densities and Building Schedules for the 2028 Energy Code, referred to as "Plug load and schedules project with CEC, 2025" (Docket Number =25-BSTD-03 & TN=265693) | https://efiling.energy.ca.gov/GetDocument.aspx?tn=265693&DocumentContentId=102545
| ASHRAE/AIHA/ACS, Classification of Laboratory Ventilation Design Levels | https://www.ashrae.org/File%20Library/Technical%20Resources/Free%20Resources/Publications/ClassificationOfLabVentDesLevels.pdf
| ANSI/ASSP Z9.5-2022, Laboratory Ventilation | https://webstore.ansi.org/standards/asse/ansiasspz92022
| U.S. DOE Federal Energy Management Program, Right-Sizing Laboratory Equipment Loads. | https://www.osti.gov/servlets/purl/922847
| I2SL Laboratory Benchmarking Tool (successor to the Labs21 Energy Benchmarking Tool) | https://lbt.i2sl.org/
| Commercial Building Prototypes Based on ANSI/ASHRAE/IES Standard 90.1-2019 Appendix G PRM: Technical Support Document | https://www.pnnl.gov/main/publications/external/technical_reports/PNNL-32815.pdf
| California Code of Regulations, Title 8, Section 5154.1 - Ventilation Requirements for Laboratory-Type Hood Operations (Cal/OSHA). | https://www.dir.ca.gov/title8/5154_1.html
| Raising the Bar in High Performance Laboratory Design, ASHRAE Journal, June 2020 | https://www.ashrae.org/technical-resources/ashrae-journal/featured-articles/raising-the-bar-in-high-performance-laboratory-design
| Performance-Based Approach to Laboratory Exhaust Systems, ASHRAE Journal Engineers Notebook, September 2020 | http://www.nxtbook.com/nxtbooks/ashrae/ashraejournal_QVMNEO/
| 2019 T24 Fume Hoods CASE Report | https://efiling.energy.ca.gov/GetDocument.aspx?tn=222188
| Whole Building Design Guide (WBDG, National Institute of Building Sciences), Space Types: Laboratory - Wet. | https://legacy.wbdg.org/space-types/laboratory-wet
| ENERGY STAR certified commercial water heaters | https://www.energystar.gov/productfinder/product/certified-commercial-water-heaters/results?fuel_filter=Gas&markets_filter=United+States
| Grainger gas tank water heaters (sizes below commercial, e.g. 30–75 kBtu/h) | https://www.grainger.com/category/plumbing/water-heaters/gas-tank-water-heaters
| Grainger electric tank water heaters | https://www.grainger.com/category/plumbing/water-heaters/electric-tank-water-heaters
Construction Rate
Four vintage bins (Pre-1978, 1978-1997, 1998-2007, 2008-2018) plus New Construction (2019+) are derived from the California nonresidential construction-rate analysis shown in the Construction Rate block above, binned at the Title 24 code-cycle boundaries that changed the governing envelope and equipment requirements.
Notes
2025 T24 | Laboratory is a space or room where hazardous materials are used for activities such as testing, analysis, instruction, research, or developmental activities. Laboratory Suite is a Group L occupancy space within a building or structure, which may include multiple laboratories, offices, storage, equipment rooms or similar support functions. Laboratory, Scientific Area is a room or area where research, experiments, and measurement in medical and physical sciences are performed requiring examination of fine details. The area may include workbenches, countertops, scientific instruments, and associated floor spaces. Scientific laboratory does not refer to film, computer, and other laboratories where scientific experiments are not performed.
Laboratory type and ventilation design level | The prototype represents a WET RESEARCH LABORATORY BUILDING (medical / biological research), operating at Laboratory Ventilation Design Level LVDL-2 per ASHRAE/AIHA/ACS, Classification of Laboratory Ventilation Design Levels (2018). Lab space is classified as "Laboratory, Scientific" under the T24 2025 definition quoted above. Declaring the LVDL - not only the lab type - is what fixes the downstream assumptions: minimum air change rates, occupied/unoccupied setback, fume hood face velocity and sash control, and exhaust discharge. Pharmaceutical / biopharma GMP production facilities are EXCLUDED from this prototype: they fall outside the OSHA 29 CFR 1910.1450(b) definition of "laboratory scale", which expressly excludes production-scale work, and cleanroom classification, process loads and 24/7 operation would reopen ventilation, internal loads, schedules and humidity control. PENDING CONFIRMATION - this decision governs the Ventilation tab.
Wet laboratory Definition | A WET LABORATORY is a space where chemicals, drugs, or other material or biological matter are tested and analyzed, requiring water, direct ventilation and specialized piped utilities (WBDG, Space Types: Laboratory - Wet). The NIH Design Requirements Manual makes the same distinction operationally: wet laboratories handle liquid solutions, biological materials and chemicals and are fitted with bench space, hand-wash and work sinks, chemical fume hoods and/or biological safety cabinets, and piped services such as DI or RO water and laboratory gases; DRY laboratories are computational, bioinformatics, electronics and instrumentation spaces and require no wet services. MIT Design Standards T10 characterizes wet laboratories as spaces that use and store chemical and biological materials, equipped with sinks or fume hoods, specialized local exhaust ventilation (SLEV) and containment equipment such as biological safety cabinets. All three are consistent with the OSHA definition of laboratory scale at 29 CFR 1910.1450(b) - work with hazardous chemicals on a NON-PRODUCTION basis, in containers that can be handled safely by one person.
Laboratory types the prototype does NOT represent (LAB4) | Laboratory is not a single building type. MIT Design Standards T10 lists SEVENTEEN laboratory types (Baseline; Life Science/Bio; Optical; Engineering/Physical Sciences; Maker Space/Machine Shop; Chemistry; BL1; BL2; BL2+; BL3; Radioactive Material; Radiation Producing; Clinical Lab; Animal/Survival Surgery; ABSL-1; ABSL-2; ABSL-2+). The prototype is proposed to represent a general WET RESEARCH laboratory (medical/biological, broadly MIT types Baseline and Life Science/Bio) at LVDL-2. It does NOT represent: DRY/COMPUTATIONAL laboratories (no hoods or piped services; office-like ventilation, load-driven); TEACHING laboratories (very high hood density per unit area but low occupied hours); CLINICAL and DIAGNOSTIC laboratories (biological safety cabinets rather than chemical fume hoods; ventilation governed by ASHRAE 170 and the CMC rather than by hood demand); VIVARIA and animal holding (high fixed air change rates with tight temperature and humidity control, 24/7); HIGH-CONTAINMENT laboratories at BSL-3 and above (single-pass air, sealed envelope, HEPA filtration, deeper interstitial space); and PHARMACEUTICAL/BIOPHARMA GMP PRODUCTION (cleanroom classification, process loads, 24/7 operation), which is excluded because it falls outside the OSHA 29 CFR 1910.1450(b) laboratory-scale definition. Each of these carries a materially different ventilation rate, exhaust configuration, internal load and schedule, so a prototype cannot represent them all.
Table 2: Distribution of lab (Institutional Labs) - Dodge 2023
Area (KSF) |  | Number of Story
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7+
| 0-10 | 1.7 | 0.3 | 0 | 0 | 0 | 0 | 0
| 10.001-25 | 3.3 | 1.6 | 0.2 | 0 | 0 | 0 | 0
| 25.001-50 | 4 | 3.4 | 1.5 | 0.3 | 0.2 | 0 | 0
| 50.001-75 | 1.8 | 3.7 | 1.5 | 1.2 | 0.4 | 0.1 | 0
| 75.001-100 | 1.6 | 3.5 | 2.2 | 1.3 | 0.9 | 0.2 | 0.2
| 100.001-150 | 1.9 | 4.1 | 2.9 | 2.7 | 1 | 1 | 1.6
| 150.001-200 | 0.4 | 3.3 | 2.4 | 1.9 | 2.3 | 1.3 | 1.8
| 200.001-300 | 1.1 | 4.6 | 2.4 | 1 | 1.9 | 0.9 | 3.7
| 300.001-500 | 2 | 3.8 | 1.7 | 1.1 | 1.3 | 1.4 | 3.1
| 500.001-1000 | 1.3 | 0 | 0 | 0.5 | 0 | 0.5 | 4.3
| >1000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 19.1 | 28.3 | 14.8 | 10 | 8 | 5.4 | 14.7
New Labs distribution 1,000 sf/yr [[2017 - 2022 average]
| 1 Story | 2 Story | 3 Story | 4 Story | 5 Story | 6 Story | 7 Story | 8 Story | 9+ Story
Manufacturing Labs | 10.1 | 24.2 | 16.5 | 0 | 70.6 | 0 | 0 | 49 | 0
Institutional Labs | 108.9 | 76.5 | 348.6 | 198 | 218.6 | 147.5 | 60.2 | 105.6 | 299.8

## Prototype
NORESCO, Updated September 2026
Laboratory
Characteristic | Value | Data Sources
Building Type | Laboratory
Building Category | Nonresidential
Version | v2-0
Vintages | 4 Vintages: Pre-1978 , 1978-1997 ,1998-2007 , 2008-2018 New Construction (2019+) | Based on the vintage bin analysis. A summary of the findings is presented in the following paper, with a link provided in the Notes tab: Yousefi, F., Athalye, R. (2025). “Determining Vintage Bins for Prototype Development: An Analysis of California Commercial Buildings.” ASHRAE Annual Conference.
Shape |  | Assume rectangular shape; supported by CBECS, CEC, and LBNL/DOE. The windows have been updated from ribbon style to punched openings.
Total Floor Area (ft²) | 53627 | Based on CEC Lab prototype, which is based on the Medium Office prototype. External features, such as number of floors, conditioned floor area, WWR, etc., are identical to Medium Office prototype. Lab buildings are similar to office buildings in their characteristics. They are outfitted for lab purposes, such as with exhaust hoods, etc., though they are designed to be repurposed as office space. This prototype is based on the Medium Office prototype geometry. The program/spaces, people, ventilation, and other loads are those for a lab building.
Aspect Ratio | 1.5
Number of Floors | 3
Roof type | Flat
WWR | 33%
Shading Geometry | No Shades
Floor to floor height (feet) | 15 | LBNL/DOE prototype
Floor to ceiling height (feet) | 9 (6 ft above-ceiling plenum)
Glazing sill height (feet) | 3.35 ft (top of the window is 7.64 ft high with 4.29 ft high glass) | Based on CEC Lab prototype
Laboratory Program Metrics
Laboratory, Scientific area (ft2) | 28800 | 53.9% of conditioned area. Eleven laboratory spaces: the core on all three floors, plus the north, west, east, south and conference spaces on FloorM and the north, south and conference spaces on FloorT.
Office area (ft2) | 11537 | 21.7% of conditioned area - office area (10,036 ft2), conference (1,112), lobby (1,059) and lounge/breakroom (2,814).
Lab support area (ft2) | 13290 | 24.4% of conditioned area - corridor (4,816 ft2), storage (2,949), stairwell (1,983), restrooms (1,932), mechanical/electrical (1,071) and IT room (537). The previous layout had NO support space at all.
Total floor area (ft2) | 53627 | Conditioned total. Excludes the three plenums at 17,876 ft2 each. The IDF geometry gives 53,633 ft2
Fume hood count | 90 | At 18.6 ft of hood per 1,000 ft2 of laboratory area (CEC TN 222188 Table 29) applied to 28,800 ft2 of laboratory space: 536 ft of hood, about 90 six-foot hoods. T
Above grade wall area (ft²) | 21287.4627
Gross wall area (ft²) | 21287.4627
Roof area (ft²) | 17875.9489
Underground Gross Wall Area (ft²) | 0

## Zones
Proposed Layout - Laboratory
Building | Space/Thermal Zone | Space Type Primarily from [T24, 2022 Appendix 5.4A] - See Notes column | HVAC System Name (New Construction) | Schedule Category | Conditioned (Y/N) | Area Fraction | Area (ft²) | Volume (ft³) | Multipliers | Number of People | People (Persons/1,000 ft²) [T24, 2025,Table 120.1-A] | Notes
Laboratory | Lab_Core_FloorG | Laboratory, Scientific | BaseAirSys14 | Lab | Yes | 7.987% | 4283 | 38547 | 1 | 21 | 5 | Laboratory Space Occupancy level Derived from the LBNL/DOE Prototype
Laboratory | Lab_N_FloorG | Laboratory, Scientific | BaseAirSys14-2 | Lab | Yes | 4.285% | 2298 | 20682 | 1 | 11 | 5
Laboratory | Enclosed_Office_W_FloorG | Office Area (>250 square feet) | BaseAirSys5-1 | Office | Yes | 3.054% | 1638 | 14741 | 1 | 8 | 5
Laboratory | Enclosed_Office_E_FloorG | Office Area (>250 square feet) | BaseAirSys5-1 | Office | Yes | 3.054% | 1638 | 14741 | 1 | 8 | 5
Laboratory | Lab_S_FloorG | Laboratory, Scientific | BaseAirSys14-3 | Lab | Yes | 2.212% | 1186 | 10676 | 1 | 6 | 5
Laboratory | Conference_FloorG | Convention, Conference, Multipurpose and Meeting Area | BaseAirSys5-1 | Office | Yes | 2.074% | 1112 | 10006 | 1 | 37 | 33
Laboratory | Lobby_FloorG | Lobby, Main Entry | BaseAirSys5-1 | Office | Yes | 1.975% | 1059 | 9533 | 1 | 11 | 10
Laboratory | Storage_FloorG | Storage (General) | BaseAirSys5-1 | Office | Yes | 1.833% | 983 | 8848 | 1 | 0 | 0
Laboratory | Mechanical/Electrical_FloorG | Electrical, Mechanical, Telephone Rooms | BaseAirSys5-1 | Ancillary | Yes | 0.6657% | 357 | 3216 | 1 | 0 | 0
Laboratory | IT-Room_FloorG | IT Room (EPD 12) | BaseAirSys5-1 | Data | Yes | 0.3338% | 179 | 1610 | 1 | 0 | 1.5
Laboratory | Restroom_FloorG | Restrooms |  | Office | Yes | 1.201% | 644 | 5792 | 1 | 0 | 0 | Indirectly conditioned
Laboratory | BreakRoom/Kitchenette_FloorG | Lounge, Breakroom, or Waiting Area | BaseAirSys5-1 | Office | Yes | 0.4326% | 232 | 2091 | 1 | 8 | 33
Laboratory | Stairway_FloorG | Stairwell | BaseAirSys5-1 | Ancillary | Yes | 1.233% | 661 | 5953 | 1 | 0 | 0
Laboratory | Corridor_W_FloorG | Corridor Area | BaseAirSys5-1 | Office | Yes | 0.5594% | 300 | 2700 | 1 | 2 | 5
Laboratory | Corridor_N_FloorG | Corridor Area | BaseAirSys5-1 | Office | Yes | 0.938% | 503 | 4527 | 1 | 3 | 5
Laboratory | Corridor_E_FloorG | Corridor Area | BaseAirSys5-1 | Office | Yes | 0.5576% | 299 | 2693 | 1 | 1 | 5
Laboratory | Corridor_S_FloorG | Corridor Area | BaseAirSys5-1 | Office | Yes | 0.938% | 503 | 4527 | 1 | 3 | 5
Laboratory | Plenum_FloorG | Plenum | n/a | Office | No |  | 17876 | 71504 | 1 | 0 | 0
Laboratory | Lab_Core_FloorM | Laboratory, Scientific | BaseAirSys14-4 | Lab | Yes | 7.987% | 4283 | 38547 | 1 | 21 | 5 |  | Ground floor (FloorG) |  |  |  | Middle floor (FloorM) | Top floor (FloorT)
Laboratory | Lab_N_FloorM | Laboratory, Scientific | BaseAirSys14-5 | Lab | Yes | 4.285% | 2298 | 20682 | 1 | 11 | 5
Laboratory | Lab_W_FloorM | Laboratory, Scientific | BaseAirSys14-6 | Lab | Yes | 3.054% | 1638 | 14741 | 1 | 8 | 5
Laboratory | Lab_E_FloorM | Laboratory, Scientific | BaseAirSys14-7 | Lab | Yes | 3.054% | 1638 | 14741 | 1 | 8 | 5
Laboratory | Lab_S_FloorM | Laboratory, Scientific | BaseAirSys14-8 | Lab | Yes | 2.212% | 1186 | 10676 | 1 | 6 | 5 |  | Area Distribution By Space Type
Laboratory | Lab_FloorM | Laboratory, Scientific | BaseAirSys14-9 | Lab | Yes | 2.074% | 1112 | 10006 | 1 | 6 | 5 |  | Space Type | % Area | Number of People | % People
Laboratory | Lounge_FloorM | Lounge, Breakroom, or Waiting Area | BaseAirSys5-2 | Office | Yes | 1.975% | 1059 | 9533 | 1 | 16 | 15 |  | Laboratory, Scientific | 53.71% | 142 | 46.25%
Laboratory | Storage_FloorM | Storage (General) | BaseAirSys5-2 | Office | Yes | 1.833% | 983 | 8848 | 1 | 0 | 0 |  | Office Area (>250 square feet) | 12.22% | 32 | 10.42%
Laboratory | Mechanical/Electrical_FloorM | Electrical, Mechanical, Telephone Rooms | BaseAirSys5-2 | Ancillary | Yes | 0.6657% | 357 | 3216 | 1 | 0 | 0 |  | Convention, Conference, Multipurpose and Meeting Area | 2.074% | 37 | 12.05%
Laboratory | IT-Room_FloorM | IT Room (EPD 12) | BaseAirSys5-2 | Data | Yes | 0.3338% | 179 | 1610 | 1 | 0 | 1.5 |  | Lobby, Main Entry | 1.975% | 11 | 3.583%
Laboratory | Restroom_FloorM | Restrooms |  | Office | Yes | 1.201% | 644 | 5792 | 1 | 0 | 0 | Indirectly conditioned | Storage (General) | 5.499% | 0 | 0%
Laboratory | BreakRoom/Kitchenette_FloorM | Lounge, Breakroom, or Waiting Area | BaseAirSys5-2 | Office | Yes | 0.4326% | 232 | 2091 | 1 | 8 | 33 |  | Electrical, Mechanical, Telephone Rooms | 1.997% | 0 | 0%
Laboratory | Stairway_FloorM | Stairwell | BaseAirSys5-2 | Ancillary | Yes | 1.233% | 661 | 5953 | 1 | 0 | 0 |  | IT Room (EPD 12) | 1.001% | 0 | 0%
Laboratory | Corridor_W_FloorM | Corridor Area | BaseAirSys5-2 | Office | Yes | 0.5594% | 300 | 2700 | 1 | 2 | 5 |  | Restrooms | 3.603% | 0 | 0%
Laboratory | Corridor_N_FloorM | Corridor Area | BaseAirSys5-2 | Office | Yes | 0.938% | 503 | 4527 | 1 | 3 | 5 |  | Lounge, Breakroom, or Waiting Area | 5.247% | 56 | 18.24%
Laboratory | Corridor_E_FloorM | Corridor Area | BaseAirSys5-2 | Office | Yes | 0.5594% | 300 | 2693 | 1 | 2 | 5 |  | Stairwell | 3.698% | 0 | 0%
Laboratory | Corridor_S_FloorM | Corridor Area | BaseAirSys5-2 | Office | Yes | 0.938% | 503 | 4527 | 1 | 3 | 5 |  | Corridor Area | 8.982% | 29 | 9.446%
Laboratory | Plenum_FloorM | Plenum | n/a | Office | No |  | 17876 | 71504 | 1 | 0 | 0 |  | Total | 100% | 307 | 100%
Laboratory | Lab_Core_FloorT | Laboratory, Scientific | BaseAirSys14-10 | Lab | Yes | 7.987% | 4283 | 38547 | 1 | 21 | 5
Laboratory | Lab_N_FloorT | Laboratory, Scientific | BaseAirSys14-11 | Lab | Yes | 4.285% | 2298 | 20682 | 1 | 11 | 5
Laboratory | Enclosed_Office_W_FloorT | Office Area (>250 square feet) | BaseAirSys5-3 | Office | Yes | 3.054% | 1638 | 14741 | 1 | 8 | 5
Laboratory | Enclosed_Office_E_FloorT | Office Area (>250 square feet) | BaseAirSys5-3 | Office | Yes | 3.054% | 1638 | 14741 | 1 | 8 | 5
Laboratory | Lab_S_FloorT | Laboratory, Scientific | BaseAirSys14-12 | Lab | Yes | 2.212% | 1186 | 10676 | 1 | 6 | 5
Laboratory | Lab_FloorT | Laboratory, Scientific | BaseAirSys14-13 | Lab | Yes | 2.074% | 1112 | 10006 | 1 | 6 | 5
Laboratory | Lounge_FloorT | Lounge, Breakroom, or Waiting Area | BaseAirSys5-3 | Office | Yes | 1.975% | 1059 | 9533 | 1 | 16 | 15
Laboratory | Storage_FloorT | Storage (General) | BaseAirSys5-3 | Office | Yes | 1.833% | 983 | 8848 | 1 | 0 | 0
Laboratory | Mechanical/Electrical_FloorT | Electrical, Mechanical, Telephone Rooms | BaseAirSys5-3 | Ancillary | Yes | 0.6657% | 357 | 3216 | 1 | 0 | 0
Laboratory | IT-Room_FloorT | IT Room (EPD 12) | BaseAirSys5-3 | Data | Yes | 0.3338% | 179 | 1610 | 1 | 0 | 1.5
Laboratory | Restroom_FloorT | Restrooms |  | Office | Yes | 1.201% | 644 | 5792 | 1 | 0 | 0 | Indirectly conditioned
Laboratory | BreakRoom/Kitchenette_FloorT | Lounge, Breakroom, or Waiting Area | BaseAirSys5-3 | Office | Yes | 0.4326% | 232 | 2091 | 1 | 8 | 33
Laboratory | Stairway_FloorT | Stairwell | BaseAirSys5-3 | Ancillary | Yes | 1.233% | 661 | 5953 | 1 | 0 | 0
Laboratory | Corridor_W_FloorT | Corridor Area | BaseAirSys5-3 | Office | Yes | 0.5594% | 300 | 2700 | 1 | 2 | 5
Laboratory | Corridor_N_FloorT | Corridor Area | BaseAirSys5-3 | Office | Yes | 0.938% | 503 | 4527 | 1 | 3 | 5
Laboratory | Corridor_E_FloorT | Corridor Area | BaseAirSys5-3 | Office | Yes | 0.5594% | 300 | 2693 | 1 | 2 | 5
Laboratory | Corridor_S_FloorT | Corridor Area | BaseAirSys5-3 | Office | Yes | 0.938% | 503 | 4527 | 1 | 3 | 5
Laboratory | Plenum_FloorT | Plenum | n/a | Office | No |  | 17876 | 71504 | 1 | 0 | 0
Total (1 Building) | Total (54 Space) | Total (11 Space Type) | Total (4 HVAC Systems/Airloops) | Total (1 category) | Total (51 Conditioned zones, 3 unconditioned zones) | 100% | 53627 | 658610 |  | 307
N

## Envelope
Envelope - Laboratory
Element | Prototype | Assembly Type | Construction | Thermal properties | Vintage | Selected T24 | Notes | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
External Wall | Laboratory | ExtWall_MetalFramed_NonRes | Metal framed wall: Metal frame + insulation + Gypsum board | U-value IP | Pre 1978 | N/A | Using DOE pre-1980 U-values and a 7.4% cumulative wall renovation rate through 2028, based on the average annual rate from CBECS 2003 and 2012 projected over 48 years. | 0.21745 | 0.21479 | 0.21627 | 0.21479 | 0.21479 | 0.21745 | 0.21745 | 0.21479 | 0.21479 | 0.21479 | 0.21479 | 0.21479 | 0.21479 | 0.21479 | 0.21479 | 0.21479
[5 empty] | 1978-1997 | 1986 | Similar to Low-rise office (Table 2-53V): Package A/ Heat Capacity was considered 0-3.99 (BTU/F/ft²) | 0.13298 | 0.13298 | 0.13298 | 0.13298 | 0.13298 | 0.13298 | 0.13298 | 0.13298 | 0.13298 | 0.13298 | 0.13298 | 0.13298 | 0.13298 | 0.13298 | 0.13298 | 0.13298 | *U = 1 / R_assembly, with the per-CZ R-values for Heat capacity of ~10: (4.7 / 4.4 / 4.4 / 4.6 / 3.9 CZ5-10 / 4.2 CZ11-13 / 4.8 CZ14-15 / 4.7 CZ16) | These values have better performance than the next vintage
[5 empty] | 1998-2007 | 2001 | Table 1-H | 0.182 | 0.182 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.098 | 0.062 | 0.082 | 0.062 | 0.062 | 0.098 | 0.098 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062
[5 empty] | Existing |  | Weighted average of all 4 vintages | 0.1887 | 0.18024 | 0.17122 | 0.16927 | 0.14804 | 0.16911 | 0.15706 | 0.16674 | 0.1669 | 0.15346 | 0.17834 | 0.16754 | 0.19318 | 0.15895 | 0.16022 | 0.16594
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.06 | 0.055 | 0.071 | 0.055 | 0.055 | 0.06 | 0.06 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055
Roof | Laboratory | FlatRoof_WoodFramedAndOther_NonRes | Metal deck roof: roof membrane+roof insulation+metal decking | U-value IP | Pre 1978 | N/A | Considering 30 years for roof/ insulation replacement. | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 1978-1997 | 1992 |  | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 1998-2007 | 2001 | Table 1-H | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.049 | 0.039 | 0.039 | 0.039 | 0.049 | 0.075 | 0.067 | 0.067 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039
[5 empty] | Existing |  | Weighted average of all 4 vintages | 0.056695 | 0.056997 | 0.055521 | 0.055512 | 0.056752 | 0.077797 | 0.07722 | 0.077387 | 0.075394 | 0.067987 | 0.05516 | 0.055315 | 0.056011 | 0.055794 | 0.053452 | 0.055656
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038
Windows | Laboratory | FixedWindow_NonRes | Single pane | U-value IP | Pre 1978 | N/A | ASHRAE Handbook of Fundamentals (Table 4-Ch15) for single pane & T24, 2013 for double pane (33%-67%)* | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108
[5 empty] | 1978-1997 | N/A |  | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108
|  |  | Double pane |  | 1998-2007 | 2001 | Table 1-H | 0.49 | 0.49 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36
[5 empty] | Existing |  | Weighted average of all 4 vintages | 0.5908 | 0.59337 | 0.62222 | 0.62222 | 0.61014 | 0.62626 | 0.63665 | 0.62107 | 0.61347 | 0.55042 | 0.56472 | 0.56611 | 0.59173 | 0.56543 | 0.52742 | 0.55943
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.34 | 0.36 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.36
| Laboratory | FixedWindow_NonRes | Single pane | SHGC | Pre 1978 | N/A | ASHRAE Handbook of Fundamentals (Table 10-Ch15) for single pane & T24, 2013 for double pane (33%-67%)* | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282
[5 empty] | 1978-1997 | N/A |  | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282
|  |  | Double pane |  | 1998-2007 | 2001 | Table 1-H - WWR:31-40% / SHGC non-north | 0.43 | 0.31 | 0.41 | 0.41 | 0.41 | 0.34 | 0.34 | 0.34 | 0.34 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.43
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
[5 empty] | Existing |  | Weighted average of all 4 vintages | 0.42155 | 0.41116 | 0.41063 | 0.41053 | 0.42204 | 0.40182 | 0.39624 | 0.40753 | 0.40769 | 0.37618 | 0.38998 | 0.39076 | 0.41323 | 0.38831 | 0.35986 | 0.41538
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.22 | 0.25 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.25
Infiltration
|  |  | Building | Zones | Vintage | I_75 6-sdied Infiltration rate @ 75 pa | Note | I-design (cfm/ft²) (4-sided Infiltration rate at normal pressure) (Design flow rate approach and Flow/Exterior Wall Area calculation method)
|  | Infiltration | Laboratory |  | Pre 1978 | 1.1 | 2022 CASE report (Table 38) | 0.3301
[5 empty] | 1978-1997 | 1.1 | 2022 CASE report (Table 38) | 0.3301
[5 empty] | 1998-2007 | 1.1 | 2022 CASE report (Table 38) | 0.3301
[5 empty] | 2008-2018 | 1 | 2022 CASE report (Table 38) & T24, 2008-2016 (Table 140.3-B)--Air barrier is required in CZ 10-16 | 0.3021
[5 empty] | Existing | 1.1 | Same as Pre 2008 because of their higher weights | 0.3301
[5 empty] | 2019+ | 0.6 | 2022 CASE report (Table 38) & T24, 2025 (Table 140.3-B)-Air barrier is required in all CZs | 0.1801
[5 empty] | Air Leakage Memo: | Infiltration_rate_report_14May2025-Short-Version.docx
-
Pre-1978 exterior wall U value calculation:
External Wall | Laboratory | ExtWall_MetalFramed_NonRes | Metal framed wall: Metal frame + insulation + Gypsum board | U-value IP | Pre 1978 | N/A | ASHRAE 90.1, 2022 Table A3.3.3.1, 3.5", R-0 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352
[7 empty] | T24 2008 (U value) | 0.098 | 0.062 | 0.082 | 0.062 | 0.062 | 0.098 | 0.098 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062
[7 empty] | DOE pre 1980 Office prototype LA (U value) | 0.227 | 0.227 | 0.227 | 0.227 | 0.227 | 0.227 | 0.227 | 0.227 | 0.227 | 0.227 | 0.227 | 0.227 | 0.227 | 0.227 | 0.227 | 0.227
[7 empty] | Renovation rate since 1980 (yearly renovation rate was calculated from CBECS 2003 and 2012 and then projected over 48 years) | 7.4%

## HVAC System
HVAC system - Laboratory
Vintage | Zones | Heating | Cooling | Air Distribution | Source | Note
Existing | Offices and support area | Gas Boiler | Packaged (DX) | Multi zone VAV with hydronic reheat | Engineering Judgement | System 5 PVAV for offices and support area
| Other Conditioned zones (Labs) | Gas Boiler | Packaged (DX) | Multi zone VAV with hydronic reheat |  | System 5 PVAV- 100% outdoor air for labs, but no required energy recovery For V1 and V2. V3 has Heat recovery.
New Construction | Offices and support area | Gas Boiler | Packaged (DX) | Multi zone VAV with hydronic reheat | T24 2025 ACM 2025, Table 1 and 2 | System 5 PVAV for offices and support area
| Other Conditioned zones (Labs) | Central air-to-water HP | Central air-cooled Chiller | Single zone VAV ( Each zone has a chilled water or hot water changeover coil with a 6-way valve for cooling or heating) |  | System 14a for Labs– Air-cooled 4 pipe VAV with Exhaust heat recovery-
*The New Construction HVAC system is assigned by the 2025 ACM Reference Manual, Table 1 (Nonresidential HVAC System Map), which selects the standard design system by space function rather than building type. For a covered process laboratory, Table 1 assigns System 14a – ACSZVAV (air-cooled single zone VAV) where the design maximum exhaust exceeds 20,000 cfm, no exception applies, and total conditioned floor area is below 150,000 ft²; above that area it becomes System 14b (water-cooled), and where the exhaust test is not met or an exception applies it drops to System 5 – PVAV. The laboratory prototype meets all three conditions: laboratory exhaust is a covered process under the ACM, design exhaust is 25,317 cfm, and conditioned floor area is 53,626 ft², which is why 14a rather than 14b was selected. The ACM is used as the basis because no observed stock dataset reports laboratory HVAC system type: CEUS 2022 has twelve building types with no laboratory or R&D category. Existing vintages use System 5 – PVAV on the same ACM basis, applied as a documented proxy.
** DEDICATED FANS: each of the laboratory zones carries its own exhaust fan, in every vintage and in New Construction. The exhaust is modelled as a per-zone dedicated fan, i.e. non-manifolded; no common exhaust plenum or manifold is represented. HEAT RECOVERY: present in New Construction and V3 only, as part of System 14a and system 5, and absent from the other vintages. PLUME AND EXIT VELOCITY: not modelled and not modellable with the current objects, since EnergyPlus zone exhaust fans carry no stack or discharge model.
Efficiency of HVAC system (Efficiency is capacity-dependent. The following table provides a general estimate of system efficiency based on preliminary simulations in one climate zone, or assuming cooling load based on rule of thumb)
Vintage | Upgrade/Installed year | Air-Cooled Chiller | DX | Gas Boiler | Air-to-Water HP | Sources | Note
Pre 1978 | 2008 | n/a | ≥ 65,000 Btu/h and < 135,000 Btu/h , 11.0 EER | 80% Ec | n/a | T24, 2008 , Table 112-A (for DX Coil) -Title 24-2008 §111 / Title 20 Table E-3 (and 10 CFR 431.87 as in effect through March 1, 2012) for Boiler Efficiency
1978-1997
1998-2007
2008-2018 | 2013 | n/a | ≥ 65,000 Btu/h and < 135,000 Btu/h , 11.0 EER | Gas-Fired Boiler > 300,000 Btu/h and ≤2,500,000 Btu/h-- 80% Et Gas-Fired Boiler > 2,500,000 Btu/h -- 82% Ec | n/a | T24, 2013 , Table 110.2-A (for DX Coil) -Table 110.2-k (for Gas Fired Boiler)
New Construction | 2025 | Air-cooled Chiller >150 Tons--≥ 10.100 EER, ≥ 14.000 IPLV | ≥ 65,000 Btu/h and < 135,000 Btu/h , 11.0 EER | Gas-Fired Boiler > 300,000 Btu/h and ≤2,500,000 Btu/h-- 80% Et Gas-Fired Boiler > 2,500,000 Btu/h -- 82% Ec | Air Cooled (Heating Mode) Split system and single package≥ 135,000 Btu/h and < 240,000 Btu/h 3.3 COP | T24, 2025 , Table 110.2-A (for DX Coil), Table 110.2-D (for chiller COP) - 10 CFR 431.86 , section § 431.87 Table 1 (for Boiler thermal efficiency).
|  | * Et = Combustion efficiency | * Et = Thermal efficiency
Fan power
Vintage | Approach | System | Total Static Pressure (TSP) (in w.c.) | Fan Efficiency [ACM 2025] | Motor Efficiency | Fan Power Index (W/cfm) | Data Source | Note
Existing | PNNL 90.1-2011, TSP | System 5 PVAV | 5.58 | 0.65 | ASHRAE 90.1, 2004, Table 10.8 * |  | Fan power formula: PNNL 20405, 2010, section 5.2.2.5 TSP and fan efficiency: PNNL 20405, 2010, Table 5.11, 90.1-04ac values Motor efficiency: ASHRAE 90.1, 2004, Table 10.8
Brake horsepower (bhp) = (Supply cfm × TSP in w.c.) / (6356 × fan efficiency)
Fan power (w/cfm) = (bhp × 746) / ( supply cfm × motor efficiency )
New Construction | ACM 2025 | System 5 PVAV, by supply cfm | TSP = fan power × motor efficiency × fan efficiency × 6356 / 746 | 0.65 | 2025 ACM Table 12 ** | 0.978 at or below 5,000 cfm; 1.022 above 5,000 and at or below 10,000 cfm | Fan power index: [ACM 2025, Table 13] Motor efficiency: [ ACM 2025, Table 12]
* 0.9 is an average fan efficiency according to ACM 2025, Table 13
* According to PNNL 20405 section 5.2.2.5, the full-load efficiency of the motor serving the fan is taken from ASHRAE 90.1, 2004, Table 10.8, based on motor nameplate and assuming enclosed motors operating at 1,800 rotations per minute (rpm) Motor nameplate size (bhp) = brake horsepower (bhp) × 1.1 ( using a 10% oversizing factor)
** The full‑load efficiency of the motor serving the fan is taken from ACM 2025 Table 12 based on the motor nameplate horsepower. Brake horsepower (bhp) = (Supply cfm from sizing run × fan power in W/cfm) / 746. System 5 PVAV is 0.978 W/cfm at or below 5,000 cfm, 1.022 above 5,000 and at or below 10,000, and 0.964 above 10,000. System 14a is 0.666, 0.681, and 0.623 W/cfm for those same airflow bins. Motor efficiency uses ACM 2025 Table 12 by nameplate horsepower.
Background Data [To be deleted prior to publication]

## Thermostat
Thermostat Setpoints - Laboratory
Spaces/Zones | Setpoint | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16 | Source
Laboratory | Heating Setpoint (F) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | LBNL/DOE Prototype for Labs
| Heating Setback (F) | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68
| Cooling Setpoint (F) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
| Cooling Setback (F) | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78
All conditioned zones except server rooms, Storage, Stairway & Mechanical_Electrical | Heating Setpoint (F) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | T24 2025 - Appendix 5.4B
| Heating Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
| Cooling Setpoint (F) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
| Cooling Setback (F) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
Storage, Stairway, and Mechanical_Electrical | Heating Setpoint (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | Engineering Judgment
| Heating Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | (Semi‑conditioned space)
| Cooling Setpoint (F) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
| Cooling Setback (F) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
IT rooms | Cooling Setpoint (F)* | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | Title 24, Part 6, 2025, section 140.9 (a) and PNNL ASHRAE 90.1 2022 Large Office prototype
| Heating Setpoint (F)* | *The IT room with over 12 W/ft2 load doesn't require heating system as the equipment constantly generate enough heat.
*Relative Humidity Ratio: 40%-60%

## Ventilation
Outdoor Airflow Rate - Laboratory
Space Type | Space/Thermal Zone | Number of People | Floor Area (ft²) | cfm/person (T24, 2025, Equation 120.1-F and Table 120.1-A) | cfm/ft² (T24, 2025, Equation 120.1-F and Table 120.1-A) | Required exhaust rate-CFM/ft²- (T24, part 6 2025, Table 120.1-B – minimum exhaust rates) | Hood Exhaust Rate (cfm) @133 cfm/ft - At sash stop | Total cfm driven by people | Total cfm driven by area | Total cfm driven by exhaust | Total cfm | Notes
Laboratory, Scientific | Lab_Core_FloorG | 107.075 | 4283 | 15 | 0.15 | 1 | 10612.3746 | 1606.125 | 642.45 | 4283 | 10612.3746
Laboratory, Scientific | Lab_N_FloorG | 57.45 | 2298 | 15 | 0.15 | 1 | 5693.9614 | 861.75 | 344.7 | 2298 | 5693.9614
Office Area (>250 square feet) | Enclosed_Office_W_FloorG | 8 | 1638 | 15 | 0.15 |  |  | 120 | 245.7 | 0 | 245.7
Office Area (>250 square feet) | Enclosed_Office_E_FloorG | 8 | 1638 | 15 | 0.15 |  |  | 120 | 245.7 | 0 | 245.7
Laboratory, Scientific | Lab_S_FloorG | 29.65 | 1186 | 15 | 0.15 | 1 | 2938.6589 | 444.75 | 177.9 | 1186 | 2938.6589
Convention, Conference, Multipurpose and Meeting Area | Conference_FloorG | 37 | 1112 | 15 | 0.15 |  |  | 555 | 166.8 | 0 | 555
Lobby, Main Entry | Lobby_FloorG | 11 | 1059 | 15 | 0.15 |  |  | 165 | 158.85 | 0 | 165
Storage (General) | Storage_FloorG | 0 | 983 | 15 | 0.15 |  |  | 0 | 147.45 | 0 | 147.45
Electrical, Mechanical, Telephone Rooms | Mechanical/Electrical_FloorG | 0 | 357 | 15 | 0.15 |  |  | 0 | 53.55 | 0 | 53.55
IT Room (EPD 12) | IT-Room_FloorG | 0 | 179 | 15 | 0.15 |  |  | 0 | 26.85 | 0 | 26.85
Restrooms | Restroom_FloorG | 0 | 644 | 15 | 0.15 | 4*50/70 cfm per unit |  | 0 | 96.6 | 200 | 200
Lounge, Breakroom, or Waiting Area | BreakRoom/Kitchenette_FloorG | 8 | 232 | 15 | 0.15 |  |  | 120 | 34.8 | 0 | 120
Stairwell | Stairway_FloorG | 0 | 661 | 15 | 0.15 |  |  | 0 | 99.15 | 0 | 99.15
Corridor Area | Corridor_W_FloorG | 2 | 300 | 15 | 0.15 |  |  | 30 | 45 | 0 | 45
Corridor Area | Corridor_N_FloorG | 3 | 503 | 15 | 0.15 |  |  | 45 | 75.45 | 0 | 75.45
Corridor Area | Corridor_E_FloorG | 1 | 299 | 15 | 0.15 |  |  | 15 | 44.85 | 0 | 44.85
Corridor Area | Corridor_S_FloorG | 3 | 503 | 15 | 0.15 |  |  | 45 | 75.45 | 0 | 75.45
Plenum | Plenum_FloorG | 0 | 17876 |  | - |  |  | 0 | 0 | 0 | 0
Laboratory, Scientific | Lab_Core_FloorM | 107.075 | 4283 | 15 | 0.15 | 1 | 10612.3746 | 1606.125 | 642.45 | 4283 | 10612.3746
Laboratory, Scientific | Lab_N_FloorM | 57.45 | 2298 | 15 | 0.15 | 1 | 5693.9614 | 861.75 | 344.7 | 2298 | 5693.9614
Laboratory, Scientific | Lab_W_FloorM | 40.95 | 1638 | 15 | 0.15 | 1 | 4058.62 | 614.25 | 245.7 | 1638 | 4058.62
Laboratory, Scientific | Lab_E_FloorM | 40.95 | 1638 | 15 | 0.15 | 1 | 4058.62 | 614.25 | 245.7 | 1638 | 4058.62
Laboratory, Scientific | Lab_S_FloorM | 29.65 | 1186 | 15 | 0.15 | 1 | 2938.6589 | 444.75 | 177.9 | 1186 | 2938.6589
Laboratory, Scientific | Lab_FloorM | 27.8 | 1112 | 15 | 0.15 | 1 | 2755.3025 | 417 | 166.8 | 1112 | 2755.3025
Lounge, Breakroom, or Waiting Area | Lounge_FloorM | 16 | 1059 | 15 | 0.15 |  |  | 240 | 158.85 | 0 | 240
Storage (General) | Storage_FloorM | 0 | 983 | 15 | 0.15 |  |  | 0 | 147.45 | 0 | 147.45
Electrical, Mechanical, Telephone Rooms | Mechanical/Electrical_FloorM | 0 | 357 | 15 | 0.15 |  |  | 0 | 53.55 | 0 | 53.55
IT Room (EPD 12) | IT-Room_FloorM | 0 | 179 | 15 | 0.15 |  |  | 0 | 26.85 | 0 | 26.85
Restrooms | Restroom_FloorM | 0 | 644 | 15 | 0.15 | 4*50/70 cfm per unit |  | 0 | 96.6 | 200 | 200
Lounge, Breakroom, or Waiting Area | BreakRoom/Kitchenette_FloorM | 8 | 232 | 15 | 0.15 |  |  | 120 | 34.8 | 0 | 120
Stairwell | Stairway_FloorM | 0 | 661 | 15 | 0.15 |  |  | 0 | 99.15 | 0 | 99.15
Corridor Area | Corridor_W_FloorM | 2 | 300 | 15 | 0.15 |  |  | 30 | 45 | 0 | 45
Corridor Area | Corridor_N_FloorM | 3 | 503 | 15 | 0.15 |  |  | 45 | 75.45 | 0 | 75.45
Corridor Area | Corridor_E_FloorM | 2 | 300 | 15 | 0.15 |  |  | 30 | 45 | 0 | 45
Corridor Area | Corridor_S_FloorM | 3 | 503 | 15 | 0.15 |  |  | 45 | 75.45 | 0 | 75.45
Plenum | Plenum_FloorM | 0 | 17876 | 0 | - |  |  | 0 |  | 0 | 0
Laboratory, Scientific | Lab_Core_FloorT | 107.075 | 4283 | 15 | 0.15 | 1 | 10612.3746 | 1606.125 | 642.45 | 4283 | 10612.3746
Laboratory, Scientific | Lab_N_FloorT | 57.45 | 2298 | 15 | 0.15 | 1 | 5693.9614 | 861.75 | 344.7 | 2298 | 5693.9614
Office Area (>250 square feet) | Enclosed_Office_W_FloorT | 8 | 1638 | 15 | 0.15 |  |  | 120 | 245.7 | 0 | 245.7
Office Area (>250 square feet) | Enclosed_Office_E_FloorT | 8 | 1638 | 15 | 0.15 |  |  | 120 | 245.7 | 0 | 245.7
Laboratory, Scientific | Lab_S_FloorT | 29.65 | 1186 | 15 | 0.15 | 1 | 2938.6589 | 444.75 | 177.9 | 1186 | 2938.6589
Laboratory, Scientific | Lab_FloorT | 27.8 | 1112 | 15 | 0.15 | 1 | 2755.3025 | 417 | 166.8 | 1112 | 2755.3025
Lounge, Breakroom, or Waiting Area | Lounge_FloorT | 16 | 1059 | 15 | 0.15 |  | 240 | 158.85 | 0 | 240 | 240
Storage (General) | Storage_FloorT | 0 | 983 | 15 | 0.15 |  |  | 147.45 | 0 | 147.45 | 147.45
Electrical, Mechanical, Telephone Rooms | Mechanical/Electrical_FloorT | 0 | 357 | 15 | 0.15 |  |  | 53.55 | 0 | 53.55 | 53.55
IT Room (EPD 12) | IT-Room_FloorT | 0 | 179 | 15 | 0.15 |  |  | 26.85 | 0 | 26.85 | 26.85
Restrooms | Restroom_FloorT | 0 | 644 | 15 | 0.15 | 4* 50/70 cfm per unit |  | 96.6 | 200 | 200 | 200
Lounge, Breakroom, or Waiting Area | BreakRoom/Kitchenette_FloorT | 8 | 232 | 15 | 0.15 |  |  | 34.8 | 0 | 34.8 | 34.8
Stairwell | Stairway_FloorT | 0 | 661 | 15 | 0.15 |  |  | 99.15 | 0 | 99.15 | 99.15
Corridor Area | Corridor_W_FloorT | 2 | 300 | 15 | 0.15 |  |  | 45 | 0 | 45 | 45
Corridor Area | Corridor_N_FloorT | 3 | 503 | 15 | 0.15 |  |  | 75.45 | 0 | 75.45 | 75.45
Corridor Area | Corridor_E_FloorT | 2 | 300 | 15 | 0.15 |  |  | 45 | 0 | 45 | 45
Corridor Area | Corridor_S_FloorT | 3 | 503 | 15 | 0.15 |  |  | 75.45 | 0 | 75.45 | 75.45
Plenum | Plenum_FloorT | 0 | 17876 | 0 | - |  |  |  | 0 | 0 | 0
Total (11 Space Type) | Total (54 Space) | 307 | 53627
Exhaust Fume Hood
Sash position | h (in) | h (ft) | cfm/hood | cfm/ft of hood
Fully open (29 in) | 29 | 2.4167 | 1288.0833 | 214.6806
At 18 in sash stop | 18 | 1.5 | 799.5 | 133.25
Closed (6 in) | 6 | 0.5 | 266.5 | 44.4167
*Source for every number: CEC TN 222188 (2019 Fume Hoods CASE report), Table 29. Per-hood basis , a 6 ft nominal hood, 5.33 ft workspace width, 100 fpm face velocity (Cal/OSHA §5154.1). Flow = sash opening area × face velocity. A "6-foot hood" is a nominal cabinet dimension. The actual sash opening is narrower because of the side posts and frame — 5.33 ft. So airflow is computed on 5.33 ft but expressed per 6 ft of nominal hood. That's the only subtlety in the calculation, and getting it wrong would overstate flow by 13%.
Exhaust Fume Hood
Type of hood | Space | Area (ft² ) | Hood length (ft) | Number of Hoods | Hood Exhaust Rate (cfm) @215 cfm/ft | Hood Exhaust Rate (cfm) @133 cfm/ft - At sash stop | Hood Exhaust Rate (cfm) @44 cfm/ft - closed | Schedule (Pre-1978, 1978–19970 | Schedule (1998–2007, 2008–2018) | Schedule (New Construction) | Note | Source
Fume Hood | Lab_Core_FloorG | 4283 | 79.7923 | 13.2987 | 17155.3424 | 10612.3746 | 3510.8608 | CAV (0.90 flat) | Manual VAV (0.50–0.56) | Auto-sash VAV (0.20–0.33) | Hood density: 18.63 ft per 1,000 ft² — Table 29's 95 ft of hood in a 5,100 ft² lab. | 2019 High Efficiency Fume Hoods in Laboratory Spaces CASE Report
Fume Hood | Lab_N_FloorG | 2298 | 42.8117 | 7.1353 | 9204.5241 | 5693.9614 | 1883.7166 | CAV (0.90 flat) | Manual VAV (0.50–0.56) | Auto-sash VAV (0.20–0.33)
Fume Hood | Lab_S_FloorG | 1186 | 22.0952 | 3.6825 | 4750.4637 | 2938.6589 | 972.1879 | CAV (0.90 flat) | Manual VAV (0.50–0.56) | Auto-sash VAV (0.20–0.33)
Fume Hood | Lab_Core_FloorM | 4283 | 79.7923 | 13.2987 | 17155.3424 | 10612.3746 | 3510.8608 | CAV (0.90 flat) | Manual VAV (0.50–0.56) | Auto-sash VAV (0.20–0.33)
Fume Hood | Lab_N_FloorM | 2298 | 42.8117 | 7.1353 | 9204.5241 | 5693.9614 | 1883.7166 | CAV (0.90 flat) | Manual VAV (0.50–0.56) | Auto-sash VAV (0.20–0.33)
Fume Hood | Lab_W_FloorM | 1638 | 30.5159 | 5.086 | 6560.9271 | 4058.62 | 1342.7014 | CAV (0.90 flat) | Manual VAV (0.50–0.56) | Auto-sash VAV (0.20–0.33)
Fume Hood | Lab_E_FloorM | 1638 | 30.5159 | 5.086 | 6560.9271 | 4058.62 | 1342.7014 | CAV (0.90 flat) | Manual VAV (0.50–0.56) | Auto-sash VAV (0.20–0.33)
Fume Hood | Lab_S_FloorM | 1186 | 22.0952 | 3.6825 | 4750.4637 | 2938.6589 | 972.1879 | CAV (0.90 flat) | Manual VAV (0.50–0.56) | Auto-sash VAV (0.20–0.33)
Fume Hood | Lab_FloorM | 1112 | 20.7166 | 3.4528 | 4454.0604 | 2755.3025 | 911.5286 | CAV (0.90 flat) | Manual VAV (0.50–0.56) | Auto-sash VAV (0.20–0.33)
Fume Hood | Lab_Core_FloorT | 4283 | 79.7923 | 13.2987 | 17155.3424 | 10612.3746 | 3510.8608 | CAV (0.90 flat) | Manual VAV (0.50–0.56) | Auto-sash VAV (0.20–0.33)
Fume Hood | Lab_N_FloorT | 2298 | 42.8117 | 7.1353 | 9204.5241 | 5693.9614 | 1883.7166 | CAV (0.90 flat) | Manual VAV (0.50–0.56) | Auto-sash VAV (0.20–0.33)
Fume Hood | Lab_S_FloorT | 1186 | 22.0952 | 3.6825 | 4750.4637 | 2938.6589 | 972.1879 | CAV (0.90 flat) | Manual VAV (0.50–0.56) | Auto-sash VAV (0.20–0.33)
Fume Hood | Lab_FloorT | 1112 | 20.7166 | 3.4528 | 4454.0604 | 2755.3025 | 911.5286 | CAV (0.90 flat) | Manual VAV (0.50–0.56) | Auto-sash VAV (0.20–0.33)
*ANSI Z9.5 is the American National Standard for Laboratory Ventilation, and Section 6.4 focuses on how and where lab exhaust air must be discharged to ensure safety, health, and code compliance.
*2025 California Title 24, Part 6, the prescriptive exhaust requirements for laboratory spaces are detailed in Section 140.9(c).
Background Data [To be deleted prior to publication]
Requirement | Description | Criterion | Value / Standard
Airflow Modulation | Reduce to minimum 10 ACH or pressurization limit | Pressure relationship | Negative relative to adjacent spaces
Variable Exhaust/Makeup Air | Coordinated VAV systems for pressurization | Pressure differential target | 0.01–0.05 in. w.c.
Fan Power Limit | ≤ 0.65 W/CFM (standard); ≤ 0.85 W/CFM (with filtration) | Infiltration modeling | Not the primary OA source; modeled as tightly controlled
Sash Closure Controls | Auto-close after 5 min inactivity with safety features | Envelope air barrier | Required per T24 standards
Makeup Air Compliance | Must meet Section 140.4(o) standards | Standard reference | ANSI Z9.5-2022, ASHRAE 62.1, ASHRAE 90.1

## Water Heater
Water Heater - Laboratory
Vintage | WH Type | Efficiency | Number of WH | Tank Volume (gal) | Tank Loss | Source
Existing | Gas | 0.8 | 1 | See table below for CZ-specific values: Climate Zone Water Heater Sizing and Loss Coefficients, Storage Volume column (col F) | See table below: Climate Zone Water Heater Sizing and Loss Coefficients, Standby Loss column (col G) | See table below for sources: Climate Zone Water Heater Sizing and Loss Coefficients
New Construction | Gas | 0.8 | 1 | See table below for CZ-specific values: Climate Zone Water Heater Sizing and Loss Coefficients, Storage Volume column (col F) | See table below: Climate Zone Water Heater Sizing and Loss Coefficients, Standby Loss column (col G) | See table below for sources: Climate Zone Water Heater Sizing and Loss Coefficients
Peak Hot Water Consumption
Space Name | Baseline WH Type [CEUS 2022] | Total Area (ft²) | Number of People | Hot Water Usage Specification (gal/hr per person) [T24, 2022, Appendix 5.4A , sheet: "2022 SpaceFuncData-Input"] | Peak Hot Water Usage (gal/hr) | Peak Hot Water Usage (gal/min) | Note
Lab_Core_FloorG | Gas* | 4283 | 107.075 | 0.18 | 19.2735 | 0.32122 | For space types marked with an asterisk (the ‘*’ symbol), the water‑heater type is listed as electric in Appendix 5.4A, sheet ‘2022 SpaceFuncData‑Input.’ However, we modified the value based on CEUS data, which indicates that gas is the primary fuel type.
Lab_N_FloorG | Gas* | 2298 | 57.45 | 0.18 | 10.341 | 0.17235
Enclosed_Office_W_FloorG | Gas* | 1638 | 8 | 0.18 | 1.44 | 0.024
Enclosed_Office_E_FloorG | Gas* | 1638 | 8 | 0.18 | 1.44 | 0.024
Lab_S_FloorG | Gas* | 1186 | 29.65 | 0.18 | 5.337 | 0.08895
Conference_FloorG | Gas* | 1112 | 37 | 0.09 | 3.33 | 0.0555
Lobby_FloorG | Gas | 1059 | 11 | 0.09 | 0.99 | 0.0165
Storage_FloorG | Gas* | 983 | 0 | 0 | 0 | 0
Mechanical/Electrical_FloorG | Gas* | 357 | 0 | 0.18 | 0 | 0
IT-Room_FloorG | Gas* | 179 | 0 | 0.18 | 0 | 0
Restroom_FloorG | Gas | 644 | 0 | 0 | 0 | 0
BreakRoom/Kitchenette_FloorG | Gas | 232 | 8 | 0.58 | 4.64 | 0.077333
Stairway_FloorG | Gas* | 661 | 0 | 0 | 0 | 0
Corridor_W_FloorG | Gas* | 300 | 2 | 0 | 0 | 0
Corridor_N_FloorG | Gas* | 503 | 3 | 0 | 0 | 0
Corridor_E_FloorG | Gas* | 299 | 1 | 0 | 0 | 0
Corridor_S_FloorG | Gas* | 503 | 3 | 0 | 0 | 0
Plenum_FloorG |  | 17876 | 0 | 0 | 0 | 0
Lab_Core_FloorM | Gas* | 4283 | 107.075 | 0.18 | 19.2735 | 0.32122
Lab_N_FloorM | Gas* | 2298 | 57.45 | 0.18 | 10.341 | 0.17235
Lab_W_FloorM | Gas* | 1638 | 40.95 | 0.18 | 7.371 | 0.12285
Lab_E_FloorM | Gas* | 1638 | 40.95 | 0.18 | 7.371 | 0.12285
Lab_S_FloorM | Gas* | 1186 | 29.65 | 0.18 | 5.337 | 0.08895
Lab_FloorM | Gas* | 1112 | 27.8 | 0.09 | 2.502 | 0.0417
Lounge_FloorM | Gas | 1059 | 16 | 0.09 | 1.44 | 0.024
Storage_FloorM | - | 983 | 0 | 0 | 0 | 0
Mechanical/Electrical_FloorM | Gas* | 357 | 0 | 0.18 | 0 | 0
IT-Room_FloorM | Gas* | 179 | 0 | 0.18 | 0 | 0
Restroom_FloorM | Gas | 644 | 0 | 0 | 0 | 0
BreakRoom/Kitchenette_FloorM | Gas | 232 | 8 | 0.58 | 4.64 | 0.077333
Stairway_FloorM | Gas* | 661 | 0 | 0 | 0 | 0
Corridor_W_FloorM | Gas* | 300 | 2 | 0 | 0 | 0
Corridor_N_FloorM | Gas* | 503 | 3 | 0 | 0 | 0
Corridor_E_FloorM | Gas* | 300 | 2 | 0 | 0 | 0
Corridor_S_FloorM | Gas* | 503 | 3 | 0 | 0 | 0
Plenum_FloorM |  | 17876 | 0 | 0 | 0 | 0
Lab_Core_FloorT | Gas* | 4283 | 107.075 | 0.18 | 19.2735 | 0.32122
Lab_N_FloorT | Gas* | 2298 | 57.45 | 0.18 | 10.341 | 0.17235
Enclosed_Office_W_FloorT | Gas* | 1638 | 8 | 0.18 | 1.44 | 0.024
Enclosed_Office_E_FloorT | Gas* | 1638 | 8 | 0.18 | 1.44 | 0.024
Lab_S_FloorT | Gas* | 1186 | 29.65 | 0.18 | 5.337 | 0.08895
Lab_FloorT | Gas* | 1112 | 27.8 | 0.09 | 2.502 | 0.0417
Lounge_FloorT | Gas | 1059 | 16 | 0.09 | 1.44 | 0.024
Storage_FloorT | Gas* | 983 | 0 | 0 | 0 | 0
Mechanical/Electrical_FloorT | Gas* | 357 | 0 | 0.18 | 0 | 0
IT-Room_FloorT | Gas* | 179 | 0 | 0.18 | 0 | 0
Restroom_FloorT | Gas | 644 | 0 | 0 | 0 | 0
BreakRoom/Kitchenette_FloorT | Gas | 232 | 8 | 0.58 | 4.64 | 0.077333
Stairway_FloorT | Gas* | 661 | 0 | 0 | 0 | 0
Corridor_W_FloorT | Gas* | 300 | 2 | 0 | 0 | 0
Corridor_N_FloorT | Gas* | 503 | 3 | 0 | 0 | 0
Corridor_E_FloorT | Gas* | 300 | 2 | 0 | 0 | 0
Corridor_S_FloorT | Gas* | 503 | 3 | 0 | 0 | 0
|  | 17876 | 0 | 0 | 0 | 0
Total | Gas storage |  |  |  | 151.4805 |  | Minimum peak hot water usage is 75 gal according to ACM 2025
Total | Electric resistance |  |  |  | 0
Design supply temperature (°F) | 135 | CEC-400-2022-009-CMF-REV2-AP5.4B
WH system factor | 0.6 | 2025 ACM §5.9.2 Rated Capacity
Water mass conversion (lb/gal) | 8.2877 | 2025 ACM §5.9.2 Rated Capacity
Reheat multiplier | 0.4 | 2025 ACM §5.9.2 Storage Volume
Climate Zone Water Heater Sizing and Loss Coefficients
Climate Zone | Minimum Monthly Mains Temp (°F) [T24 2022 - Appendix 5.4B] | Heat Output (Btu/hr) [ACM, 2025, 5.9.2: Rated capacity section] | WH Capacity (Btu/hr) [ACM, 2025, 5.9.2: Rated capacity section] | Required Energy Input (Btu/hr) | Storage Volume (gal) | Standby Loss [Title 20, §1605.1 Table F-4; Appendix B: Water Heating Calculation Method] |  | Off/On Cycle Loss Coefficient to Ambient Temp |  | Source/Note
CZ01 | 47.9 | 109347.5123 | 65608.5074 | 99900 | 65 | 1011.7234 | Btu/hr | 14.4532 | Btu/h·°F | Required Energy Input: vendor/available catalog size (Market data table). Storage Volume: standard/available catalog tank size (Market data table).
CZ02 | 50.8 | 105706.7799 | 63424.068 | 80000 | 65 | 986.8484 | Btu/hr | 14.0978 | Btu/h·°F
CZ03 | 52.2 | 103949.185 | 62369.511 | 80000 | 65 | 986.8484 | Btu/hr | 14.0978 | Btu/h·°F
CZ04 | 52.7 | 103321.4725 | 61992.8835 | 80000 | 65 | 986.8484 | Btu/hr | 14.0978 | Btu/h·°F
CZ05 | 51.6 | 104702.44 | 62821.464 | 80000 | 65 | 986.8484 | Btu/hr | 14.0978 | Btu/h·°F
CZ06 | 56.8 | 98174.2303 | 58904.5382 | 75100 | 65 | 980.7234 | Btu/hr | 14.0103 | Btu/h·°F
CZ07 | 58.4 | 96165.5504 | 57699.3302 | 75100 | 65 | 980.7234 | Btu/hr | 14.0103 | Btu/h·°F
CZ08 | 58.4 | 96165.5504 | 57699.3302 | 75100 | 65 | 980.7234 | Btu/hr | 14.0103 | Btu/h·°F
CZ09 | 57.6 | 97169.8903 | 58301.9342 | 75100 | 65 | 980.7234 | Btu/hr | 14.0103 | Btu/h·°F
CZ10 | 57.1 | 97797.6028 | 58678.5617 | 75100 | 65 | 980.7234 | Btu/hr | 14.0103 | Btu/h·°F
CZ11 | 50.5 | 106083.4074 | 63650.0445 | 80000 | 65 | 986.8484 | Btu/hr | 14.0978 | Btu/h·°F
CZ12 | 51.4 | 104953.525 | 62972.115 | 80000 | 65 | 986.8484 | Btu/hr | 14.0978 | Btu/h·°F
CZ13 | 51.7 | 104576.8975 | 62746.1385 | 80000 | 65 | 986.8484 | Btu/hr | 14.0978 | Btu/h·°F
CZ14 | 50.1 | 106585.5774 | 63951.3464 | 80000 | 65 | 986.8484 | Btu/hr | 14.0978 | Btu/h·°F
CZ15 | 63.2 | 90139.5107 | 54083.7064 | 75100 | 65 | 980.7234 | Btu/hr | 14.0103 | Btu/h·°F
CZ16 | 41.4 | 117507.7744 | 70504.6646 | 99900 | 65 | 1011.7234 | Btu/hr | 14.4532 | Btu/h·°F
Market data
Catalog gas input (Btu/h) | Input source | Elec resistance tank (kW) | Elec resistance (Btu/h) | Catalog gas tank (gal) | Tank source | Elec tank (gal) | Elec tank source | Sources and links → Note tab
60000 | Grainger | 1.5 | 5118 | 34 | ENERGY STAR | 6 | Grainger
75100 | Grainger | 2 | 6824 | 35 | Grainger | 10 | Grainger
76000 | Both | 3 | 10236 | 48 | Grainger | 15 | Grainger
80000 | Grainger | 4.5 | 15355 | 50 | Both | 20 | Grainger
99900 | ENERGY STAR | 6 | 20473 | 55 | ENERGY STAR | 28 | Grainger
100000 | Both | 8 | 27297 | 60 | ENERGY STAR | 30 | Grainger
120000 | ENERGY STAR | 9 | 30709 | 65 | Both | 36 | Grainger
125000 | Both | 10 | 34121 | 72 | Grainger | 40 | Grainger
130000 | Both | 12 | 40946 | 75 | Both | 47
145000 | ENERGY STAR | 12.1 | 41287 | 76 | Grainger | 50
150000 | ENERGY STAR | 18 | 61419 | 80 | Both | 65
156000 | Grainger | 24 | 81891 | 82 | Grainger | 80
160000 | Both | 27 | 92128 | 85 | Grainger | 85
175000 | ENERGY STAR | 36 | 122837 | 90 | Both | 105
180000 | Grainger | 54 | 184256 | 91 | Grainger | 120
199000 | ENERGY STAR |  |  | 100 | Both
199900 | Both |  |  | 110 | ENERGY STAR
200000 | ENERGY STAR |  |  | 119 | Both
250000 | Both |  |  | 125 | ENERGY STAR
251000 | ENERGY STAR
270000 | Grainger
285000 | ENERGY STAR
300000 | Both
320000 | ENERGY STAR
360000 | Grainger
398000 | ENERGY STAR
399000 | ENERGY STAR
399900 | Both
499900 | Grainger
550000 | Grainger
715000 | Grainger

## Interior Lights
Interior Lighting - Laboratory
Space Type | New Construction |  |  | Existing |  |  | Notes
| Lighting density (W/ft²) | Additional LPD for Portable Lighting (W/ft²) | Source | LPD (W/ft²) | Additional LPD for Portable Lighting (W/ft²) | Source
Laboratory, Scientific | 0.9 | 0.35 | T24, part 6, 2025, Table 140.6 C (Area category method) | 1.4 |  | T24, part 6, 2016, Table 140.6 C (Area category method) | Additional lighting for: Detailed Task Work
Office Area (>250 square feet) | 0.6 | 0.1 |  | 0.75 |  |  | Additional lighting for: decorative/display It is assumed that 50% of the additional allowance lighting is in use.
Convention, Conference, Multipurpose and Meeting Area | 0.75 |  |  | 1.2
Lobby, Main Entry | 0.7 | 0.25 |  | 0.95 | 0.5 |  | Additional lighting for: decorative/display
Storage (General) | 0.4 |  |  | 0.6
Electrical, Mechanical, Telephone Rooms | 0.4 |  |  | 0.55
IT Room (EPD 12) | 0.75 |  |  | 1.2
Restrooms | 0.65 |  |  | 0.6
Lounge, Breakroom, or Waiting Area | 0.55 | 0.25 |  | 0.9 | 0.5 |  | Additional lighting for: decorative/display
Stairwell | 0.6 |  |  | 0.6
Corridor Area | 0.4 |  |  | 0.6

## Ext Lighting
Exterior Lighting - Laboratory
Motion Controlled Luminaires (W) | Non-motion Controlled Luminaires (W) | Total (W) | Source
2533.08 | 1392.3 | 3925.38 | T24, 2022 & 2025 2019 Outdoor Lighting CASE report PNNL 90.1-2010 TSD
Exterior Lighting
Items (Assume LZ2) | Assumptions [2019 Outdoor Lighting CASE Report] |  | Unit | Lighting Power Allowance (T24, part 6, 2025, Table 140.7-A & 140.7-B) | Unit | Exterior Lighting Power (W)
IWA (Initial Wattage Allowance) | Lighting Zone 3 |  |  | 350 | (W) | 350
Parking area | 400 ft² for every parking space [2019 Lighting CASE report, Appendix H] 1 parking space per 250 ft² of gross building area [2019 Lighting CASE report,Table 38] | 85803.2 | (ft²) | 0.025 | (W/ft²) | 2145.08
Building Entrance | 2 building entrance | 2 | (count) | 19 | (W/ea) | 38
Hardscape Ornamental Light | 0.1 ft² per 1 ft² of gross building area for hardscape ornamental light [2019 Lighting CASE report,Table 36] | 0 | (ft²) | 0.013 | (W/ft²) | 0
Building façade | 0.1 W per 1 ft² of facade area Façade Area = Perimeter × 0.5 × 30 ft (30 ft is the max height that is lit) * The 0.5 factor assumes that only half of the perimeter walls are lit. [2019 Lighting CASE report] | 8190 | (ft²) | 0.17 | (W/ft²) | 1392.3
Non-sales canopy |  |  | (ft²) | 0.27 | (W/ft²) | 0
Motion Controlled Luminaires (W) | [5 empty] | 2533.08
Non-motion-controlled Luminaires | [5 empty] | 1392.3
Total | [5 empty] | 3925.38
Total floor area | 53627
Perimeter | 546
Floors | 3

## Equipment
Equipment - Laboratory
Space Type | Plug load Intensity (W/ft²) | Gas Power Density (Btu/hr-ft²) | Refrigeration Power Density (W/ft²) | Source
Office Area (>250 square feet) | 0.7 |  |  | Proposed Updates to Equipment Power Densities and Schedules in the 2028 Energy Code Nonresidential and Multifamily Alternative Calculation Method (NRMFACM) Reference Manual, August 7, 2025
Laboratory, Scientific | 4 | 12.6926 | 0.28 | The Plug load density is set based on the LBNL/DOE Prototype. The gas power density and the refrig power density are based onT24 2025 - Appendix 5.4A
Convention, Conference, Multipurpose and Meeting Area | 1 |  |  | T24 2025 - Appendix 5.4A
Lobby, Main Entry | 0.5
Storage (General) | 0.2
Electrical, Mechanical, Telephone Rooms | 3
IT Room (EPD 12) | 12 |  |  | Feedback from TAG team
Restrooms | 0 |  |  | T24 2025 - Appendix 5.4A
Lounge, Breakroom, or Waiting Area | 1
Stairwell | 0
Corridor Area | 0
Elevator
Vintage | Class | Number of elevators (ne) | Cab Lighting Power Limit (W/ft2) | Fan Power Limit (W/CFM) | Cab Ventilation Fan & Lighting Shutoff | Design Motor Load (W) | Fan Load (W) | Lighting Load (W) | Total (W) | Note
Existing | F/G | 2 | 1.14 | 0.33 | When stopped and unoccupied with doors closed for over 15 minutes, cab interior lighting and ventilation shall be de-energized until required for operation. | 21656.57 | 165 | 68.17 | 21889.74 | Design load is calculated according to ISO 25745-2 method using Class F/G. Cab lighting and fan requirements are based on ASHRAE 90.1 2013.
New Construction | E | 2 | 0.6 | 0.33 | When the elevator cab is stopped and unoccupied with doors closed for over 15 minutes, the cab interior lighting and ventilation fans shall be switched off until elevator cab operation resumes. | 11273.07 | 165 | 35.88 | 11473.95 | Design load is calculated according to ISO 25745-2 method using Class E. Cab lighting and fan requirements are based on T24 2025 §120.6 (f).
Lab Elevator Calculations
Symbol | Definition | Value | Units | Source
E | Annual energy consumption of the elevator - Existing | 31370.62 | kWh/year | Calculated
| Annual energy consumption of the elevator - New Construction | 16329.61 | kWh/year | Calculated
C1 | Running-energy coefficient | 3.65 for Class E; 5.47 for Class F | Coefficient | ISO 25745-2 Table 7
C2 | Idle/standby coefficient | 800 for Class E; 1,600 for Class F | Coefficient | ISO 25745-2 Table 7
Q | Rated load of elevator | 1361 | kg | Assumed for all prototypes
Elevator Size | Cab floor area | 29.9 | ft^2 | W=6.781 ft, L=4.406 ft; assumed based on representative manufacturer
CFM | Cab fan airflow | 250 | cfm | Assumed for multifamily and commercial prototypes
cat | Usage category | 2 | - | ISO 25745-2 Table A.1
d | Operating days per year | 260 | days/year | ISO 25745-2 Table A.1
nf | Number of floors | 3 | floors | Prototype assumptions
h | Floor-to-floor height | 3.96 | m | Prototype assumptions
v | Elevator lift speed | 1 | m/s | ISO 25745-2 Table A.1
nd | Number of trips per day | 125 | trips/day | ISO 25745-2 Table A.1
S_pct | Percent of average travel distance | 0.67 | % | ISO 25745-2 Table 2
a | Acceleration | 1 | m/s^2 | Annex B of ISO 25745-2
j | Jerk | 1.25 | m/s^3 | Annex B of ISO 25745-2
td | Door time | 8 | seconds | Annex B of ISO 25745-2
S_av | Average distance traveled per trip | 7.96 | m/trip | Calculated (nf * h * S_pct)
t_av | Average trip time | 17.76 | seconds/trip | Calculated (S_av/v + v/a + a/j + td)
t_nr | Time not running per day | 23.38 | hours/day | Calculated (24 - nd * t_av)
Standby Hours | Annual standby hours | 8599.67 | hours/year | Calculated (24*(365-d)+t_nr*d)
Total light level | Total light level | 40 | lm/ft2 | PNNL Prototypes
EFLH | Equivalent full load hours | 1448.55 | hours | Calculated using the elevator schedule

## Schedules
Schedules - Laboratory
Zone | Schedule | Source | Zone | Type | Hour
[5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Laboratory | Lab | Occupancy | T24 2022 - Appendix 5.4B, [Lab] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.9 | 0.9 | 0.45 | 0.45 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Laboratory | Lab | Lights | T24 2022 - Appendix 5.4B, [Lab] | Weekday | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2
|  |  |  | Saturday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
|  |  |  | Sunday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Laboratory | Lab | ElecEquipment | T24 2022 - Appendix 5.4B, [Lab] | Weekday | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.5 | 0.7 | 0.8 | 0.5 | 0.6 | 0.7 | 0.9 | 0.8 | 0.5 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Laboratory | Lab | ServiceHotWater | Based on the Medium Office Prototype | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05
|  |  |  | Saturday | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04
|  |  |  | Sunday | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04
Laboratory | Lab | GasEquipment | T24 2022 - Appendix 5.4B, [Lab] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.9 | 0.9 | 0.45 | 0.45 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1 | 0.1 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0
Laboratory | Lab | Refrigeration | T24 2022 - Appendix 5.4B, [Lab] | Weekday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Saturday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Sunday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
Laboratory | Lab | Infiltration | T24 2022 - Appendix 5.4B, [Lab] | Weekday | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  |  | Saturday | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  |  | Sunday | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Laboratory | Lab | HVACAvail | T24 2022 - Appendix 5.4B, [Lab] | Weekday | bar: Hour 1 to Hour 24
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
Laboratory | Lab | ExhaustCAV | T24 2022 - Appendix 5.4B, [Lab] | Weekday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Saturday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Sunday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
Laboratory | Lab | ExhaustVAVManualSashCtrl | T24 2022 - Appendix 5.4B, [Lab] | Weekday | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.51 | 0.56 | 0.56 | 0.53 | 0.53 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.52 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  |  | Saturday | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.52 | 0.52 | 0.52 | 0.52 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  |  | Sunday | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.52 | 0.52 | 0.52 | 0.52 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Laboratory | Lab | ExhaustVAVAutoSashCtrl | T24 2022 - Appendix 5.4B, [Lab] | Weekday | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.21 | 0.22 | 0.33 | 0.33 | 0.26 | 0.26 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.24 | 0.21 | 0.21 | 0.21 | 0.2 | 0.2
|  |  |  | Saturday | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.21 | 0.21 | 0.24 | 0.24 | 0.24 | 0.24 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
|  |  |  | Sunday | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.21 | 0.21 | 0.24 | 0.24 | 0.24 | 0.24 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Laboratory | Lab | HtgSetpt | T24 2022 - Appendix 5.4B, [Office] | Weekday | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 68 | 68 | 68 | 68 | 68 | 68
|  |  |  | Saturday | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 68 | 68 | 68 | 68 | 68 | 68
|  |  |  | Sunday | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 68 | 68 | 68 | 68 | 68 | 68
Laboratory | Lab | ClgSetpt | T24 2022 - Appendix 5.4B, [Office] | Weekday | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 78 | 78 | 78 | 78 | 78 | 78
|  |  |  | Saturday | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 78 | 78 | 78 | 78 | 78 | 78
|  |  |  | Sunday | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 78 | 78 | 78 | 78 | 78 | 78
Office
All Office zones except for IT Rooms, Lab, Stairway, and Mechanical_Electrical | Office | Occupancy | T24 2022 - Appendix 5.4B, [Office] Updated based on Plug load and schedules project with CEC, 2025 | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
All Office zones except for IT Rooms, Lab, Stairway, and Mechanical_Electrical | Office | Lights | T24 2022 - Appendix 5.4B, [Office] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.35 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
All Office zones except for IT Rooms, Lab, Stairway, and Mechanical_Electrical | Office | ElecEquipment | Plug load and schedules project with CEC, 2025 | Weekday | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.74 | 0.87 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.5 | 0.45 | 0.45 | 0.45
|  |  |  | Saturday | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43
|  |  |  | Sunday | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43
All Office zones except for IT Rooms, Lab, Stairway, and Mechanical_Electrical | Office | HVACAvail | T24 2022 - Appendix 5.4B, [Office] Updated based on Plug load and schedules project with CEC, 202 | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
All Office zones except for IT Rooms, Lab, Stairway, and Mechanical_Electrical | Office | ServiceHotWater | T24 2022 - Appendix 5.4B, [Office] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05
|  |  |  | Saturday | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04
|  |  |  | Sunday | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04
All Office zones except for IT Rooms, Lab, Stairway, and Mechanical_Electrical | Office | Infiltration | T24 2022 - Appendix 5.4B, [Office] Updated based on Plug load and schedules project with CEC, 202 | Weekday | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
All Office zones except for IT Rooms, Lab, Stairway, and Mechanical_Electrical | Office | HtgSetpt | T24 2022 - Appendix 5.4B, [Office] | Weekday | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
|  |  |  | Saturday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  |  | Sunday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
All Office zones except for IT Rooms, Lab, Stairway, and Mechanical_Electrical | Office | ClgSetpt | T24 2022 - Appendix 5.4B, [Office] | Weekday | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
|  |  |  | Saturday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
|  |  |  | Sunday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
Data
IT room | Data | Occupancy | T24 2022 - Appendix 5.4B, [Data] Updated based on office schedule | Weekday | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.25 | 0.65 | 0.65 | 0.65 | 0.65 | 0.6 | 0.6 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.25 | 0.1 | 0.05 | 0.05 | 0.05 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0
IT room | Data | Lights | T24 2022 - Appendix 5.4B, [Data] Updated based on office schedule | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.7 | 0.8 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.8 | 0.35 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05
IT room | Data | HVACAvail | T24 2022 - Appendix 5.4B, [Data] | Weekday | bar: Hour 1 to Hour 24
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
IT room | Data | ServiceHotWater | T24 2022 - Appendix 5.4B, [Data] | Weekday | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.9 | 0.9 | 0.5 | 0.5 | 0.7 | 0.5 | 0.5 | 0.5 | 0.1 | 0.1 | 0.1 | 0.1 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IT room | Data | Infiltration | T24 2022 - Appendix 5.4B, [Data] | Weekday | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  |  | Saturday | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  |  | Sunday | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
IT room | Data | ClgSetpt | Based on Activity level and thermostat setpoint | Weekday | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
|  |  |  | Saturday | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
|  |  |  | Sunday | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
Other
Stairway | Building | Elevator | T24 2022 - Appendix 5.4B, [Office] Updated based on Plug load and schedules project with CEC, 202 | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.69 | 0.43 | 0.37 | 0.43 | 0.58 | 0.48 | 0.37 | 0.37 | 0.46 | 0.62 | 0.2 | 0.12 | 0.04 | 0.04 | 0 | 0 | 1448.55
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Building | ExtLightingNonMotionCtrl |  | Weekday | bar: Hour 1 to Hour 24
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
| Building | ExtLightingMotionCtrl |  | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Office | Building | FunctionalAreaPeopleActivityLevel | Based on Activity level schedules in CEC Prototypes | Weekday | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132
|  |  |  | Saturday | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132
|  |  |  | Sunday | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132
IT room | Building | ComputerRoomPeopleActivityLevel | Based on Activity level schedules in CEC Prototypes | Weekday | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
|  |  |  | Saturday | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
|  |  |  | Sunday | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
Conference room | Building | MeetingAreaPeopleActivityLevel | Based on Activity level schedules in CEC Prototypes | Weekday | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117
|  |  |  | Saturday | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117
|  |  |  | Sunday | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117
Corridor, Stair, Lobby, Restroom, Mech, Storage, Break | Building | CommonAreaPeopleActivityLevel | Based on Activity level schedules in CEC Prototypes | Weekday | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147
|  |  |  | Saturday | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147
|  |  |  | Sunday | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147
Ancillary
Stairway, Mechanical | Ancillary | Occupancy | T24 2022 - Appendix 5.4B, [Office] Updated based on Plug load and schedules project with CEC, 2025 | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
Stairway, Mechanical | Ancillary | Lights | T24 2022 - Appendix 5.4B, [Office] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.35 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Stairway, Mechanical | Ancillary | ElecEquipment | Plug load and schedules project with CEC, 2025 | Weekday | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.74 | 0.87 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.5 | 0.45 | 0.45 | 0.45
|  |  |  | Saturday | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43
|  |  |  | Sunday | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43
Stairway, Mechanical | Ancillary | HVACAvail | T24 2022 - Appendix 5.4B, [Office] Updated based on Plug load and schedules project with CEC, 202 | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stairway, Mechanical | Ancillary | ServiceHotWater | T24 2022 - Appendix 5.4B, [Office] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05
|  |  |  | Saturday | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04
|  |  |  | Sunday | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04
Stairway, Mechanical | Ancillary | Infiltration | T24 2022 - Appendix 5.4B, [Office] Updated based on Plug load and schedules project with CEC, 202 | Weekday | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
Stairway, Mechanical | Ancillary | HtgSetpt | T24 2022 - Appendix 5.4B, [Office] | Weekday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  |  | Saturday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  |  | Sunday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Stairway, Mechanical | Ancillary | ClgSetpt | T24 2022 - Appendix 5.4B, [Office] | Weekday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
|  |  |  | Saturday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
|  |  |  | Sunday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85

## Energy Usage
CalBEM Energy Consumption - Laboratory | [11 empty] | Energy Consumption - Laboratory
Prototype | CZ | CalBEM Electricity EUI (KBTU/ft²) | CalBEM Gas EUI (KBTU/ft²) | CalBEM Total EUI (KBTU/ft²) | New Construction Electricity EUI (KBTU/ft²) | New Construction Gas EUI (KBTU/ft²) | New Construction Total EUI (KBTU/ft²) | National Average | Acceptable Range (25% Higher) | Acceptable Range (25% Lower) | National Average Acceptable EUI Range | Prototype | CZ | Total Floorspace (Thousand of ft²) | CEUS 2023 Electricity EUI (kBtu/ft²) | CEUS 2023 Gas EUI (kBtu/ft²) | CEUS 2023 Total EUI (kBtu/ft²) | Acceptable Range (20% Higher) | Acceptable Range (20% Lower) | CEUS 2022 Acceptable EUI Range
Laboratory | 1 | [6 empty] | 135.3 | 169.125 | 101.475 | 67.65 | Laboratory | 1 |  |  |  |  | 0 | 0 | 0
| 2 | [6 empty] | 135.3 | 169.125 | 101.475 | 67.65 |  | 2 |  |  |  |  | 0 | 0 | 0
| 3 | [6 empty] | 135.3 | 169.125 | 101.475 | 67.65 |  | 3 |  |  |  |  | 0 | 0 | 0
| 4 | [6 empty] | 135.3 | 169.125 | 101.475 | 67.65 |  | 4 |  |  |  |  | 0 | 0 | 0
| 5 | [6 empty] | 135.3 | 169.125 | 101.475 | 67.65 |  | 5 |  |  |  |  | 0 | 0 | 0
| 6 | [6 empty] | 135.3 | 169.125 | 101.475 | 67.65 |  | 6 |  |  |  |  | 0 | 0 | 0
| 7 | [6 empty] | 135.3 | 169.125 | 101.475 | 67.65 |  | 7 |  |  |  |  | 0 | 0 | 0
| 8 | [6 empty] | 135.3 | 169.125 | 101.475 | 67.65 |  | 8 |  |  |  |  | 0 | 0 | 0
| 9 | [6 empty] | 135.3 | 169.125 | 101.475 | 67.65 |  | 9 |  |  |  |  | 0 | 0 | 0
| 10 | [6 empty] | 135.3 | 169.125 | 101.475 | 67.65 |  | 10 |  |  |  |  | 0 | 0 | 0
| 11 | [6 empty] | 135.3 | 169.125 | 101.475 | 67.65 |  | 11 |  |  |  |  | 0 | 0 | 0
| 12 | [6 empty] | 135.3 | 169.125 | 101.475 | 67.65 |  | 12 |  |  |  |  | 0 | 0 | 0
| 13 | [6 empty] | 135.3 | 169.125 | 101.475 | 67.65 |  | 13 |  |  |  |  | 0 | 0 | 0
| 14 | [6 empty] | 135.3 | 169.125 | 101.475 | 67.65 |  | 14 |  |  |  |  | 0 | 0 | 0
| 15 | [6 empty] | 135.3 | 169.125 | 101.475 | 67.65 |  | 15 |  |  |  |  | 0 | 0 | 0
| 16 | [6 empty] | 135.3 | 169.125 | 101.475 | 67.65 |  | 16 |  |  |  |  | 0 | 0 | 0
Ref: CEUS 2022 Report
And converted FZ level data to CZ level
CEUS has only one category for healthcare.

## Weights
% of Floor Area per CZ and Vintage Bin - Laboratory | [6 empty] | % of Floor Area per CZ and Vintage Bin - Laboratory
Prototype | CZ | Vintage Bin |  |  |  |  | Prototype | Vintage Bin | CZ
|  | Pre-1978 | 1978-1997 | 1998-2007 | 2008-2018 |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
Laboratory | 1 | 62.54% | 25.02% | 8.627% | 3.817% | 100% | Laboratory | Pre-1978 | 0.6498% | 1.202% | 19.18% | 10.98% | 0.1407% | 7.539% | 2.549% | 13.18% | 19.2% | 2.24% | 1.95% | 13.43% | 2.979% | 0.8729% | 1.53% | 2.374% | 100%
| 2 | 49.16% | 36.43% | 14.39% | 0.01642% | 100% |  | 1978-1997 | 0.2479% | 0.8493% | 16.22% | 9.084% | 0.5373% | 8.723% | 7.776% | 14.8% | 19.39% | 5.452% | 0.6412% | 10.68% | 0.5403% | 1.647% | 0.8097% | 2.588% | 100%
| 3 | 40.12% | 35.58% | 16.08% | 8.216% | 100% |  | 1998-2007 | 0.2092% | 0.8213% | 17.94% | 10.22% | 0.0627% | 8.23% | 7.707% | 9.914% | 10.77% | 8.53% | 1.422% | 13.82% | 0.4026% | 2.06% | 2.99% | 4.898% | 100%
| 4 | 40.48% | 35.11% | 16.14% | 8.268% | 100% |  | 2008-2018 | 0.1915% | 0.0019% | 18.97% | 10.83% | 0.1127% | 7.07% | 5.162% | 9.395% | 15.27% | 6.583% | 1.777% | 15.24% | 1.044% | 1.208% | 4.34% | 2.8% | 100%
| 5 | 18.66% | 74.68% | 3.564% | 3.094% | 100%
| 6 | 34.78% | 42.2% | 16.27% | 6.754% | 100% |  | Total | 0.3871% | 0.9108% | 17.81% | 10.11% | 0.281% | 8.076% | 5.616% | 13% | 17.63% | 4.834% | 1.341% | 12.56% | 1.466% | 1.39% | 1.699% | 2.893% | 100%
| 7 | 16.91% | 54.09% | 21.91% | 7.091% | 100%
| 8 | 37.77% | 44.49% | 12.17% | 5.575% | 100%
| 9 | 40.58% | 42.98% | 9.756% | 6.683% | 100%
| 10 | 17.27% | 44.06% | 28.17% | 10.51% | 100%
| 11 | 54.17% | 18.68% | 16.93% | 10.22% | 100%
| 12 | 39.85% | 33.23% | 17.56% | 9.362% | 100%
| 13 | 75.72% | 14.4% | 4.383% | 5.494% | 100%
| 14 | 23.39% | 46.26% | 23.64% | 6.701% | 100%
| 15 | 33.56% | 18.62% | 28.1% | 19.71% | 100%
| 16 | 30.57% | 34.94% | 27.02% | 7.466% | 100%
| Statewide | 37.26% | 39.07% | 15.96% | 7.714% | 100%
Ref: CEUS 2022 dataset: Large Office group. CEUS doesn't have specific weights for laboratories.

## PV (hidden)
PV - Laboratory
TBD

## EV Charger (hidden)
EV Charger - Laboratory
TBD
Background Data [To be deleted prior to publication]

## Data (hidden)
Space Function | Exhaust Required? | Electric Equipment Load Intensity | Electric Equipment Load Intensity | LPD
Aging Eye/Low-vision (Corridor Area) |  |  |  | 2013 | 2016 | 2019 | 2025
Aging Eye/Low-vision (Dining)
Aging Eye/Low-vision (Lobby, Main Entry)
Aging Eye/Low-vision (Lounge/Waiting Area)
Aging Eye/Low-vision (Multipurpose Room)
Aging Eye/Low-vision (Religious Worship Area)
Aging Eye/Low-vision (Restroom)
Aging Eye/Low-vision (Stairwell)
Audience Seating Area
Auditorium Area
Auto Repair / Maintenance Area
Barber, Beauty Salon, Spa Area
Civic Meeting Place Area
Classroom, Lecture, Training, Vocational Areas
Concourse and Atria Area
Convention, Conference, Multipurpose and Meeting Area
Copy Room | Yes
Corridor Area
Dining Area (Bar/Lounge and Fine Dining)
Dining Area (Cafeteria/Fast Food)
Dining Area (Family and Leisure)
Electrical, Mechanical, Telephone Rooms
Exercise/Fitness Center and Gymnasium Areas
Financial Transaction Area
Healthcare Facility and Hospitals (Exam/Treatment Room)
Healthcare Facility and Hospitals (Imaging Room)
Healthcare Facility and Hospitals (Medical Supply Room)
Healthcare Facility and Hospitals (Nursery)
Healthcare Facility and Hospitals (Nurse's Station)
Healthcare Facility and Hospitals (Operating Room)
Healthcare Facility and Hospitals (Patient Room)
Healthcare Facility and Hospitals (Physical Therapy Room)
Healthcare Facility and Hospitals (Recovery Room)
Hotel Function Area
Kitchen/Food Preparation Area | Yes
Kitchenette or Residential Kitchen | Yes
Laboratory, Scientific | Yes
Laundry Area | Yes
Library (Reading Area)
Library (Stacks Area)
Lobby, Main Entry
Locker Room | Yes
Lounge, Breakroom, or Waiting Area
Manufacturing, Commercial & Industrial Work Area (Low Bay)
Manufacturing, Commercial & Industrial Work Area (High Bay)
Manufacturing, Commercial & Industrial Work Area (Precision)
Museum Area (Exhibition/Display)
Museum Area (Restoration Room)
Office Area (>250 square feet)
Office Area (<250 square feet)
Parking Garage Area (Parking Zone and Ramps)
Parking Garage Area (Daylight Adaptation Zones)
Pharmacy Area
Retail Sales Area (Grocery Sales)
Retail Sales Area (Retail Merchandise Sales)
Retail Sales Area (Fitting Room)
Religious Worship Area
Restrooms
Stairwell
Storage, Commercial/Industrial (Warehouse)
Storage, Commercial/Industrial (Refrigerated)
Storage, Commercial/Industrial (Shipping & Handling)
Storage (General)
Sports Arena - Playing Area (> 5,000 Spectators)
Sports Arena - Playing Area (2,000 - 5,000 Spectators)
Sports Arena - Playing Area (< 2,000 Spectators)
Sports Arena - Playing Area (Recreational)
Theater Area (Motion Picture)
Theater Area (Performance)
Transportation Function (Baggage Area)
Transportation Function (Ticketing Area)
Videoconferencing Studio
High-Rise Residential Living Spaces
Hotel/Motel Guest Room
All other
Attic
Reception Area
Elevator
Plenum
IT Room (EPD 12)
Computer Room (EPD 20)
Server Room (EPD 45)