## Notes
Data Sources
Dataset | Dodge 2023
| Commercial End-Use Survey (CEUS) 2022 | https://www.energy.ca.gov/publications/2023/2022-california-commercial-end-use-survey-ceus-final-report
| Commercial Buildings Energy Consumption Survey (CBECS) 2018 | https://www.eia.gov/consumption/commercial/data/2018/
| ComStock 2023 | https://comstock.nlr.gov/page/datasets
| Database for Energy Efficient Resources (DEER) Grocery Store prototype (June 2023) | https://github.com/sound-data/DEER-Prototypes-EnergyPlus
| Oak Ridge National Laboratory (ORNL) (2019) Supermarket Building Energy Model | https://www.osti.gov/servlets/purl/3019970
Codes | Title 24, part 6, referred to as T24 (1984, 1992,1998, 2001, 2005, 2008, 2013, 2016,2019, 2022, 2025) | https://www.energy.ca.gov/publications/2025/2025-building-energy-efficiency-standards-residential-and-nonresidential | 2025
|  | https://codes.iccsafe.org/codes/united-states/california | 2010+
| American Society of Heating, Refrigerating and Air-Conditioning Engineers (ASHRAE) 90.1 (2022) | https://www.ashrae.org/technical-resources/standards-and-guidelines/read-only-versions-of-ashrae-standards
| Code of Federal Regulations (CFR) Title 10 (2010) | https://www.govinfo.gov/content/pkg/FR-2009-03-23/pdf/FR-2009-03-23.pdf
| CFR Title 10 (2024) | https://www.govinfo.gov/content/pkg/CFR-2024-title10-vol3/pdf/CFR-2024-title10-vol3-part431-subpartF.pdf
| Title 20 | https://govt.westlaw.com/calregs/Document/I270DCA634B4011EFA8F7F119BAF97AD6?viewType=FullText&originationContext=documenttoc&transitionType=CategoryPageItem&contextData=(sc.Default)
Others | Alternative Calculation Method (ACM) (2022) | https://www.energy.ca.gov/publications/2022/2022-nonresidential-and-multifamily-alternative-calculation-method-reference
| ACM (2025) | https://www.energy.ca.gov/publications/2025/2025-nonresidential-and-multifamily-alternative-calculation-method-reference
| Title 24, 2025, Appendix B: Water Heating Calculation Method | https://www.energy.ca.gov/sites/default/files/2025-11/CEC-400-2025-006-AP-B.pdf
| Nonres ACM 2022, Appendix 5.4A and Appendix 5.4B | https://www.energy.ca.gov/publications/2022/2022-nonresidential-and-multifamily-alternative-calculation-method-reference
| 2022 Reduced infiltration Codes and Standards Enhancement (CASE) report | https://title24stakeholders.com/wp-content/uploads/2020/10/2022-T24-Final-CASE-Report_Reduce-Infiltration.pdf
| 2019 Outdoor Lighting CASE Report | https://title24stakeholders.com/wp-content/uploads/2016/10/T24-2019-CASE-Study-Results-Report-Outdoor-Sources_Final_with-Attachments.pdf
| PNNL 20405, 2011 | https://www.pnnl.gov/main/publications/external/technical_reports/PNNL-20405.pdf
| Air leakage Memo, NORESCO, 2025 | Infiltration_rate_report_14May2025-Short-Version.docx
| Retail Building Guide for Entrance Energy Efficiency Measures (2012) | https://www.osti.gov/servlets/purl/1037934
| Yousefi, F., Athalye, R., (2025), "Determining Vintage Bins for Prototype Development: An Analysis of California Commercial Buildings," ASHRAE Annual Conference | https://www.thefreelibrary.com/Determining+Vintage+Bins+for+Prototype+Development%3a+An+Analysis+of...-a0879271125
| Proposed Updates to Equipment Power Densities and Building Schedules for the 2028 Energy Code, referred to as "Plug load and schedules project with CEC, 2025" (Docket Number =25-BSTD-03 & TN=265693) | https://efiling.energy.ca.gov/GetDocument.aspx?tn=265693&DocumentContentId=102545
| ENERGY STAR certified commercial water heaters | https://www.energystar.gov/productfinder/product/certified-commercial-water-heaters/results?fuel_filter=Gas&markets_filter=United+States
| Grainger gas tank water heaters (sizes below commercial, e.g. 30–75 kBtu/h) | https://www.grainger.com/category/plumbing/water-heaters/gas-tank-water-heaters
| Grainger electric tank water heaters | https://www.grainger.com/category/plumbing/water-heaters/electric-tank-water-heaters
Construction Rate
Notes
The grocery prototype represents the "big-box" stand-alone retail model typical of Ralph's, Safeway, Albertsons. Where needed, the Grocery and Medium Retail could be weighted to represent a Super Walmart type of space.
Background Data [To be deleted prior to publication]
Dodge categories 1, 4, and 101
Store only

## Prototype
NORESCO, Updated September 2026
RetailGrocery
Characteristic | Value | Data Sources
Building Type | Grocery
Building Category | Nonresidential
Version | v2-0
Vintages | 4 Vintages: Pre-1978 , 1978-1997 ,1998-2007 , 2008-2018 New Construction (2019+) | Based on the vintage bin analysis. A summary of the findings is presented in the following paper, with a link provided in the Notes tab: Yousefi, F., Athalye, R. (2025). “Determining Vintage Bins for Prototype Development: An Analysis of California Commercial Buildings.” ASHRAE Annual Conference.
Shape |  | Proposed Plan Based on Typical Grocery Store
Total Floor Area (ft²) | 50,000 (250 ft x 200 ft) | Proposed Plan Based on Typical Grocery Store
Aspect Ratio | 1.25 | Proposed Plan Based on Typical Grocery Store
Number of Floors | 1 | Proposed Plan Based on Typical Grocery Store
Roof type | Flat | Proposed Plan Based on Typical Grocery Store
WWR | 7.75% | Proposed Plan Based on Typical Grocery Store
Shading Geometry | N/A | Proposed Plan Based on Typical Grocery Store
Floor to floor height (feet) | N/A | Proposed Plan Based on Typical Grocery Store
Floor to ceiling height (feet) | 25 | Proposed Plan Based on Typical Grocery Store
Glazing sill height (feet) | 3 ft (top of the window is 10 ft high with 7 ft high glass) | CPUC (DEER 2023) Grocery prototype
Skylight-to-Roof-Ratio (SRR) | 2.3% | Title 24 Skylight Requirement
Background Data [To be deleted prior to publication]
Existing Grocery Prototypes
CPUC: Retail_Grocery
Geometry/ Floor plan |  |  | Zones of DEER prototype | Floor area | Share
Total floor area (ft²) | 49997 |  | IndLoadDock | 2850.9 | 5.702%
|  |  | RefWalkInCool | 1559.65 | 3.119%
|  |  | RefWalkInFreeze | 812.23 | 1.625%
|  |  | RefFoodPrep | 1267.01 | 2.534%
|  |  | Grocery Sale | 40007.28 | 80.02%
|  |  | Office | 3499.89 | 7%
49996.96
Other Existing Retail Prototypes
Large size prototype
| CEC: Retail_Large | CPUC: Retail_Multistory Large (Rt3) | CPUC: Retail_Single-Story Large (RtL)
Geometry
Total floor area (ft²) | 240000 | 120000 | 130502
Medium size prototype
| CEC: Retail_Medium |  |  | PNNL : Retail_Standalone | PNNL: Retail_Stripmall
Geometry | zoning same as PNNL Stand alone with more skylight
Total floor area (ft²) | 24692 |  |  | 24692 | 22500
Small size prototype
| CEC: Retail_Stripmall (Mixed use) | CPUC: Retail_Small (RtS)
Geometry
Total floor area (ft²) | 9375 | 8001

## Zones
Proposed Layout - RetailGrocery | [15 empty] | Spaces and Zoning layout - "Rn" indicates which refrigerated cases are in each zone.
Building | Space/Thermal Zone | Space Type [Primarily from: T24, 2022 Appendix 5.4A] - See Notes column | HVAC System Name (NC) | HVAC System Name (Existing) | Schedule Category | Conditioned (Y/N) | Area Fraction | Area (ft²) | Volume (ft³) | Multipliers | Number of People | People (Persons/1,000 ft²) [T24, 2025,Table 120.1-A] | Notes | --- 40 ft --- | --- 70ft --- | N --- 34 ft --- | 250' North Façade | --- 106 ft ---
RetailGrocery | Checkout Area | Retail Sales Area (Grocery Sales) | SZVAVHP_Checkout Area_NC | PSZAC_Checkout Area_Existing | Grocery | Yes | 20% | 10000 | 250000 | 1 | 170 | 17 |  | Back Office | Refr Food Prep | Walk-in Freezers | Loading Dock - Semi-Conditioned |  | 30 ft
RetailGrocery | Produce | Retail Sales Area (Grocery Sales) | SZVAVHP_Produce_NC | PSZAC_Produce_Existing | Grocery | Yes | 8.8% | 4400 | 110000 | 1 | 74.8 | 17 |  | (1200 sf) | 2100 sf) | Walk-in Coolers | (stock area) | 3200 sf
RetailGrocery | General Merch | Retail Sales Area (Grocery Sales) | SZVAVHP_General Merch_NC | PSZAC_General Merch_Existing | Grocery | Yes | 15.4% | 7700 | 192500 | 1 | 130.9 | 17 |  |  | 5000 sf (250'x20') | Meat and Dairy |  | R1, R2 | 20'
RetailGrocery | Frozen | Retail Sales Area (Grocery Sales) | SZVAVHP_Frozen_NC | SPSZAC_Frozen_Existing | Grocery | Yes | 13.2% | 6600 | 165000 | 1 | 112.2 | 17
RetailGrocery | Beverage | Retail Sales Area (Grocery Sales) | SZVAVHP_Beverage_NC | PSZAC_Beverage_Existing | Grocery | Yes | 8.8% | 4400 | 110000 | 1 | 74.8 | 17 |  | Produce | Grocery - General | Grocery - Frozen | Beverage | Bakery and Deli
RetailGrocery | Bakery and Deli | Retail Sales Area (Grocery Sales) | SZVAVHP_Bakery and Deli | PSZAC_Bakery and Deli_Existing | Grocery | Yes | 8.8% | 4400 | 110000 | 1 | 74.8 | 17
RetailGrocery | Meat and Dairy | Retail Sales Area (Grocery Sales) | SZVAVHP_Meat and Dairy | PSZAC_Meat and Dairy_Existing | Grocery | Yes | 10% | 5000 | 125000 | 1 | 85 | 17 | [6 empty] | 200' totalEastFacade
RetailGrocery | Back_Office | Lounge, Breakroom, or Waiting Area | SZVAVHP_Back Office | PSZAC_Back Office_Existing | Grocery | Yes | 2.4% | 1200 | 30000 | 1 | 6 | 5 |  | R4, R7 |  | R5 | R6, R9 | R3,R10
RetailGrocery | Loading Dock EL1 | Storage, Commercial/Industrial (Shipping & Handling) | SZVAVHP_Loading Dock EL1 | PSZAC_Loading Dock EL1_Existing | Ancillary | Yes | 6.4% | 3200 | 80000 | 1 | 6.4 | 2 |  | 4400 sf | 7700 sf | 6600 sf | 4400 sf | 4400 sf | 110'
RetailGrocery | Food Prep | Storage, Commercial/Industrial (Refrigerated) | - | - | Refrigeration | No | 4.2% | 2100 | 52500 | 1 | 0 | 0 |  | (40'x110') | (70'x110') | (60'x110') | (40'x110') | (40'x110')
RetailGrocery | RefWalkInCool Core | Storage, Commercial/Industrial (Refrigerated) | - | - | Refrigeration | No | 1% | 500 | 12500 | 1 | 0 | 0
RetailGrocery | Ref WalkInFreezer Core | Storage, Commercial/Industrial (Refrigerated) | - | - | Refrigeration | No | 1% | 500 | 12500 | 1 | 0 | 0
Total (1 Building) | Total (12 Thermal zones) | Total (4 Space Types) |  |  |  | Total (12 Conditioned zones) | 100% | 50000 | 1250000 |  | 734.9
Retail Sales Area (Grocery Sales)
Lounge, Breakroom, or Waiting Area
Storage, Commercial/Industrial (Shipping & Handling)
Storage, Commercial/Industrial (Refrigerated)
[16 empty] | Cashier area and front of the store |  |  | 40'
10,000 sf (250'*40')
N

## Envelope
Envelope - RetailGrocery
Element | Prototype | Assembly Type | Construction | Thermal Properties | Vintage | Selected T24 | Notes | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
External Wall | RetailGrocery | ExtWall_MetalFramed_NonRes | Metal frame + insulation + Gypsum board | U-factor IP | Pre 1978 | N/A | Using DOE pre-1980 U-values of 0.227 and a 6.1% cumulative wall renovation rate through 2028, based on the average annual rate from CBECS 2003 and 2012 projected over 48 years. | 0.21913 | 0.21694 | 0.21816 | 0.21694 | 0.21694 | 0.21913 | 0.21913 | 0.21694 | 0.21694 | 0.21694 | 0.21694 | 0.21694 | 0.21694 | 0.21694 | 0.21694 | 0.21694
[5 empty] | 1978-1997 | 1986 | Copied from low-rise office alternative table: Package A with heat capacity of 0-3.99 (Btu/F-ft²) | 0.13298 | 0.13298 | 0.13298 | 0.13298 | 0.13298 | 0.13298 | 0.13298 | 0.13298 | 0.13298 | 0.13298 | 0.13298 | 0.13298 | 0.13298 | 0.13298 | 0.13298 | 0.13298 | These values have better performance than the next vintage
[5 empty] | 1998-2007 | 2001 | Table 1-H | 0.182 | 0.182 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.098 | 0.062 | 0.082 | 0.062 | 0.062 | 0.098 | 0.098 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062
[5 empty] | Existing |  | Weighted average of all 4 vintages | 0.16456 | 0.17468 | 0.18227 | 0.18273 | 0.16758 | 0.18413 | 0.16609 | 0.18348 | 0.18051 | 0.15478 | 0.16201 | 0.16351 | 0.16016 | 0.17204 | 0.1469 | 0.15748
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.06 | 0.055 | 0.071 | 0.055 | 0.055 | 0.06 | 0.06 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055
Roof | RetailGrocery | FlatRoof_WoodFramedAndOther_NonRes | Built-up roof: Roof membrane+ insulation+metal decking | U-factor IP | Pre 1978 | N/A | Considering 30 years for roof/ insulation replacement. | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 1978-1997 | 1992 |  | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 1998-2007 | 2001 | Table 1-H | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.049 | 0.039 | 0.039 | 0.039 | 0.049 | 0.075 | 0.067 | 0.067 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039
[5 empty] | Existing |  | Weighted average of all 4 vintages | 0.05629 | 0.056327 | 0.056385 | 0.056357 | 0.056693 | 0.077538 | 0.077824 | 0.077861 | 0.07664 | 0.072249 | 0.055095 | 0.055311 | 0.055015 | 0.055679 | 0.054709 | 0.054695
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.047 | 0.047 | 0.047 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028
Window | RetailGrocery | FixedWindow_NonRes | CBECS 2018 shows that ~ 50 % of retail that were built before 2000 are single pane | U-factor IP | Pre 1978 | N/A | 2021 ASHRAE Handbook of Fundamentals - Section 15.9 Table 4 for single pane & T24, 2013 Table 140.3-B for double pane (50%-50%) | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74
[5 empty] | 1978-1997 | N/A |  | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74
|  |  | Double pane |  | 1998-2007 | 2001 | Table 1-H | 0.49 | 0.49 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36
[5 empty] | Existing |  | Weighted average of all 4 vintages | 0.68409 | 0.69385 | 0.7441 | 0.74401 | 0.74335 | 0.72879 | 0.73239 | 0.73247 | 0.7326 | 0.68066 | 0.66179 | 0.65597 | 0.68247 | 0.68525 | 0.68732 | 0.66247
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.34 | 0.36 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.36
|  | FixedWindow_NonRes | CBECS 2018 shows that ~ 50 % of retail that were built before 2000 are single pane | SHGC | Pre 1978 | N/A | 2021 ASHRAE Handbook of Fundamentals - Section 15.22 Table 10 for single pane & T24, 2013 Table 140.3-B for double pane (50%-50%) | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52
[5 empty] | 1978-1997 | N/A |  | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52
|  |  | Double pane |  | 1998-2007 | 2001 | Table 1-H (Non north 0-10%) | 0.49 | 0.47 | 0.61 | 0.61 | 0.61 | 0.61 | 0.61 | 0.61 | 0.61 | 0.47 | 0.47 | 0.47 | 0.47 | 0.46 | 0.46 | 0.49
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
[5 empty] | Existing |  | Weighted average of all 4 vintages | 0.49337 | 0.50351 | 0.53274 | 0.53258 | 0.53376 | 0.51549 | 0.51737 | 0.51688 | 0.5181 | 0.48699 | 0.48455 | 0.48611 | 0.48828 | 0.49318 | 0.48392 | 0.4823
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.22 | 0.25 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.25
Skylight | RetailMedium | Skylight | Translucent | U-factor IP | Pre 1978 | N/A | from 1992 code cycle | 0.85 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
[5 empty] | 1978-1997 | N/A |  | 0.85 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
|  |  | Plastic curb mounted |  | 1998-2007 | 2001 | Table 1-H | 0.87 | 1.1 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 0.87
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88
[5 empty] | Existing |  | Weighted average of all 4 vintages | 0.85444 | 1.2671 | 1.2929 | 1.2923 | 1.289 | 1.2876 | 1.2967 | 1.2981 | 1.2935 | 1.2491 | 0.88973 | 0.89897 | 0.8666 | 0.88027 | 0.8596 | 0.85505
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88
| RetailMedium | Skylight | Translucent | SHGC | Pre 1978 | N/A | From 1992 code cycle | 0.7047 | 0.7482 | 0.7482 | 0.7482 | 0.7482 | 0.7482 | 0.7482 | 0.7482 | 0.7482 | 0.7482 | 0.7047 | 0.7047 | 0.7047 | 0.7047 | 0.7047 | 0.7047
[5 empty] | 1978-1997 | N/A |  | 0.7047 | 0.7482 | 0.7482 | 0.7482 | 0.7482 | 0.7482 | 0.7482 | 0.7482 | 0.7482 | 0.7482 | 0.7047 | 0.7047 | 0.7047 | 0.7047 | 0.7047 | 0.7047
|  |  | Plastic curb mounted |  | 1998-2007 | 2001 | Table 1-H (For SRR 2.1-5%) | 0.58 | 0.62 | 0.65 | 0.65 | 0.65 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.58 | 0.58 | 0.58
[5 empty] | 2008-2018 | 2013 | There is no requirement in the code (considered same as 2001) | 0.58 | 0.62 | 0.65 | 0.65 | 0.65 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.58 | 0.58 | 0.58
[5 empty] | Existing |  | Weighted average of all 4 vintages | 0.68257 | 0.72703 | 0.72086 | 0.72032 | 0.71669 | 0.72921 | 0.73671 | 0.73888 | 0.73229 | 0.72607 | 0.68109 | 0.67763 | 0.68719 | 0.6835 | 0.68833 | 0.67367
[5 empty] | 2019+ | 2025 | There is no requirement in the code (considered same as 2001) | 0.58 | 0.62 | 0.65 | 0.65 | 0.65 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.58 | 0.58 | 0.58
Infiltration
|  |  | Building | Zones | Vintage | I_75 (cfm/ft²) 6-sdied Infiltration rate @ 75 pa | Note | I-design (cfm/ft²) (4-sided Infiltration rate at normal pressure) (Design flow rate approach and Flow/Exterior Wall Area calculation method)
|  | Infiltration | RetailGrocery |  | Pre 1978 | 1.1 | 2022 CASE report (Table 38) | 0.67076 | [16 empty] | Floor or roof area (ft2) | 50000
[5 empty] | 1978-1997 | 1.1 | 2022 CASE report (Table 38) | 0.67076 | [16 empty] | Walls area (ft2) | 22500
[5 empty] | 1998-2007 | 1.1 | 2022 CASE report (Table 38) | 0.67076 | [16 empty] | Building 4 sided area (ft2) | 22500
[5 empty] | 2008-2018 | 1 | 2022 CASE report (Table 38) & T24, part 6, 2008-2016 (Table 140.3-B), Dodge 2023 data | 0.60978 | [16 empty] | Building 6 sided area (ft2) | 122500
[5 empty] | Existing |  | Same as Pre 2008 because of their higher weights | 0.67076
[5 empty] | 2019+ | 0.6 (barrier in all CZ) | 2022 CASE report (Table 38) & T24, part 6, 2025 (Table 140.3-B) | 0.36587 | [16 empty] | 6 sided /4 sided factor | 5.4444
Source: T24 air barrier requirements (all editions) , the standardized infiltration rate reported in the 2022 CASE report, and Dodge 2023 data
Infiltration_rate_report_14May2025-Short-Version.docx
Entrance Door Infiltration
Parameter | Value | Units | Description | Source
Entrance Door Infiltration | 1105.5366 | cfm | Entrance infiltration airflow;CFM = CA × Door Area × Rp | NREL, Retail Building Guide for Entrance Energy Efficiency Measures, Section 1
CA | 175.482 | cfm/ft²/√in.H₂O | Airflow coefficient based on PPH and entrance/vestibule configuration | NREL, Retail Building Guide for Entrance Energy Efficiency Measures, Section 1, Equations 1-1 through 1-4
PPH | 76.9231 | people/hr | Annual average one-way trips through each modeled entrance during entrance operating hours | NREL, Retail Building Guide for Entrance Energy Efficiency Measures, Section 1
Transactions/week | 3500 | transactions/week | Example weekly retail transaction volume used to estimate door traffic | NREL, Retail Building Guide for Entrance Energy Efficiency Measures
Operating hours/week | 91 | hr/week | Weekly hours during which the customer entrance is available for use | 8 AM–9 PM, 7 days/week
Trips/customer | 2 | one-way trips/customer | Assumes each transaction represents one customer who enters once and exits once | Assumed
Number of main entrances | 1 | entrance | Number of equivalent customer entrances among which traffic is distributed | Based on the Geometry
Vestibule Type | Sliding doors - across | — | Entrance/vestibule configuration used to select the CA equation | Based on the Geometry
Door Area | 42 | ft² | Effective/total open area of modeled entrance door | Based on the Geometry
Wind Speed | 10 | mph | Average wind speed while the entrance is in use | Assumed based on representative California weather
Wind Impact | Moderate | — | Wind-pressure exposure assumption; Moderate corresponds to Cp = 0.45 | Assumed; Cp definition and options from NREL, Retail Building Guide for Entrance Energy Efficiency Measures, Table 1-1
Rp | 0.15 | √in.H₂O | Pressure factor based on average wind speed and wind-pressure impact | NREL, Retail Building Guide for Entrance Energy Efficiency Measures, Section 1, Step 2, Table 1-1
Loading Dock Infiltration
Parameter | Value / Formula | Units | Description | Source
Loading Dock CFM | 31108.6957 | cfm | Design infiltration rate through loading dock when open | Retail Building Guide for Entrance Energy Efficiency Measures, Section 5, Eq. 5-1
Loading Dock Door Area | 90 | ft² | Effective open area of loading dock door | Assumed
Loading Dock Door Number | 3 | # |  | Assumed
Reference Door Area | 230 | ft² | Reference effective door area used to produce Table 5-1 | Retail Building Guide for Entrance Energy Efficiency Measures, Section 5
CFM230 | 26500 | cfm | Infiltration rate for 230-ft² reference opening for climate Zone 3B | Retail Building Guide for Entrance Energy Efficiency Measures, Table 5-1
Vestibule Types:
without a vestibule | No vestibule
vestibule with swinging doors | Swinging doors
vestibule with sliding doors, where the inner and outer doors are across from each other | Sliding doors - across
vestibule with sliding doors, where the outer doors are on the left or right side of the vestibule | Sliding doors - side
Wind speed | (C_p=0.45) | (C_p=0.70) | Source
5 mph | 0.07 | 0.09 | NREL, Retail Building Guide for Entrance Energy Efficiency Measures, Section 1, Step 2, Table 1-1
10 mph | 0.15 | 0.18
15 mph | 0.22 | 0.28
20 mph | 0.29 | 0.37
Pre-1978 exterior wall U value calculation
External Wall | RetailGrocery | ExtWall_MetalFramed_NonRes | Metal framed wall: Metal frame + insulation + Gypsum board | U-factor IP | Pre 1978 | N/A | ASHRAE 90.1, 2022 Table A3.3.3.1, 3.5", R-0 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352
[7 empty] | T24, 2008 (U value): Metal framed wall Nonres | 0.098 | 0.062 | 0.082 | 0.062 | 0.062 | 0.098 | 0.098 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062
[7 empty] | DOE pre 1980 prototype LA (U value) | 0.227 | 0.227 | 0.227 | 0.227 | 0.227 | 0.227 | 0.227 | 0.227 | 0.227 | 0.227 | 0.227 | 0.227 | 0.227 | 0.227 | 0.227 | 0.227
[7 empty] | Renovation rate since 1980 (yearly renovation rate was calculated from CBECS 2003 and 2012 and then projected over 48 years) | 6.1%
Background Data [To be deleted prior to publication] | [26 empty] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication] | Background Data [To be deleted prior to publication]
External Wall | RetailGrocery | ExtWall_MetalFramed_NonRes | Metal frame + insulation + Gypsum board | U-factor IP | Pre 1978 | N/A | ASHRAE 90.1, 2022, Table A3.3.3.1, 3.5", R-0 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352
[5 empty] | 1978-1997 | 1986 | Package A with Heat Capacity 10.0-14.99 (Btu/F-ft²) - Still are lower than the next vintage! | 0.15083 | 0.15748 | 0.15748 | 0.14368 | 0.14368 | 0.21645 | 0.21645 | 0.21645 | 0.21645 | 0.21645 | 0.18622 | 0.18622 | 0.18622 | 0.15873 | 0.15873 | 0.15083

## HVAC System
HVAC system - RetailGrocery
Vintage | Heating | Cooling | Air Distribution | Other systems | Source
Existing | PSZAC (furnace) | PSZAC (DX cooling) | PSZAC | OA mixing Economizer for Vintage 3 and 4 | CEUS 2022
New Construction | SZVAVHP | SZVAVHP | PSZVAVHP | OA mixing Economizer ERV | Title 24, 2025, Engineering judgement
Efficiency of HVAC system (Efficiency is capacity-dependent. The following table provides a general estimate of system efficiency based on preliminary simulations in one climate zone, or assuming cooling load based on rule of thumb)
Vintage | Upgrade/Installed year | Heating | Cooling | Source
Pre 1978 | 2008 | Thermal Efficiency of 80% | SEER=13.0 for <65 kBtu/h EER 10.1 for 65-135 kBtu/h EER 9.5 for 135-240 kBtu/h EER 9.3 for 240-760 kBtu/h | T24, Table 112-A (2008) 10 CFR § 431.97, Table 1 (2008) California Title 20 Appliance Efficiency Regulations, Table E-4, Standards for Gas- and Oil-Fired Central Furnaces (2008)
1978-1997
1998-2007
2008-2018 | 2013 | Thermal Efficiency of 80%; | SEER 13 for <65 kBtu/h EER 11.0 for 65-135 kBtu/h EER 10.8 for 135-240 kBtu/h EER 9.8 for 240-760 kBtu/h | T24, 2013 Table 110.2-J & Table 110.2-A (2013) 10 CFR § 431.97(b) Table 1 (2013)
New Construction | 2025 | HSPF 8.0 for <65 kBtu/h COP 3.4 for 65-135 kBtu/h COP 3.3 for 135-240 kBtu/h COP 3.2 for >240 kBtu/h | SEER 14 for <65 kBtu/h EER 10.8, IEER 13.9 for 65-135 kBtu/h EER 10.4, IEER = 13.3 135-240 kBtu/h EER 9.3, IEER=12.3 for >240 kBtu/h | 10 CFR § 431.97(b) Table 1 (2025) Title 20 Appliance Efficiency Regulations, Section 1605.1, Table C-5 (2025) T24, Table 110.2-B (2025)
Fan Power
Vintage | Approach | System | Total Static Pressure (TSP) (in w.c.) | Fan Efficiency [ACM 2025] | Motor Efficiency | Fan Power Index (W/cfm) | Data Source
Existing | PNNL 90.1-2011, TSP | CAV < 7,437 cfm | 2.5 | 0.65 | ASHRAE 90.1, 2004, Table 10.8 * |  | Fan power formula: PNNL 20405, 2010, section 5.2.2.5 TSP and fan efficiency: PNNL 20405, 2010, Table 5.11, 90.1-04ac values Motor and drive efficiency: ASHRAE 90.1, 2004, Table 10.8
|  | CAV >= 7,437 cfm | 4.09
Brake horsepower (bhp) = (Supply cfm × TSP in w.c.) / (6356 × fan efficiency)
Fan power (w/cfm) = (bhp × 746) / ( supply cfm × motor efficiency )
New Construction | ACM 2025 | SZVAVHP (System 7b), ≤5,000 cfm | TSP = fan power × motor efficiency × fan efficiency × 6356 / 746 | 0.65 | 2025 ACM Table 12 ** | 0.744 | Fan power index: [ACM 2025, Table 13] Motor efficiency: [ACM 2025, Table 12]
|  | SZVAVHP (System 7b), >5,000 and ≤10,000 cfm | TSP = fan power × motor efficiency × fan efficiency × 6356 / 746 |  |  | 0.72
|  | SZVAVHP (System 7b), >10,000 cfm | TSP = fan power x motor efficiency x fan efficiency x 6356 / 746 |  |  | 0.676
* According to PNNL 20405 section 5.2.2.5, the full-load efficiency of the motor serving the fan is taken from ASHRAE 90.1, 2004, Table 10.8, based on motor nameplate and assuming enclosed motors operating at 1,800 rotations per minute (rpm) Motor nameplate size (bhp) = brake horsepower (bhp) × 1.1 ( using a 10% oversizing factor)
** The full‑load efficiency of the motor serving the fan is taken from ACM 2025 Table 12 based on the cfm of the fan. Brake horsepower (bhp) = (Supply cfm from sizing run × fan power in W/cfm) / 746. Note: HVAC New Construction is SZVAVHP, not multi-zone VAV. ACM System 7b ≤5,000 cfm. Note: ACM System 7b mid bin. Existing PSZAC CAV rows above stay on PNNL.
〖𝐹𝑎𝑛 𝑝𝑜𝑤𝑒𝑟〗_(𝑤/𝑐𝑓𝑚)=(〖𝑇𝑆𝑃〗_(𝑖𝑛 𝑤.𝑐)∗746)/(6356∗𝜇_𝑓𝑎𝑛∗𝜇_𝑚𝑜𝑡𝑜𝑟 )
𝑏ℎ𝑝=(𝑐𝑓𝑚∗〖𝑇𝑆𝑃〗_(𝑖𝑛 𝑤.𝑐.))/〖6356∗𝜇〗_𝑓𝑎𝑛
〖𝐹𝑎𝑛 𝑝𝑜𝑤𝑒𝑟〗_(𝑤/𝑐𝑓𝑚)=(𝑏ℎ𝑝∗746)/(𝑐𝑓𝑚∗𝜇_𝑚𝑜𝑡𝑜𝑟 )
𝑏ℎ𝑝=(〖𝐹𝑎𝑛 𝑝𝑜𝑤𝑒𝑟〗_(𝑤/𝑐𝑓𝑚)∗𝑐𝑓𝑚∗𝜇_𝑚𝑜𝑡𝑜𝑟)/746

## Ventilation
Outdoor Airflow Rate - RetailGrocery
Space/Thermal Zone | Number of People | Floor Area (ft²) | cfm/person [T24, 2025, Equation 120.1-F and Table 120.1-A] | cfm/ft² [T24, 2025, Equation 120.1-F and Table 120.1-A] | Required Exhaust Rate [T24, 2025, Table 120.1-B – minimum exhaust rates] | Total cfm Driven by People | Total cfm Driven by Area | Total cfm Driven by Exhaust | Total cfm | Notes
Checkout Area | 170 | 10000 | 15 | 0.2 | _ | 2550 | 2000 | _ | 2550
Produce | 74.8 | 4400 | 15 | 0.2 | _ | 1122 | 880 | _ | 1122
General Merch | 130.9 | 7700 | 15 | 0.2 | _ | 1963.5 | 1540 | _ | 1963.5
Frozen | 112.2 | 6600 | 15 | 0.2 | _ | 1683 | 1320 | _ | 1683
Beverage | 74.8 | 4400 | 15 | 0.2 | _ | 1122 | 880 | _ | 1122
Bakery and Deli | 74.8 | 4400 | 15 | 0.2 | _ | 1122 | 880 | _ | 1122
Meat and Dairy | 85 | 5000 | 15 | 0.2 | _ | 1275 | 1000 | _ | 1275
Back_Office | 6 | 1200 | 15 | 0.15 | 8*50/70 cfm/unit | 90 | 180 | 400 | 400
Loading Dock EL1 | 6.4 | 3200 | 15 | 0.15 |  | 96 | 480 | _ | 480
Food Prep | 0 | 2100 |  |  | 0.7 | 0 | 0 | 1470 | 1470
RefWalkInCool Core | 0 | 500 |  |  |  | 0 | 0 |  | 0
Ref WalkInFreezer Core | 0 | 500 |  | 0 | _ | 0 | 0 | _ | 0

## Thermostat
Thermostat Setpoints - RetailGrocery
Setpoint | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16 | Source
Grocery Sales & Office Heating Setpoint (F) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | T24 2022 - Appendix 5.4B, [Retail]
Grocery Sales & Office Heating Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Grocery Sales & Office Cooling Setpoint (F) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
Grocery Sales & Office Cooling Setback (F) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
Ancillary Heating Setpoint (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | Engineering Judgment
Ancillary Heating Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Ancillary Cooling Setpoint (F) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
Ancillary Cooling Setback (F) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85

## Water Heater
Water Heater Summary - RetailGrocery
Vintage | WH Type | Efficiency | Number of WH | Tank Volume (gal) | Tank Loss | Source
Existing | Electric | 1 | 1 | See table below for CZ-specific values: Climate Zone Water Heater Sizing and Loss Coefficients, Storage Volume column (col F) | See table below: Climate Zone Water Heater Sizing and Loss Coefficients, Standby Loss column (col G) | See table below for sources: Climate Zone Water Heater Sizing and Loss Coefficients
New Construction | Electric | 1 | 1 | See table below for CZ-specific values: Climate Zone Water Heater Sizing and Loss Coefficients, Storage Volume column (col F) | See table below: Climate Zone Water Heater Sizing and Loss Coefficients, Standby Loss column (col G) | See table below for sources: Climate Zone Water Heater Sizing and Loss Coefficients
Peak Hot Water Consumption
Space Name | Baseline WH Type [CEUS 2022] | Total Area (ft²) | Number of People | Hot Water Usage Specification (gal/hr per person) [T24, 2022, Appendix 5.4A , sheet: "2022 SpaceFuncData-Input"] | Peak Hot Water Usage (gal/hr) | Peak Hot Water Usage (gal/min) | Note
Checkout Area | Electric resistance WH | 10000 | 170 | 0.18 | 30.6 | 0.51 | For space types marked with an asterisk (the ‘*’ symbol), the water‑heater type is listed as electric in Appendix 5.4A, sheet ‘2022 SpaceFuncData‑Input.’ However, we modified the value based on CEUS data, which indicates that gas is the primary fuel type.
Produce | Electric resistance WH | 4400 | 74.8 | 0.18 | 13.464 | 0.2244
General Merch | Electric resistance WH | 7700 | 130.9 | 0.18 | 23.562 | 0.3927
Frozen | Electric resistance WH | 6600 | 112.2 | 0.18 | 20.196 | 0.3366
Beverage | Electric resistance WH | 4400 | 74.8 | 0.18 | 13.464 | 0.2244
Bakery and Deli | Electric resistance WH | 4400 | 74.8 | 0.18 | 13.464 | 0.2244
Meat and Dairy | Electric resistance WH | 5000 | 85 | 0.18 | 15.3 | 0.255
Back_Office | Electric resistance WH | 1200 | 6 | 0.09 | 0.54 | 0.009
Loading Dock EL1 | Electric resistance WH | 3200 | 6.4 | 0.18 | 1.152 | 0.0192
Food Prep | Electric resistance WH | 2100 | 0 | 0.18 | 0 | 0
RefWalkInCool Core | Electric resistance WH | 500 | 0 | 0.18 | 0 | 0
Ref WalkInFreezer Core | Electric resistance WH | 500 | 0 | 0.18 | 0 | 0
Total | Gas storage |  |  |  | 0 |  | Minimum peak hot water usage is 75 gal according to ACM 2025
Total | Electric resistance |  |  |  | 131.742
Design supply temperature (°F) | 135 | CEC-400-2022-009-CMF-REV2-AP5.4B
WH system factor | 0.6 | 2025 ACM §5.9.2 Rated Capacity
Water mass conversion (lb/gal) | 8.2877 | 2025 ACM §5.9.2 Rated Capacity
Reheat multiplier | 0.4 | 2025 ACM §5.9.2 Storage Volume
Climate Zone Water Heater Sizing and Loss Coefficients (Individual WH)
Climate Zone | Minimum Monthly Mains Temp (°F) [T24 2022 - Appendix 5.4B] | Heat Output (Btu/hr) [ACM, 2025, 5.9.2: Rated capacity section] | WH Capacity (Btu/hr) [ACM, 2025, 5.9.2: Rated capacity section] | Required Energy Input (Btu/hr) | Storage Volume (gal) | Standby Loss [Title 20, §1605.1 Table F-4; Appendix B: Water Heating Calculation Method] |  | Off/On Cycle Loss Coefficient to Ambient Temp |  | Source/Note
CZ01 | 47.9 | 95099.1049 | 57059.4629 | 61419 | 65 | 0.71538 | %/hr | 3.8781 | Btu/h·°F | Required Energy Input: vendor/available catalog size (Market data table). Storage Volume: standard/available catalog tank size (Market data table).
CZ02 | 50.8 | 91932.7742 | 55159.6645 | 61419 | 65 | 0.71538 | %/hr | 3.8781 | Btu/h·°F
CZ03 | 52.2 | 90404.2008 | 54242.5205 | 61419 | 65 | 0.71538 | %/hr | 3.8781 | Btu/h·°F
CZ04 | 52.7 | 89858.2817 | 53914.969 | 61419 | 65 | 0.71538 | %/hr | 3.8781 | Btu/h·°F
CZ05 | 51.6 | 91059.3037 | 54635.5822 | 61419 | 65 | 0.71538 | %/hr | 3.8781 | Btu/h·°F
CZ06 | 56.8 | 85381.7452 | 51229.0471 | 61419 | 65 | 0.71538 | %/hr | 3.8781 | Btu/h·°F
CZ07 | 58.4 | 83634.8041 | 50180.8824 | 61419 | 65 | 0.71538 | %/hr | 3.8781 | Btu/h·°F
CZ08 | 58.4 | 83634.8041 | 50180.8824 | 61419 | 65 | 0.71538 | %/hr | 3.8781 | Btu/h·°F
CZ09 | 57.6 | 84508.2746 | 50704.9648 | 61419 | 65 | 0.71538 | %/hr | 3.8781 | Btu/h·°F
CZ10 | 57.1 | 85054.1937 | 51032.5162 | 61419 | 65 | 0.71538 | %/hr | 3.8781 | Btu/h·°F
CZ11 | 50.5 | 92260.3257 | 55356.1954 | 61419 | 65 | 0.71538 | %/hr | 3.8781 | Btu/h·°F
CZ12 | 51.4 | 91277.6713 | 54766.6028 | 61419 | 65 | 0.71538 | %/hr | 3.8781 | Btu/h·°F
CZ13 | 51.7 | 90950.1198 | 54570.0719 | 61419 | 65 | 0.71538 | %/hr | 3.8781 | Btu/h·°F
CZ14 | 50.1 | 92697.0609 | 55618.2366 | 61419 | 65 | 0.71538 | %/hr | 3.8781 | Btu/h·°F
CZ15 | 63.2 | 78393.9809 | 47036.3885 | 61419 | 65 | 0.71538 | %/hr | 3.8781 | Btu/h·°F
CZ16 | 41.4 | 102196.053 | 61317.6318 | 61419 | 65 | 0.71538 | %/hr | 3.8781 | Btu/h·°F
Market data
Catalog gas input (Btu/h) | Input source | Elec resistance tank (kW) | Elec resistance (Btu/h) | Catalog gas tank (gal) | Tank source | Elec tank (gal) | Elec tank source | Sources and links → Note tab
60000 | Grainger | 1.5 | 5118 | 34 | ENERGY STAR | 6 | Grainger
75100 | Grainger | 2 | 6824 | 35 | Grainger | 10 | Grainger
76000 | Both | 3 | 10236 | 48 | Grainger | 15 | Grainger
80000 | Grainger | 4.5 | 15355 | 50 | Both | 20 | Grainger
99900 | ENERGY STAR | 6 | 20473 | 55 | ENERGY STAR | 28 | Grainger
100000 | Both | 8 | 27297 | 60 | ENERGY STAR | 30 | Grainger
120000 | ENERGY STAR | 9 | 30709 | 65 | Both | 36 | Grainger
125000 | Both | 10 | 34121 | 72 | Grainger | 40 | Grainger
130000 | Both | 12 | 40946 | 75 | Both | 47
145000 | ENERGY STAR | 12.1 | 41287 | 76 | Grainger | 50
150000 | ENERGY STAR | 18 | 61419 | 80 | Both | 65
156000 | Grainger | 24 | 81891 | 82 | Grainger | 80
160000 | Both | 27 | 92128 | 85 | Grainger | 85
175000 | ENERGY STAR | 36 | 122837 | 90 | Both | 105
180000 | Grainger | 54 | 184256 | 91 | Grainger | 120
199000 | ENERGY STAR |  |  | 100 | Both
199900 | Both |  |  | 110 | ENERGY STAR
200000 | ENERGY STAR |  |  | 119 | Both
250000 | Both |  |  | 125 | ENERGY STAR
251000 | ENERGY STAR
270000 | Grainger
285000 | ENERGY STAR
300000 | Both
320000 | ENERGY STAR
360000 | Grainger
398000 | ENERGY STAR
399000 | ENERGY STAR
399900 | Both
499900 | Grainger
550000 | Grainger
715000 | Grainger

## Interior Lights
Interior Lighting - RetailGrocery
Space Type | New Construction |  |  | Existing |  |  | Note
| LPD (W/ft²) | Additional LPD for Portable Lighting (W/ft²) | Source | LPD (W/ft²) | Additional LPD for Portable Lighting (W/ft²) | Source
Retail Sales Area (Grocery Sales) | 1 | 0.189 | T24, part 6, 2025, Table 140.6-C (Area category method) | 1.2 | 0.081 | T24, part 6, 2016, Table 140.6-C (Area category method) | Additional lighting was allocated for the Bakery & Deli and Produce areas, which together represent about 27% of the store’s retail sales area; accordingly, the code allowance for extra lighting was multiplied by 27%.
Lounge, Breakroom, or Waiting Area | 0.55 |  |  | 0.9
Storage, Commercial/Industrial (Shipping & Handling) | 0.6 |  |  | 0.6
Storage, Commercial/Industrial (Refrigerated) | 0.4 |  |  | 0.7

## Ext Lighting
Exterior Lighting - RetailGrocery
Motion Controlled Luminaires (W) | Non-motion Controlled Luminaires (W) | Total (W) | Source
1405.5556 | 1160 | 2565.5556 | T24, 2022
Exterior Lighting
Items (Assume LZ2) | Assumptions [2019 Outdoor Lighting CASE Report & PNNL 90.1-2010 TSD] |  | Unit | Lighting Power Allowance [T24, 2025, Table 140.7-A & 140.7-B] | Unit | Exterior lighting power (w)
IWA (Initial Wattage Allowance) |  |  |  | 200 | W | 200
Parking area | 400 ft² for every parking space 1 parking space per 360 ft² of gross building area | 55555.5556 | (ft²) | 0.019 | (W/ft²) | 1055.5556
Building Entrance | 1 per 5,000 sf footprint | 10 | (count) | 15 | (W/ea) | 150
Hardscape Ornamental Light | 0.1 ft² per 1 ft² of gross bldg area [2019 Lighting CASE report,Table 36] *The 0.5 multiplier has not been applied, as it is assumed it will be incorporated later during the measure analysis study. | 5000 | (ft²) | 0.007 | (W/ft²) | 35
Building façade | 0.1 W per 1 ft² of facade area Façade Area = Perimeter × 0.5 × 25 ft The 0.5 factor assumes that only half of the perimeter walls are lit. -Formula is developed based on the 2019 Outdoor Lighting CASE report | 11250 | (ft²) | 0.1 | (W/ft²) | 1125
Sales canopy | 0.1 ft² per ft² of gross bldg area | 0 | (ft²) | 0.47 | (W/ft²) | 0
Motion controlled Luminaires | [5 empty] | 1405.5556
Non-motion-controlled Luminaires | [5 empty] | 1160
Total | [5 empty] | 2565.5556
*Developed based on 2019 Outdoor Lighting CASE Report
Perimeter | 900
Total floor area | 50000
Floors | 1

## Equipment
Equipment - RetailGrocery
Space Type | Plug Load Power Density (W/ft²) | Gas Power Density (Btu/hr-ft²) | Refrigeration Power Density (W/ft²) | Source | Note
Retail Sales Area (Grocery Sales) | 0.4 |  |  | Proposed Updates to Equipment Power Densities and Schedules in the 2028 Energy Code Nonresidential and Multifamily Alternative Calculation Method (NRMFACM) Reference Manual, August 7, 2025 | Matches Retail/All Other; PNNL prototype =~0.7; T24 Appendix 5.4A =0.2
Lounge, Breakroom, or Waiting Area | 1 |  |  | T24 2022 - Appendix 5.4A: Space Use Data-T24N-2022
Storage, Commercial/Industrial (Shipping & Handling) | 0.5
Storage, Commercial/Industrial (Refrigerated) | 0.2
Refrigeration Equipment
Tag | Equipment Type | Location | Duty / Type | Number of Units | Case Length (ft) | Dimensions (LxDxH) | Temp Range (°F) | Refrigerant | Vintage | Rated Power (W/m) | Defrost Power (W/m) | Fan Power (W/m) | Lights Power (W/m) | Anti Sweat (W) | Compressor Type | Lighting | Defrost Type | Notes | Source
R1 | Open Multideck Dairy Case | Dairy Aisle | Medium Temp | 12 | 12 | 12' x 42" x 84" | 34–38 | R-448A | New Construction | 1143 | 0 | 16 | 16 | 0 | Remote | LED canopy/shelves | Off-cycle | Glass end panels, night curtain | Grocery Store 50% Energy Savings Technical Support Document NREL (2009) ORNL Prototype Supermarket Building Energy Model (2019) Performance Comparison of Three High Efficiency Medium-Temperature Display Cases (2009)
[8 empty] | R22 | Vintage | 1438 | 0 | 43 | 73 | 0
R2 | Service Deli Case | Deli Counter | Medium Temp | 2 | 8 | 8' x 36" x 50" | 36–40 | R-448A | New Construction | 599 | 0 | 20 | 18 | 64 | Remote | LED top light | Off-cycle | Dual temp option for meats/cheeses
[8 empty] | R22 | Vintage | 808 | 0 | 32 | 72 | 0
R3 | Meat Self-Service Case | Meat Department | Medium Temp | 14 | 12 | 12' x 42" x 84" | 28–32 | R-448A | New Construction | 1143 | 0 | 16 | 16 | 0 | Remote | LED lighting | Off-cycle | Gravity coil, low temp
[8 empty] | R22 | Vintage | 1438 | 0 | 43 | 73 | 0
R4 | Produce Case (Refrigerated) | Produce Aisle | Medium Temp | 10 | 8 | 8' x 42" x 84" | 36–40 | R-448A | New Construction | 1143 | 0 | 16 | 16 | 0 | Remote | LED canopy light | Off-cycle | Mist system optional
[8 empty] | R22 | Vintage | 1438 | 0 | 43 | 73 | 0
R5 | Frozen Food Upright Case | Frozen Foods Aisle | Low Temp | 20 | 12 | 12' x 36" x 84" | -5 to 0 | R-448A | New Construction | 426 | 971 | 30 | 26 | 139 | Remote | LED door lighting | Electric | Glass doors, anti-sweat heaters
[8 empty] | R22 | Vintage | 584 | 1222 | 70 | 99 | 78
R6 | Ice Cream Low-Temp Case | Frozen Foods Aisle | Low Temp | 6 | 6 | 6' x 36" x 84" | -10 to -20 | R-448A or CO₂ | New Construction | 521 | 971 | 30 | 26 | 139 | Remote | LED lighting | Electric | Critical temp holding, tight door seals
[8 empty] | R22 | Vintage | 618 | 1222 | 70 | 99 | 78
R7 | Walk-In Cooler (Produce) | Back of House | Medium Temp | 1 | N/A | 10' x 12' x 8' | 34–38 | R-448A | New Construction | 2917 (W) | 0 | 152 (W) | 60 (W) | 0 | Remote condensing unit | LED ceiling | Off-cycle | Floorless, strip curtain at door
[8 empty] | R22 | Vintage | 2917 (W) | 0 | 169 (W) | 120 (W) | 0
R8 | Walk-In Freezer | Back of House | Low Temp | 1 | N/A | 10' x 10' x 8' | -10 to -20 | R-448A | New Construction | 2454 (W) | 1939 (W) | 128 (W) | 50 (W) | 0 | Remote condensing unit | LED ceiling | Electric | Insulated floor, heated door frame
[8 empty] | R22 | Vintage | 2454 (W) | 1939 (W) | 196 (W) | 100 (W) | 0
R9 | Beverage Case | Front of Store | Medium Temp | 4 | 8 | 8' x 36" x 84" | 34–38 | R-448A | New Construction | 1143 | 0 | 16 | 16 | 64 | Remote | LED shelves | Off-cycle | Reach-in with glass doors
[8 empty] | R22 | Vintage | 1438 | 0 | 43 | 73 | 0
R10 | Grab-n-Go Sandwich Cooler | Front Grab-n-Go Area | Medium Temp | 2 | 6 | 6' x 30" x 60" | 36–40 | R-448A | New Construction | 599 | 0 | 20 | 18 | 64 | Self-contained | LED canopy | Off-cycle | Plug-in, casters for mobility
[8 empty] | R22 | Vintage | 808 | 0 | 32 | 72 | 0
Total |  |  |  | 72 | 728
Refrigeration Systems
Vintage | Name | Service | # of compressors | # of condensors | Connected Load (KW) | Heat Rejection | Min SCT (°F) | Condensor Design Capacity (kW) | Condensor Fan Power (W) | Fan Control | Source
New Construction | LT_Refrigeration System | Low Temp (R5, R6, R8) | 4 | 1 | 39.3 | Outdoors | 70 | 83.5 | 4378 | Two Speed | ORNL Prototype Supermarket Building Energy (2019)
| MT_Refrigeration System | Medium Temp (R1–R4, R9, R7) | 5 | 1 | 153.6 | Outdoors | 70 | 276.4 | 12884 | Two Speed
| R10_SelfContained System | Medium Temp _ Self Contained | 1 | 1 | 2.19 | Checkout_Area | 70 | 3.94 | 869 | Fixed
Vintage | LT_Refrigeration System | Low Temp (R5, R6, R8) | 4 | 1 | 52 | Outdoors | 70 | 110.3 | 5560 | Two Speed | ORNL Prototype Supermarket Building Energy (2019)
| MT_Refrigeration System | Medium Temp (R1–R4, R9, R7) | 5 | 1 | 192.7 | Outdoors | 70 | 346.9 | 15991 | Two Speed
| R10_SelfContained System | Medium Temp _ Self Contained | 1 | 1 | 2.96 | Checkout_Area | 70 | 5.32 | 930 | Fixed

## Schedules
Schedules - RetailGrocery
Zone | Schedule Category | Schedule | Source | Type | Hour
[5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Grocery Sales, Office | Grocery | Occupancy | NLR Study "Final Optimization Report: Empowering Energy Efficiency in Existing Big-Box Retail/Grocery Stores", (2020) & Adjusted based on Google Popular Time | Weekday | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.15 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.7 | 0.8 | 0.8 | 0.8 | 0.6 | 0.3 | 0.1 | 0.05
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.2 | 0.3 | 0.5 | 0.7 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.7 | 0.6 | 0.5 | 0.3 | 0.1
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.2 | 0.3 | 0.5 | 0.7 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.7 | 0.6 | 0.5 | 0.3 | 0.1
Grocery Sales, Office | Grocery | Lights | T24 2022 - Appendix 5.4B | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Grocery Sales, Office | Grocery | ElecEquipment | Plug load and schedules project with CEC, 2025 | Weekday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Saturday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Sunday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
Grocery Sales, Office | Grocery | HVACAvail | T24 2022 - Appendix 5.4B, [Retail] | Weekday | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Grocery Sales, Office | Grocery | ServiceHotWater | T24 2022 - Appendix 5.4B, [Retail] | Weekday | 0.04 | 0.05 | 0.05 | 0.04 | 0.04 | 0.04 | 0.04 | 0.15 | 0.23 | 0.32 | 0.41 | 0.57 | 0.62 | 0.61 | 0.5 | 0.45 | 0.46 | 0.47 | 0.42 | 0.34 | 0.33 | 0.23 | 0.13 | 0.08
|  |  |  | Saturday | 0.11 | 0.1 | 0.08 | 0.06 | 0.06 | 0.06 | 0.07 | 0.2 | 0.24 | 0.27 | 0.42 | 0.54 | 0.59 | 0.6 | 0.49 | 0.48 | 0.47 | 0.46 | 0.44 | 0.36 | 0.29 | 0.22 | 0.16 | 0.13
|  |  |  | Sunday | 0.07 | 0.07 | 0.07 | 0.06 | 0.06 | 0.06 | 0.07 | 0.1 | 0.12 | 0.14 | 0.29 | 0.31 | 0.36 | 0.36 | 0.34 | 0.35 | 0.37 | 0.34 | 0.25 | 0.27 | 0.21 | 0.16 | 0.1 | 0.06
Grocery Sales, Office | Grocery | Infiltration | T24 2022 - Appendix 5.4B, [Retail] | Weekday | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  |  | Saturday | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  |  | Sunday | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Grocery Sales, Office | Grocery | HtgSetpt | T24 2022 - Appendix 5.4B, [Retail] | Weekday | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
|  |  |  | Saturday | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
|  |  |  | Sunday | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
Grocery Sales, Office | Grocery | ClgSetpt | T24 2022 - Appendix 5.4B, [Retail] | Weekday | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
|  |  |  | Saturday | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
|  |  |  | Sunday | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
Refrigeration Case Schedules
Retail Sales Area (Grocery Sales) | Refrigeration | CaseOperatingSched | EnergyPlus example files _ Detailed_Supermarket | Weekday | bar: Hour 1 to Hour 24
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
Retail Sales Area (Grocery Sales) | Refrigeration | CaseCleanedOnMonday | EnergyPlus example files _ Detailed_Supermarket | Monday | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | Operating Schedule for Meat and Ice Cream Cases
Tue-Fri | bar: Hour 1 to Hour 24
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
Retail Sales Area (Grocery Sales) | Refrigeration | LightingSched_AllCases | EnergyPlus example files _ Detailed_Supermarket | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Retail Sales Area (Grocery Sales) | Refrigeration | LightingSched_WalkIn | EnergyPlus example files _ Detailed_Supermarket | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
Retail Sales Area (Grocery Sales) | Refrigeration | RestockSched_AllCases | EnergyPlus example files _ Detailed_Supermarket | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Retail Sales Area (Grocery Sales) | Refrigeration | RestockSched_WalkIIn | EnergyPlus example files _ Detailed_Supermarket | Mon/Wed/Thu | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0
|  |  |  | Tue/Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Retail Sales Area (Grocery Sales) | Refrigeration | Defrost_MTCases | EnergyPlus example files _ Detailed_Supermarket | Weekday | 0 | 0 | 0 | 0 | 0.333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 min defrost / 30 min drip
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0.333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.333 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0.333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.333 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Retail Sales Area (Grocery Sales) | Refrigeration | DripDown_MTCases | `EnergyPlus example files _ Detailed_Supermarket | Weekday | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Retail Sales Area (Grocery Sales) | Refrigeration | Defrost_LTCases | EnergyPlus example files _ Detailed_Supermarket | Weekday | 0 | 0 | 0 | 0.333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0.333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0.333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Retail Sales Area (Grocery Sales) | Refrigeration | DripDown_LTCases | `EnergyPlus example files _ Detailed_Supermarket | Weekday | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Retail Sales Area (Grocery Sales) | Refrigeration | CaseCredit_LT | EnergyPlus example files _ Detailed_Supermarket | Weekday | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.2 | 0.2 | 0.2 | Credit Schedule for Ice Cream and Frozen Food cases
|  |  |  | Saturday | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.2 | 0.2 | 0.2
|  |  |  | Sunday | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.2 | 0.2 | 0.2
Retail Sales Area (Grocery Sales) | Refrigeration | CaseCredit_MT | EnergyPlus example files _ Detailed_Supermarket | Weekday | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.2 | 0.2 | 0.2
|  |  |  | Saturday | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.2 | 0.2 | 0.2
|  |  |  | Sunday | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.2 | 0.2 | 0.2
Retail Sales Area (Grocery Sales) | Refrigeration | WalkInDoorOpenSched | EnergyPlus example files _ Detailed_Supermarket | Weekday | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.02 | 0.02 | 0.02
|  |  |  | Saturday | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.02 | 0.02 | 0.02
|  |  |  | Sunday | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.02 | 0.02 | 0.02
Retail Sales Area (Grocery Sales) | Refrigeration | Lights | T24 2022 - Appendix 5.4B | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Retail Sales Area (Grocery Sales) | Refrigeration | ElecEquipment | Plug load and schedules project with CEC, 2025 | Weekday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Saturday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Sunday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
Retail Sales Area (Grocery Sales) | Refrigeration | Infiltration | T24 2022 - Appendix 5.4B, [Retail] | Weekday | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  |  | Saturday | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  |  | Sunday | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Ancillary
Loading Dock | Ancillary | Occupancy | T24 2022 - Appendix 5.4B | Weekday | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.15 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.7 | 0.8 | 0.8 | 0.8 | 0.6 | 0.3 | 0.1 | 0.05
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.2 | 0.3 | 0.5 | 0.7 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.7 | 0.6 | 0.5 | 0.3 | 0.1
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.2 | 0.3 | 0.5 | 0.7 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.7 | 0.6 | 0.5 | 0.3 | 0.1
Loading Dock | Ancillary | Lights | T24 2022 - Appendix 5.4B | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Loading Dock | Ancillary | ElecEquipment | Plug load and schedules project with CEC, 2025 | Weekday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Saturday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Sunday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
Loading Dock | Ancillary | HVACAvail | T24 2022 - Appendix 5.4B | Weekday | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Loading Dock | Ancillary | ServiceHotWater | T24 2022 - Appendix 5.4B | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Loading Dock | Ancillary | Infiltration | T24 2022 - Appendix 5.4B | Weekday | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  |  | Saturday | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  |  | Sunday | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Loading Dock | Ancillary | HtgSetpt | Engineering Judgement | Weekday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  |  | Saturday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  |  | Sunday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Loading Dock | Ancillary | ClgSetpt | Engineering Judgement | Weekday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
|  |  |  | Saturday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
|  |  |  | Sunday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
Loading Dock EL1 | Ancillary | LoadingDockDoorInfiltration | CASE Report - Dock Seals (2017) Truck Trip Generation by Grocery Stores (2010) | Weekday | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Other
| Building | ExtLightingNonMotionCtrl |  | Weekday | bar: Hour 1 to Hour 24
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
| Building | ExtLightingMotionCtrl |  | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Retails | Building | RetailSalePeopleActivityLevel | Based on Activity level schedules in CEC Prototypes | Weekday | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
|  |  |  | Saturday | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
|  |  |  | Sunday | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
Back Office | Building | CommonAreaPeopleActivityLevel | Based on Activity level schedules in CEC Prototypes | Weekday | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5
|  |  |  | Saturday | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5
|  |  |  | Sunday | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5
RefFoodPRep Core, RefWalkInCool Core, Ref WalkInFreezer Core | Building | RefStoragePeopleActivityLevel | Based on Activity level schedules in CEC Prototypes | Weekday | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8
|  |  |  | Saturday | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8
|  |  |  | Sunday | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8
Loading Dock EL1 | Building | SaleStoragePeopleActivityLevel | Based on Activity level schedules in CEC Prototypes | Weekday | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8
|  |  |  | Saturday | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8
|  |  |  | Sunday | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8
Background Data [To be deleted prior to publication]
Availability | Lighting | Restocking | Case credit fraction | Defrost | Hour 1: Drip-down; Hour 2: Walk-in door; Hour 3: Walk-in heating
CaseOperatingSched | LightingSched_AllCases | RestockSched_AllCases | CaseCredit_MT | Defrost_MTCases | Hour 1: DripDown_MTCases; Hour 2: —; Hour 3: —
CaseOperatingSched | LightingSched_AllCases | RestockSched_AllCases | CaseCredit_MT | Defrost_MTCases | Hour 1: DripDown_MTCases; Hour 2: —; Hour 3: —
CaseCleanedOnMonday | LightingSched_AllCases | RestockSched_AllCases | CaseCredit_MT | Defrost_MTCases | Hour 1: DripDown_MTCases; Hour 2: —; Hour 3: —
CaseOperatingSched | LightingSched_AllCases | RestockSched_AllCases | CaseCredit_MT | Defrost_MTCases | Hour 1: DripDown_MTCases; Hour 2: —; Hour 3: —
CaseOperatingSched | LightingSched_AllCases | RestockSched_AllCases | CaseCredit_LT | Defrost_LTCases | Hour 1: DripDown_LTCases; Hour 2: —; Hour 3: —
CaseCleanedOnMonday | LightingSched_AllCases | RestockSched_AllCases | CaseCredit_LT | Defrost_LTCases | Hour 1: DripDown_LTCases; Hour 2: —; Hour 3: —
CaseOperatingSched | LightingSched_Walkin | RestockSched_Walkin | — (WalkIn has no credit fraction field) | Defrost_MTCases | Hour 1: DripDown_MTCases; Hour 2: WalkInDoorOpenSched; Hour 3: CaseOperatingSched
CaseOperatingSched | LightingSched_Walkin | RestockSched_Walkin | — (WalkIn has no credit fraction field) | Defrost_LTCases | Hour 1: DripDown_LTCases; Hour 2: WalkInDoorOpenSched; Hour 3: CaseOperatingSched
CaseOperatingSched | LightingSched_AllCases | RestockSched_AllCases | CaseCredit_MT | Defrost_MTCases | Hour 1: DripDown_MTCases; Hour 2: —; Hour 3: —
CaseOperatingSched | LightingSched_AllCases | RestockSched_AllCases | CaseCredit_MT | Defrost_MTCases | Hour 1: DripDown_MTCases; Hour 2: —; Hour 3: —

## Energy Usage
CalBEM Energy Consumption - RetailGrocery | [7 empty] | National Average (EnergyStar Portfolio Manager) |  |  |  |  | CEUS Energy Consumption - Retail
Prototype | CZ | CalBEM Electricity EUI (KBTU/ft²) | CalBEM Gas EUI (KBTU/ft²) | CalBEM Total EUI (KBTU/ft²) | New Construction Electricity EUI (KBTU/ft²) | New Construction Gas EUI (KBTU/ft²) | New Construction Total EUI (KBTU/ft²) | National Average | Acceptable eRange (25% Higher) | Acceptable Range (25% Lower) | National Average Acceptable Range | Zip code | Prototype | CZ | Total Floorspace (Thousand of ft²) | CEUS 2022 Electric Energy Intensity (kWh/ft²) | CEUS 2022 Annual Gas Intensity (kWh/ft²) | CEUS 2022 Total EUI (kBtu/ft²) | Acceptable Range (25% Higher) | Acceptable Range (25% Lower) | CEUS 2022 Acceptable Range
HotelSmall | 1 | [6 empty] | 58.5 | 73.125 | 43.875 | 29.25 | 95519 | Retail | 1 | 13814 | 11.1 | 3.06 | 48.3139 | 60.3924 | 36.2354 | 24.157
| 2 | [6 empty] | 68.9 | 86.125 | 51.675 | 34.45 | 95403 |  | 2 | 25239 | 7.8 | 4.35 | 41.4558 | 51.8197 | 31.0918 | 20.7279
| 3 | [6 empty] | 63.5 | 79.375 | 47.625 | 31.75 | 94621 |  | 3 | 88648 | 10.2 | 3.48 | 46.6762 | 58.3452 | 35.0071 | 23.3381
| 4 | [6 empty] | 71.2 | 89 | 53.4 | 35.6 | 93446 |  | 4 | 44551 | 10.4 | 3.38 | 47.0174 | 58.7717 | 35.263 | 23.5087
| 5 | [6 empty] | 61.8 | 77.25 | 46.35 | 30.9 | 93455 |  | 5 | 9847 | 9.3 | 4.28 | 46.335 | 57.9187 | 34.7512 | 23.1675
| 6 | [6 empty] | 68.4 | 85.5 | 51.3 | 34.2 | 90045 |  | 6 | 92562 | 8.6 | 1.35 | 33.9494 | 42.4367 | 25.462 | 16.9747
| 7 | [6 empty] | 68.4 | 85.5 | 51.3 | 34.2 | 92101 |  | 7 | 63471 | 10.3 | 0.93 | 38.3168 | 47.8959 | 28.7376 | 19.1584
| 8 | [6 empty] | 69.4 | 86.75 | 52.05 | 34.7 | 92832 |  | 8 | 147354 | 8.5 | 1.31 | 33.4717 | 41.8396 | 25.1038 | 16.7359
| 9 | [6 empty] | 70.1 | 87.625 | 52.575 | 35.05 | 91505 |  | 9 | 212697 | 9.4 | 1.4 | 36.8496 | 46.062 | 27.6372 | 18.4248
| 10 | [6 empty] | 70.6 | 88.25 | 52.95 | 35.3 | 92501 |  | 10 | 149832 | 9.3 | 1.54 | 36.9861 | 46.2326 | 27.7396 | 18.493
| 11 | [6 empty] | 72.5 | 90.625 | 54.375 | 36.25 | 96080 |  | 11 | 45934 | 10.6 | 2.72 | 45.4478 | 56.8098 | 34.0859 | 22.7239
| 12 | [6 empty] | 71.6 | 89.5 | 53.7 | 35.8 | 95822 |  | 12 | 195816 | 11 | 2.87 | 47.3244 | 59.1556 | 35.4933 | 23.6622
| 13 | [6 empty] | 72.5 | 90.625 | 54.375 | 36.25 | 93727 |  | 13 | 67122 | 12.4 | 2.61 | 51.2141 | 64.0177 | 38.4106 | 25.6071
| 14 | [6 empty] | 72.8 | 91 | 54.6 | 36.4 | 93550 |  | 14 | 39049 | 8.6 | 1.28 | 33.7106 | 42.1382 | 25.2829 | 16.8553
| 15 | [6 empty] | 70.5 | 88.125 | 52.875 | 35.25 | 92262 |  | 15 | 73160 | 10 | 2.42 | 42.377 | 52.9713 | 31.7828 | 21.1885
| 16 | [6 empty] | 71.5 | 89.375 | 53.625 | 35.75 | 95726 |  | 16 | 149464 | 9.6 | 1.56 | 38.0779 | 47.5974 | 28.5584 | 19.039
Ref: CEUS 2022 Report
And converted FZ level data to CZ level
CEUS has only one category for all the retails
Background Data [To be deleted prior to publication]
Using Supermarket/Grocery Store use type
[7 empty] | Alternative One | 130 | Alternative Two | 68.7
[8 empty] | 139 |  | 80.3
[8 empty] | 135 |  | 74.2
[8 empty] | 141.5 |  | 82.8
[8 empty] | 133.6 |  | 72.3
[8 empty] | 139.1 |  | 79.7 |  |  |  |  | CEUS 2022 Electric Energy Intensity (kWh/ft²) | CEUS 2022 Annual Gas Intensity (kWh/ft²)
[8 empty] | 139.1 |  | 79.7 |  |  |  |  | Food Store
[8 empty] | 139.9 |  | 80.8 |  |  |  |  | Electricity Usage (kWh/SqF) | Gas Usage (kWh/SqF)
[8 empty] | 140.4 |  | 81.5 |  |  |  |  | 40.9 | 16.31 |  | 195.2005
[8 empty] | 140.9 |  | 82.1 |  |  |  |  | 39.8 | 13.63
[8 empty] | 142.5 |  | 84.2 |  |  |  |  | 38 | 13.46
[8 empty] | 141.7 |  | 83.2 |  |  |  |  | 37.6 | 13.59
[8 empty] | 142.4 |  | 84.2 |  |  |  |  | 41.2 | 12.4
[8 empty] | 142.7 |  | 84.5 |  |  |  |  | 33.4 | 15.7
[8 empty] | 140.8 |  | 82 |  |  |  |  | 39.4 | 17.66
[8 empty] | 141.6 |  | 83.1 |  |  |  |  | 34.7 | 16.15
[15 empty] | 33.2 | 12.45
[15 empty] | 38.8 | 27.69
[8 empty] | CA Climate Zone | Climate Character (short) | HDD vs CDD Balance | HVAC Dominance |  |  |  | 39.1 | 15.49
[8 empty] | CZ 1 | Cool coastal / marine | HDD ≫ CDD | Heating-dominated |  |  |  | 38.9 | 15.11
[8 empty] | CZ 2 | Coastal, slightly inland | HDD > CDD | Heating-leaning |  |  |  | 40 | 18.25
[8 empty] | CZ 3 | Mild coastal | HDD > CDD | Heating-leaning |  |  |  | 36.4 | 29.45
[8 empty] | CZ 4 | Mild coastal / near inland | HDD ≈ CDD (low total) | Balanced (slight heating) |  |  |  | 39 | 21.06
[8 empty] | CZ 5 | Mildest CA climate | HDD ≈ CDD (low both) | Balanced |  |  |  | 39.4 | 30.04
[8 empty] | CZ 6 | Southern coastal | CDD > HDD | Cooling-leaning
[8 empty] | CZ 7 | Inland SoCal | CDD > HDD | Cooling-dominated
[8 empty] | CZ 8 | Inland SoCal (hotter) | CDD ≫ HDD | Cooling-dominated
[8 empty] | CZ 9 | LA Basin / inland | CDD ≫ HDD | Cooling-dominated
[8 empty] | CZ 10 | Inland valleys | CDD ≫ HDD | Cooling-dominated
[8 empty] | CZ 11 | Inland north / foothills | HDD > CDD | Heating-dominated
[8 empty] | CZ 12 | Inland north (milder) | HDD > CDD | Heating-leaning
[8 empty] | CZ 13 | Central Valley | HDD ≈ CDD (both high) | Mixed (high energy)
[8 empty] | CZ 14 | Desert | CDD ≫≫ HDD | Strongly cooling-dominated
[8 empty] | CZ 15 | Hot desert | CDD ≫≫ HDD | Extremely cooling-dominated
[8 empty] | CZ 16 | Extreme desert | CDD ≫≫≫ HDD | Extreme cooling-dominated

## Weights
% of Floor Area per CZ and Vintage Bin - RetailGrocery | [6 empty] | % of Floor Area per CZ and Vintage Bin - RetailGrocery
Prototype | CZ | Vintage Bin |  |  |  |  | Prototype | Vintage Bin | CZ
|  | Pre-1978 | 1978-1997 | 1998-2007 | 2008-2018 |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
Grocery | 1 | 35.22% | 47.03% | 8.869% | 8.879% | 100% | Grocery | Pre-1978 | 1.006% | 2.566% | 7.599% | 3.969% | 0.5271% | 8.537% | 3.711% | 13.38% | 19.42% | 6.501% | 3.15% | 12.17% | 4.819% | 2.447% | 3.05% | 7.143% | 100%
| 2 | 45.37% | 38.11% | 12.78% | 3.74% | 100% |  | 1978-1997 | 1.421% | 2.28% | 5.189% | 2.419% | 0.8886% | 5.019% | 6.165% | 7.744% | 13.03% | 11.33% | 3.916% | 15.63% | 6.238% | 1.929% | 7.065% | 9.737% | 100%
| 3 | 43.85% | 28.31% | 24.42% | 3.419% | 100% |  | 1998-2007 | 0.8794% | 2.508% | 14.69% | 7.211% | 1.998% | 4.475% | 2.584% | 4.417% | 10.35% | 5.259% | 5.02% | 26.29% | 3.189% | 1.868% | 0.4591% | 8.811% | 100%
| 4 | 46% | 26.59% | 24.16% | 3.109% | 99.85% |  | 2008-2018 | 1.538% | 1.283% | 3.593% | 1.621% | 0.5575% | 3.338% | 2.547% | 5.076% | 6.886% | 14.46% | 5.366% | 18.01% | 7.401% | 2.581% | 9.491% | 16.25% | 100%
| 5 | 26% | 41.28% | 28.29% | 4.518% | 100.1%
| 6 | 56% | 31.38% | 8.527% | 3.64% | 99.55% |  | Total | 1.191% | 2.358% | 7.225% | 3.586% | 0.8484% | 6.305% | 4.463% | 9.512% | 14.95% | 8.802% | 3.829% | 15.63% | 5.36% | 2.182% | 4.765% | 8.992% | 100%
| 7 | 35% | 54.45% | 6.957% | 3.924% | 100.3%
| 8 | 59% | 32.09% | 5.579% | 3.669% | 100.3%
| 9 | 54% | 34.36% | 8.315% | 3.167% | 99.84%
| 10 | 31% | 50.73% | 7.178% | 11.3% | 100.2%
| 11 | 34% | 40.31% | 15.75% | 9.637% | 99.7%
| 12 | 32% | 39.41% | 20.2% | 7.923% | 99.54%
| 13 | 37% | 45.87% | 7.148% | 9.494% | 99.52%
| 14 | 47% | 34.84% | 10.28% | 8.133% | 100.3%
| 15 | 27% | 58.45% | 1.158% | 13.7% | 100.3%
| 16 | 33% | 42.69% | 11.77% | 12.42% | 99.88%
| Statewide | 42% | 39.42% | 12.01% | 6.876% | 100.3%
Ref: CEUS 2022 dataset: Food store group
And converted FZ level data to CZ level
Background Data [To be deleted prior to publication]

## PV (hidden)
PV - RetailGrocery
TBD

## EV Charger (hidden)
EV Charger - RetailGrocery
TBD
Background Data [To be deleted prior to publication]

## Data (hidden)
Space Function | Electric Equipment Load Intensity | Electric Equipment Load Intensity | LPD
Aging Eye/Low-vision (Corridor Area) |  |  | 2013 | 2016 | 2019 | 2025
Aging Eye/Low-vision (Dining)
Aging Eye/Low-vision (Lobby, Main Entry)
Aging Eye/Low-vision (Lounge/Waiting Area)
Aging Eye/Low-vision (Multipurpose Room)
Aging Eye/Low-vision (Religious Worship Area)
Aging Eye/Low-vision (Restroom)
Aging Eye/Low-vision (Stairwell)
Audience Seating Area
Auditorium Area
Auto Repair / Maintenance Area
Barber, Beauty Salon, Spa Area
Civic Meeting Place Area
Classroom, Lecture, Training, Vocational Areas
Concourse and Atria Area
Convention, Conference, Multipurpose and Meeting Area
Copy Room
Corridor Area
Dining Area (Bar/Lounge and Fine Dining)
Dining Area (Cafeteria/Fast Food)
Dining Area (Family and Leisure)
Electrical, Mechanical, Telephone Rooms
Exercise/Fitness Center and Gymnasium Areas
Financial Transaction Area
Healthcare Facility and Hospitals (Exam/Treatment Room)
Healthcare Facility and Hospitals (Imaging Room)
Healthcare Facility and Hospitals (Medical Supply Room)
Healthcare Facility and Hospitals (Nursery)
Healthcare Facility and Hospitals (Nurse's Station)
Healthcare Facility and Hospitals (Operating Room)
Healthcare Facility and Hospitals (Patient Room)
Healthcare Facility and Hospitals (Physical Therapy Room)
Healthcare Facility and Hospitals (Recovery Room)
Hotel Function Area
Kitchen/Food Preparation Area
Kitchenette or Residential Kitchen
Laboratory, Scientific
Laundry Area
Library (Reading Area)
Library (Stacks Area)
Lobby, Main Entry
Locker Room
Lounge, Breakroom, or Waiting Area
Manufacturing, Commercial & Industrial Work Area (Low Bay)
Manufacturing, Commercial & Industrial Work Area (High Bay)
Manufacturing, Commercial & Industrial Work Area (Precision)
Museum Area (Exhibition/Display)
Museum Area (Restoration Room)
Office Area (>250 square feet)
Office Area (<250 square feet)
Parking Garage Area (Parking Zone and Ramps)
Parking Garage Area (Daylight Adaptation Zones)
Pharmacy Area
Retail Sales Area (Grocery Sales)
Retail Sales Area (Retail Merchandise Sales)
Retail Sales Area (Fitting Room)
Religious Worship Area
Restrooms
Stairwell
Storage, Commercial/Industrial (Warehouse)
Storage, Commercial/Industrial (Refrigerated)
Storage, Commercial/Industrial (Shipping & Handling)
Storage (General)
Sports Arena - Playing Area (> 5,000 Spectators)
Sports Arena - Playing Area (2,000 - 5,000 Spectators)
Sports Arena - Playing Area (< 2,000 Spectators)
Sports Arena - Playing Area (Recreational)
Theater Area (Motion Picture)
Theater Area (Performance)
Transportation Function (Baggage Area)
Transportation Function (Ticketing Area)
Videoconferencing Studio
High-Rise Residential Living Spaces
Hotel/Motel Guest Room
All other
Attic
Reception Area
Elevator
Plenum
IT Room (EPD 12)
Computer Room (EPD 20)
Server Room (EPD 45)