## Notes
Data Sources
Dataset |  | DSA Drawings for relocatable schools
| Berkeley Lab article | https://www2.lbl.gov/Science-Articles/Archive/EETD-portable-classrooms.html
| California Portable Classroom Study | https://ww2.arb.ca.gov/sites/default/files/classic/research/apr/reports/l3006.pdf
| California Legislature Environmental Health Conditions in California's Portable Classrooms | https://ww2.arb.ca.gov/sites/default/files/2020-05/pcs_v3_es_03-23-04.pdf
Codes | Title 24, part 6, referred to as T24 (1984, 2001, 2007, 2013, 2016, 2022, 2025)
ASHRAE 90.1 (2022)
CFR Title 10 (2008, 2010, 2025)
Other | ACM 2022
| T24 2022 - Appendix 5.4A and Appendix 5.4B | https://www.energy.ca.gov/publications/2022/2022-nonresidential-and-multifamily-alternative-calculation-method-reference
| 2022 Reduced infiltration CASE report | https://title24stakeholders.com/wp-content/uploads/2020/10/2022-T24-Final-CASE-Report_Reduce-Infiltration.pdf
| 2019 Outdoor Lighting CASE Report | https://title24stakeholders.com/wp-content/uploads/2016/10/T24-2019-CASE-Study-Results-Report-Outdoor-Sources_Final_with-Attachments.pdf
| 2019 High Efficiency Fume Hoods in Laboratory Spaces CASE Report | https://title24stakeholders.com/wp-content/uploads/2017/09/2019-T24-CASE-Report_Fume-Hoods_Final_September-2017.pdf?
| PNNL 20405, 2011 | https://www.pnnl.gov/main/publications/external/technical_reports/PNNL-20405.pdf
| Air leakage Memo, NORESCO, 2025 | Infiltration_rate_report_14May2025-Short-Version.docx
| BARD Engineering Specification Guide for SPVHP | BARD Engineering Specification Guide for SPVHP
Construction Rate
Notes

## Prototype
NORESCO, Updated September 2026
SchoolRelocatable
Characteristic | Value | Data Sources
Building Type | Relocatable School
Building Category | Nonresidential
Version | v2-0
Vintages | 4 Vintages: Pre-1978, 1978-1997,1998-2007, 2008-2018 New Construction (2019+) | Based on the vintage bin analysis. A summary of the findings is presented in the following paper, with a link provided in the Notes tab: Yousefi, F., Athalye, R. (2025). “Determining Vintage Bins for Prototype Development: An Analysis of California Commercial Buildings.” ASHRAE Annual Conference.
Shape |  | The analysis uses prototype geometry originally developed by CEC.
Total Floor Area (ft²) | 1920.19 | Same as CEC prototype
Aspect Ratio | 1.6667
Number of Floors | 1
Roof type | Flat
WWR | 5.15% | Same as CEC prototype
Shading Geometry | No Shades
Floor to floor height (feet) | 12 ft | Typical height
Floor to ceiling height (feet) | 12 ft | Typical height
Glazing sill height (feet) | 2.9 ft | Typical sill height
Above grade wall area (ft²) | 1536.15
Gross wall area (ft²) | 1920.15
Roof area (ft²) | 960.09
Underground Gross Wall Area (ft²) | 384

## Zones
Proposed Layout - SchoolRelocatable
Building | Space/Thermal Zone | Space Type [Primarily from: T24, 2022 Appendix 5.4A] - See Notes column | Space/Thermal Zone | HVAC System Name/AHU Name | Schedule Category | Conditioned (Y/N) | Area Fraction | Area (ft²) | Volume (ft³) | Multipliers | Number of People | People (Persons/1,000 ft²) [T24, 2025,Table 120.1-A] | Notes
SchoolRelocatable | Classroom | Classroom, Lecture, Training, Vocational Areas | Classroom | System 5 | Classroom | Yes | 50% | 960 | 11521.69 | 1 | 24 | 25
SchoolRelocatable | Crawlspace | Unoccupied-Exclude from Gross Floor Area | Crawlspace |  |  | No | 50% | 960 | 2884 | 1
Total (1 Building) | Total (2 spaces) | Total (2 Space types) | Total (2 spaces) | Total ( 1 HVAC zone) | Total (1 Schedule categories) | Total (1 Conditioned zones) | 100% | 1920 | 14405.69 |  | 24 | 25
N

## Envelope
Envelope - SchoolRelocatable
Element | Prototype | Assembly Type | Construction | Thermal Properties | Vintage | Selected T24 | Notes | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
External Wall | SchoolRelocatable | ExtWall_MetalFramed_NonRes | Metal framed wall: Metal frame+ insulation + Gypsum board | U-factor IP | Pre 1978 | N/A | Using DOE pre-1980 U-value of 0.227 for school and a 9.2% cumulative wall renovation rate through 2028, based on the average annual rate from CBECS 2003 and 2012 projected over 48 years. | 0.1971 | 0.20041 | 0.19857 | 0.20041 | 0.20041 | 0.1971 | 0.1971 | 0.20041 | 0.20041 | 0.20041 | 0.20041 | 0.20041 | 0.20041 | 0.20041 | 0.20041 | 0.20041
[5 empty] | 1978-1997 | 1992 | TABLE NO. 1-I metal-framed | 0.182 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182
[5 empty] | 1998-2007 | 2001 | TABLE 1-H-NonRes Bldgs | 0.182 | 0.182 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182
[5 empty] | 2008-2018 | 2013 | TABLE 140.3-B-NonRes Bldgs | 0.098 | 0.062 | 0.082 | 0.062 | 0.062 | 0.098 | 0.098 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062
[5 empty] | Existing |  | Weighted average of all 4 vintages | 0.18765 | 0.19694 | 0.19533 | 0.19702 | 0.1942 | 0.19043 | 0.16914 | 0.19229 | 0.19406 | 0.17588 | 0.18973 | 0.18754 | 0.18035 | 0.1798 | 0.18001 | 0.17867
[5 empty] | 2019+ | 2025 | TABLE 140.3-B-NonRes Bldgs | 0.06 | 0.055 | 0.071 | 0.055 | 0.055 | 0.06 | 0.06 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055
Roof | SchoolRelocatable | FlatRoof_WoodFramedAndOther_NonRes | Metal framed roof: steel truss + cavity insulation + plywood deck + above deck insulation + membrane + coverboard | U-value IP | Pre 1978 | N/A | Considering 30 years for roof/ insulation replacement. | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 1978-1997 | 1986 |  | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 1998-2007 | 2001 | Table 1-H | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.049 | 0.039 | 0.039 | 0.039 | 0.049 | 0.075 | 0.067 | 0.067 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039
[5 empty] | Existing |  | Weighted average of all 4 vintages | 0.056731 | 0.056747 | 0.056871 | 0.056877 | 0.056938 | 0.077861 | 0.075305 | 0.077577 | 0.077066 | 0.066517 | 0.056651 | 0.05643 | 0.055726 | 0.055138 | 0.056117 | 0.055132
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.047 | 0.047 | 0.047 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028
Windows_Nonrs | SchoolRelocatable | OperableWindow_NonRes | Single pane | U-factor IP | Pre 1978 | N/A | ASHRAE Handbook of Fundamentals (Table 4-Ch15) for operable single pane & T24, 2013 for double pane (58%-42%) | 0.9066 | 0.9066 | 0.9066 | 0.9066 | 0.9066 | 0.9066 | 0.9066 | 0.9066 | 0.9066 | 0.9066 | 0.9066 | 0.9066 | 0.9066 | 0.9066 | 0.9066 | 0.9066
[5 empty] | 1978-1997 | N/A |  | 0.9066 | 0.9066 | 0.9066 | 0.9066 | 0.9066 | 0.9066 | 0.9066 | 0.9066 | 0.9066 | 0.9066 | 0.9066 | 0.9066 | 0.9066 | 0.9066 | 0.9066 | 0.9066
|  |  | Double pane |  | 1998-2007 | 2001 | Table1-H | 0.49 | 0.49 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46
[5 empty] | Existing |  | Weighted average of all 4 vintages | 0.85496 | 0.88432 | 0.9018 | 0.90256 | 0.90077 | 0.87534 | 0.77818 | 0.87875 | 0.88747 | 0.71666 | 0.86305 | 0.84702 | 0.80919 | 0.79739 | 0.66487 | 0.80161
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46
| SchoolRelocatable | OperableWindow_NonRes | Single pane | SHGC | Pre 1978 | N/A | ASHRAE Handbook of Fundamentals (Table 4-Ch15) for operable single pane & T24, 2013 for double pane (58%-42%) | 0.5506 | 0.5506 | 0.5506 | 0.5506 | 0.5506 | 0.5506 | 0.5506 | 0.5506 | 0.5506 | 0.5506 | 0.5506 | 0.5506 | 0.5506 | 0.5506 | 0.5506 | 0.5506
[5 empty] | 1978-1997 | N/A |  | 0.5506 | 0.5506 | 0.5506 | 0.5506 | 0.5506 | 0.5506 | 0.5506 | 0.5506 | 0.5506 | 0.5506 | 0.5506 | 0.5506 | 0.5506 | 0.5506 | 0.5506 | 0.5506
|  |  | Double pane |  | 1998-2007 | 2001 | Table 1-H (based on non north with WWR 30-40% ) | 0.45 | 0.39 | 0.51 | 0.51 | 0.51 | 0.475 | 0.475 | 0.475 | 0.475 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.45
[5 empty] | 2008-2018 | 2013 | Table 140.3-B (100% fixed, 0% operable) | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22
[5 empty] | Existing |  | Weighted average of all 4 vintages | 0.53064 | 0.53978 | 0.54756 | 0.54793 | 0.54704 | 0.52702 | 0.45473 | 0.52953 | 0.53608 | 0.45904 | 0.53074 | 0.52261 | 0.50183 | 0.49211 | 0.44964 | 0.50214
[5 empty] | 2019+ | 2025 | Table 140.3-B (100% fixed, 0% operable) | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22
* California Legislature Environmental Health Conditions in California's Portable Classrooms
Infiltration
|  |  | Building | Zones | Vintage | I_75 6-Sided Infiltration rate @ 75 pa | Note | CZ1: I-design (cfm/ft²) (4-sided Infiltration rate at normal pressure) (Design flow rate approach and Flow/Exterior Wall Area calculation method) | 0.028 | 0.028
|  | Infiltration | SchoolRelocatable | Classroom | Pre 1978 | 1.1 | 2022 CASE report (Table 38) | CZ1: 0.308
[5 empty] | 1978-1997 | 1.1 | 2022 CASE report (Table 38) | CZ1: 0.308
[5 empty] | 1998-2007 | 1.1 | 2022 CASE report (Table 38) | CZ1: 0.308
[5 empty] | 2008-2018 | 1 | 2022 CASE report (Table 38) & T24, 2008-2016 (Table 140.3-B)--Air barrier is required in CZ 10-16 | CZ1: 0.2818
[5 empty] | Existing |  | Same as Pre 2008 because of their higher weights | CZ1: 0.308
[5 empty] | 2019+ | 0.6 | 2022 CASE report (Table 38) & T24, 2025 (Table 140.3-B)--Air barrier is required in all CZs | CZ1: 0.168
Source: T24 air barrier requirements (all editions) and the standardized infiltration rate reported in the 2022 CASE report and Dodge 2023 data
|  |  |  | Air Leakage Memo: |  | Infiltration_rate_report_14May2025-Short-Version.docx
Pre-1978 exterior wall U value calculation:
External Wall | SchoolRelocatable | ExtWall_MetalFramed_NonRes | Metal framed wall: Metal frame + insulation + Gypsum board | U-value IP | Pre 1978 | N/A | ASHRAE 90.1-2022 Table A3.3.3.1 (metal-framed), 3.5 in., R-0 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352
[7 empty] | T24 2008 (U value): Metal framed wall Nonres | 0.098 | 0.062 | 0.082 | 0.062 | 0.062 | 0.098 | 0.098 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062
[7 empty] | DOE pre 1980 prototype LA (U value) | 0.227 | 0.227 | 0.227 | 0.227 | 0.227 | 0.227 | 0.227 | 0.227 | 0.227 | 0.227 | 0.227 | 0.227 | 0.227 | 0.227 | 0.227 | 0.227
[7 empty] | Renovation rate since 1980 (yearly school renovation rate was calculated from CBECS 2003 and 2012 and then projected over 48 years) | CZ1: 9.2%
Background Data [To be deleted prior to publication]
External Wall | SchoolRelocatable | ExtWall_MetalFramed_NonRes | Metal framed wall: Metal frame+ insulation + Gypsum board | U-factor IP | Pre 1978 | N/A | ASHRAE 90.1-2022 Table A3.3.3.1 (metal-framed), 3.5 in., R-0, U-0.352 all CZ. Was U-0.292 (A3.4.3.1 wood/mass); construction C3 is ExtWall_MetalFramed_NonRes. | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352
[5 empty] | 1978-1997 | 1986 | Heat Capacity was considered 10.0-14.99 (Btu/F-ft²) | 0.15083 | 0.15748 | 0.15748 | 0.14368 | 0.14368 | 0.21645 | 0.21645 | 0.21645 | 0.21645 | 0.21645 | 0.18622 | 0.18622 | 0.18622 | 0.15873 | 0.15873 | 0.15083

## HVAC System
HVAC system - SchoolRelocatable
Vintage | Zones | Heating | Cooling | Air Distribution | Other System | Source | Note
Existing | Classroom, Lecture, Training, Vocational Areas | SPVHP | DX Coil | CAV | Economizer* Fix Dry bulb; integrated; High DB Temperature Lockout: 75 °F | ACM 2025 | System 3b
New Construction | Classroom, Lecture, Training, Vocational Areas | SPVHP | DX Coil | CAV | Economizer* Fix Dry bulb; integrated; High DB Temperature Lockout: 75 °F | ACM 2025 | System 3b
Efficiency of HVAC system (Efficiency is capacity-dependent. The following table provides a general estimate of system efficiency based on preliminary simulations in one climate zone, or assuming cooling load based on rule of thumb)
Vintage | Upgrade/Installed year | Heating DX | Supplementary Heating Coil | Cooling DX | Source |  | Note
Pre 1978 | 2008 | COP = 3 | Efficiency: 100% (Electric) | EER = 9.0 | 10 CFR 431.97, Table 10 to paragraph (e)(2): SPVHP <65,000 Btu/h → EER 9.0, COP 3.0 (federal standard effective Jan 1, 2010; used here for legacy/vintage modeling consistency) |  | System 3b
1978-1997
1998-2007
2008-2018 | 2013 | COP = 3 | Efficiency: 100% (Electric) | EER = 9.0 | 10 CFR 431.97, Table 10 to paragraph (e)(2): SPVHP <65,000 Btu/h → EER 9.0, COP 3.0 (still governing in 2013; later update came in 2019)
New Construction | 2025 | COP = 3.3 | Efficiency: 100% (Electric) | EER = 11.0 | CEC 2025 Space-Conditioning Efficiency Tables, Table 5 (row: SPVHP <65,000 Btu/h → EER 11.0, COP 3.3, test AHRI 390). The table cites 10 CFR 431 Subpart F as the federal basis |  | System 3b
Fan power
Vintage | Approach | System | Total Static Pressure (TSP) (in w.c.) | Fan Efficiency [ACM 2025] | Motor Efficiency | Fan Power Index (W/cfm) | Data Source
Existing | PNNL 90.1-2011, TSP | CAV, SPVHP classroom, design airflow < 7,437 cfm | 2.5 | 0.65 | ASHRAE 90.1, 2004, Table 10.8 * |  | Fan power formula: PNNL 20405, 2010, section 5.2.2.5 TSP and fan efficiency: PNNL 20405, 2010, Table 5.11, 90.1-04ac values Motor and drive efficiency: ASHRAE 90.1, 2004, Table 10.8 | PNNL 20405, 2010, Table 5.11
Brake horsepower (bhp) = (Supply cfm × TSP in w.c.) / (6356 × fan efficiency)
Fan power (w/cfm) = (bhp × 746) / ( supply cfm × motor efficiency )
New Construction | ACM 2025 | SPVHP (System 3b), CAV classroom, ≤5,000 cfm | TSP = fan power × motor efficiency × fan efficiency × 6356 / 746 | 0.65 | 2025 ACM Table 12 ** | 0.744 | Fan power index: [ACM 2025, Table 13] Motor efficiency: [ACM 2025, Table 12]
* According to PNNL 20405 section 5.2.2.5, the full-load efficiency of the motor serving the fan is taken from ASHRAE 90.1, 2004, Table 10.8, based on motor nameplate and assuming enclosed motors operating at 1,800 rotations per minute (rpm) Motor nameplate size (bhp) = brake horsepower (bhp) × 1.1 ( using a 10% oversizing factor)
** The full‑load efficiency of the motor serving the fan is taken from ACM 2025 Table 12 based on the cfm of the fan. Brake horsepower (bhp) = (Supply cfm from sizing run × fan power in W/cfm) / 746. Note: Same index as Hotel Small System 3b SZHP ≤5,000 cfm.
Background Data [To be deleted prior to publication]
BARD Engineering Specification Guide for SPVHP

## Thermostat
Thermostat Setpoints - SchoolRelocatable
Setpoint | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16 | Source
School Heating Setpoint (F) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | T24 2022 - Appendix 5.4B
School Heating Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
School Cooling Setpoint (F) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | T24 2022 - Appendix 5.4B
School Cooling Setback (F) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85

## Ventilation
Outdoor Airflow Rate - SchoolRelocatable
Space Type | Space/Thermal Zone | Number of People | Floor Area (ft²) | cfm/person [T24, 2025, Equation 120.1-F and Table 120.1-A] | cfm/ft² [T24, 2025, Equation 120.1-F and Table 120.1-A] | Required exhaust rate-CFM/ft²- [T24, 2025, Table 120.1-B – minimum exhaust rates] | Total cfm driven by people | Total cfm driven by area | Total cfm driven by exhaust | Total cfm | Notes
Classroom, Lecture, Training, Vocational Areas | Classroom | 24 | 960 | 15 | 0.15 |  | 360 | 144 | 0 | 360
Unoccupied-Exclude from Gross Floor Area | Crawlspace | 0 | 960 |  |  |  | 0 | 0 | 0 | 0
| Total (2 spaces) | 24 | 1920 |  |  |  | 360 | 144 | 0 | 360

## Water Heater
Water Heater -SchoolRelocatable
Vintage | WH Type | Efficiency | Number of WH | Tank Volume (gal) | Tank Loss | Source | Notes
Existing | Electric | 1 | 1 | See CZ05 Table, Storage Volume column (col F) | See Climate Zone Water Heater Sizing and Loss Coefficients Table, Standby Loss column (col G) |  | Electric kept for Existing: a relocatable classroom normally has no gas service, so the gas storage water heater used for the permanent school prototypes (CEUS 2022) is not applied here.
New Construction | Electric | 1 | 1 | See CZ05 Table, Storage Volume column (col F) | See Climate Zone Water Heater Sizing and Loss Coefficients Table, Standby Loss column (col G) |  | Section 1605.1. Federal and State Standards for Federally-Regulated Appliances. Electric storage standby loss: Title 20 Table F-4 (0.30 + 27/Vm %/hr).
Peak Hot Water Consumption
Space Name | Baseline WH Type [T24, 2022, Appendix 5.4A , sheet: "2022 SpaceFuncData-Input"] | New Construction: Baseline WH Type ACM 2025 | Total Area (ft²) | Number of People | Hot Water Usage Specification (gal/hr per person) [T24, 2022, Appendix 5.4A , sheet: "2022 SpaceFuncData-Input"] | Peak Hot Water Usage (gal/hr) | Peak Hot Water Usage (gal/min)
Classroom | Electric | Electric | 960 | 24 | 0.18 | 4.32 | 0.072
Total |  |  | 960 | 24 | 0.18 | 4.32 | 0.072
| Gas storage |  |  |  |  | 0 | Minimum peak hot water usage is 75 gal according to ACM 2025
| Electric resistance |  |  |  |  | 75
Maximum flow rate (GPM) | 0.5 | CALGreen §5.303.3.4.1 (Title 24, Part 11, 2025)
Design supply temperature (°F) | 135 | Title 24 2022 Reference Appendices, Appendix 5.4B
WH system factor | 0.6 | Not used for tankless (column D = C). 2025 ACM §5.9.2 storage system factor.
Water mass conversion (lb/gal) | 8.2877 | 2025 ACM §5.9.2 Rated Capacity
Tankless storage volume (gal) | 2 | Title 20 instantaneous class (storage typically <2 gal); scorecard uses 2.
Climate Zone Water Heater Sizing and Loss Coefficients
Climate Zone | Minimum Monthly Mains Temp (°F) [T24 2022 - Appendix 5.4B] | Heat Output (Btu/hr) [ACM, 2025, 5.9.2: Rated capacity section] | WH Capacity (Btu/hr) [ACM, 2025, 5.9.2: Rated capacity section] | Required Energy Input (Btu/hr) | Storage Volume (gal) | Standby Loss [Title 20, §1605.1 Table F-4; Appendix B: Water Heating Calculation Method] |  | Off/On Cycle Loss Coefficient to Ambient Temp |  | Source/Note
CZ01 | 47.9 | 21655.7601 | 21655.7601 | 27296 | 2 | 0 | %/hr | 0 | Btu/h·°F | Required Energy Input: vendor/available catalog size (Market data table). Storage Volume: standard/available catalog tank size (Market data table).
CZ02 | 50.8 | 20934.7302 | 20934.7302 | 27296 | 2 | 0 | %/hr | 0 | Btu/h·°F
CZ03 | 52.2 | 20586.6468 | 20586.6468 | 27296 | 2 | 0 | %/hr | 0 | Btu/h·°F
CZ04 | 52.7 | 20462.3313 | 20462.3313 | 20472 | 2 | 0 | %/hr | 0 | Btu/h·°F
CZ05 | 51.6 | 20735.8254 | 20735.8254 | 27296 | 2 | 0 | %/hr | 0 | Btu/h·°F
CZ06 | 56.8 | 19442.9442 | 19442.9442 | 20472 | 2 | 0 | %/hr | 0 | Btu/h·°F
CZ07 | 58.4 | 19045.1346 | 19045.1346 | 20472 | 2 | 0 | %/hr | 0 | Btu/h·°F
CZ08 | 58.4 | 19045.1346 | 19045.1346 | 20472 | 2 | 0 | %/hr | 0 | Btu/h·°F
CZ09 | 57.6 | 19244.0394 | 19244.0394 | 20472 | 2 | 0 | %/hr | 0 | Btu/h·°F
CZ10 | 57.1 | 19368.3549 | 19368.3549 | 20472 | 2 | 0 | %/hr | 0 | Btu/h·°F
CZ11 | 50.5 | 21009.3195 | 21009.3195 | 27296 | 2 | 0 | %/hr | 0 | Btu/h·°F
CZ12 | 51.4 | 20785.5516 | 20785.5516 | 27296 | 2 | 0 | %/hr | 0 | Btu/h·°F
CZ13 | 51.7 | 20710.9623 | 20710.9623 | 27296 | 2 | 0 | %/hr | 0 | Btu/h·°F
CZ14 | 50.1 | 21108.7719 | 21108.7719 | 27296 | 2 | 0 | %/hr | 0 | Btu/h·°F
CZ15 | 63.2 | 17851.7058 | 17851.7058 | 20472 | 2 | 0 | %/hr | 0 | Btu/h·°F
CZ16 | 41.4 | 23271.8616 | 23271.8616 | 27296 | 2 | 0 | %/hr | 0 | Btu/h·°F
Market data
Catalog input (kW) | Input (Btu/h) | Max GPM | UEF | Source | Sources and links → Note tab
2.5 | 8530 | 0.5 | 0.99 | Grainger
4.5 | 15354 | 0.5 | 0.99 | Grainger
6 | 20472 | 0.7 | 0.99 | Grainger
8 | 27296 | 1 | 0.93 | Grainger
11 | 37532 | 1.5 | 0.93 | Grainger
18 | 61416 | 2 | 0.93 | Grainger
27 | 92124 | 2.5 | 0.93 | Grainger

## Interior Lights
Interior Lighting - SchoolRelocatable
Space Type | New Construction |  |  | Existing |  |  | Notes
| Lighting density (W/ft²) | Additional lighting power allowance (W/ftÂ²) [Table 140.6-C footnoted allowance] | Source | LPD (W/ft²) | Additional lighting power allowance (W/ftÂ²) [Table 140.6-C footnoted allowance] | Source
Classroom, Lecture, Training, Vocational Areas | 0.6 |  | T24, 2025, Table 140.6 C (Area category method) | 1.2 |  | T24, 2016, Table 140.6 C (Area category method)
Unoccupied-Exclude from Gross Floor Area | 0 |  |  | 0
Additional allowances are the full Table 140.6-C value for the footnoted lighting system (New Construction: T24 2025; Existing: T24 2016). The allowance only applies where that lighting system is installed. White board/chalk board allowances are per linear foot and are not included.

## Ext Lighting
Exterior Lighting - SchoolRelocatable
Motion Controlled Luminaires (W) | Non-motion Controlled Luminaires (W) | Total (W) | Source
200 | 307.8721 | 507.8721 | T24, 2022 & 2025 2019 Outdoor Lighting CASE report PNNL 90.1-2010 TSD
Exterior Lighting
Items (Assume LZ2) | Assumptions [2019 Outdoor Lighting CASE Report & PNNL 90.1-2010 TS] |  | Unit | Lighting Power Allowance [T24, 2025, Table 140.7-A & 140.7-B] | Unit | Exterior Lighting Power (W)
IWA (Initial Wattage Allowance) |  |  |  | 200 | (W) | 200
Parking area | 400 ft² for every parking space 1 parking space per 830 ft² of gross building area | 0 | (ft²) | 0.019 | (W/ft²) | 0
Building Entrance | 5 building entrance per PNNL Model (1 per 10,000 ft² footprint) | 0 | (count) | 15 | (W/ea) | 0
Hardscape Ornamental Light | 0.1 ft² per 1 ft² of gross building area for hardscape ornamental light | 96.0095 | (ft²) | 0.007 | (W/ft²) | 0.67207
Building façade | 0.1 W per 1 ft² of facade area Façade Area = Perimeter × 0.5 × max ( height and 30) (30 ft is the max height that is lit) * The 0.5 factor assumes that only half of the perimeter walls are lit. -Formula is developed based on the 2019 Outdoor Lighting CASE report | 3072 | (ft²) | 0.1 | (W/ft²) | 307.2
Motion Controlled Luminaires (W) | [5 empty] | 200
Non-motion-controlled Luminaires | [5 empty] | 307.8721
Total | [5 empty] | 507.8721
Max Height (ft) | 12
Building footprint | 480.0475
Floors | 1
Perimeter(ft) | 128
Total floor area (ft²) | 960.095

## Equipment
Equipment - SchoolRelocatable
Space Type | Plug load Power Density (W/ft²) | Gas Power Density (Btu/hr-ft²) | Refrigeration Power Density (W/ft²) | Source
Classroom, Lecture, Training, Vocational Areas | 0.8 | 0 | 0 | T24 2022 - Appendix 5.4A
Unoccupied-Exclude from Gross Floor Area | 0 | 0 | 0

## Schedules
Schedules - SchoolRelocatable
Zone | Schedule Category | Schedule | Source | Type | Hour
[5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
All zones (single classroom zone) | Classroom | Occupancy | T24 2022 - Appendix 5.4B [School] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.75 | 0.9 | 0.9 | 0.8 | 0.8 | 0.8 | 0.8 | 0.45 | 0.15 | 0.05 | 0.15 | 0.2 | 0.2 | 0.1 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
All zones (single classroom zone) | Classroom | Lights | T24 2022 - Appendix 5.4B [School] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.6 | 0.65 | 0.65 | 0.65 | 0.55 | 0.55 | 0.55 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.3 | 0.05 | 0.05
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
All zones (single classroom zone) | Classroom | ElecEquipment | T24 2022 - Appendix 5.4B [School] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.85 | 0.95 | 0.95 | 0.95 | 0.8 | 0.8 | 0.8 | 0.7 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.3 | 0.05 | 0.05
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
All zones (single classroom zone) | Classroom | ServiceHotWater | T24 2022 - Appendix 5.4B [School] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09
|  |  |  | Saturday | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
|  |  |  | Sunday | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
All zones (single classroom zone) | Classroom | GasEquipment | T24 2022 - Appendix 5.4B [School] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.75 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
All zones (single classroom zone) | Classroom | Refrigeration | T24 2022 - Appendix 5.4B [School] | Weekday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Saturday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Sunday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
All zones (single classroom zone) | Classroom | HVACAvail | T24 2022 - Appendix 5.4B [School] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
All zones (single classroom zone) | Classroom | HtgSetpt | T24 2022 - Appendix 5.4B [School] | Weekday | 60 | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 60 | 60
|  |  |  | Saturday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  |  | Sunday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
All zones (single classroom zone) | Classroom | ClgSetpt | T24 2022 - Appendix 5.4B [School] | Weekday | 85 | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 85 | 85
|  |  |  | Saturday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
|  |  |  | Sunday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
All zones (single classroom zone) | Classroom | Infiltration | T24 2022 - Appendix 5.4B [School] (0.25 while the HVAC is on, 1.0 otherwise) | Weekday | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1
|  |  |  | Saturday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Sunday | bar: Hour 1 to Hour 24
Other
| Building | ExtLightingNonMotionCtrl |  | Weekday | bar: Hour 1 to Hour 24
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
| Building | ExtLightingMotionCtrl |  | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Classroom | Building | MeetingPeopleActivityLevel | Constant activity level from the CEC prototype schedule library (as used in the SCE K-8 model, SchoolK8.idf) | Weekday | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2
|  |  |  | Saturday | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2
|  |  |  | Sunday | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2

## Energy Usage
CalBEM Energy Consumption - Relocatable School | [11 empty] | Energy Consumption - SchoolRelocatable
Prototype | CZ | CalBEM Electricity EUI (KBTU/ft²) | CalBEM Gas EUI (KBTU/ft²) | CalBEM Total EUI (KBTU/ft²) | New Construction Electricity EUI (KBTU/ft²) | New Construction Gas EUI (KBTU/ft²) | New Construction Total EUI (KBTU/ft²) | National Average | Acceptable Range (25% Higher) | Acceptable Range (25% Lower) | National Average Acceptable EUI Range | Prototype | CZ | Total Floorspace (Thousand of ft²) | CEUS 2023 Electricity EUI (kBtu/ft²) | CEUS 2023 Gas EUI (kBtu/ft²) | CEUS 2023 Total EUI (kBtu/ft²) | Acceptable Range (25% Higher) | Acceptable Range (25% Lower) | CEUS 2022 Acceptable EUI Range
Relocatable School | 1 | [6 empty] | 51.3 | 64.125 | 38.475 | 25.65 | Relocatable School | 1 | 7618.5337 | 32.3492 | 12.8481 | 45.1973 | 56.4966 | 33.898 | 22.5987
| 2 | [6 empty] | 51.3 | 64.125 | 38.475 | 25.65 |  | 2 | 11477.6706 | 15.4216 | 12.914 | 28.3356 | 35.4195 | 21.2517 | 14.1678
| 3 | [6 empty] | 51.3 | 64.125 | 38.475 | 25.65 |  | 3 | 46411.8605 | 20.4796 | 12.7992 | 33.2788 | 41.5986 | 24.9591 | 16.6394
| 4 | [6 empty] | 51.3 | 64.125 | 38.475 | 25.65 |  | 4 | 23032.968 | 21.4937 | 13.0198 | 34.5135 | 43.1419 | 25.8851 | 17.2567
| 5 | [6 empty] | 51.3 | 64.125 | 38.475 | 25.65 |  | 5 | 5978.4428 | 11.9981 | 11.5852 | 23.5833 | 29.4791 | 17.6874 | 11.7916
| 6 | [6 empty] | 51.3 | 64.125 | 38.475 | 25.65 |  | 6 | 57755.9589 | 22.6073 | 9.9467 | 32.5541 | 40.6926 | 24.4156 | 16.277
| 7 | [6 empty] | 51.3 | 64.125 | 38.475 | 25.65 |  | 7 | 35149.9926 | 24.8484 | 6.97 | 31.8184 | 39.773 | 23.8638 | 15.9092
| 8 | [6 empty] | 51.3 | 64.125 | 38.475 | 25.65 |  | 8 | 92353.4113 | 22.9353 | 8.8422 | 31.7775 | 39.7219 | 23.8331 | 15.8888
| 9 | [6 empty] | 51.3 | 64.125 | 38.475 | 25.65 |  | 9 | 141795.4506 | 26.7973 | 10.0891 | 36.8864 | 46.108 | 27.6648 | 18.4432
| 10 | [6 empty] | 51.3 | 64.125 | 38.475 | 25.65 |  | 10 | 92589.8669 | 22.4904 | 10.109 | 32.5994 | 40.7492 | 24.4495 | 16.2997
| 11 | [6 empty] | 51.3 | 64.125 | 38.475 | 25.65 |  | 11 | 33810.4884 | 26.9287 | 8.7604 | 35.6891 | 44.6114 | 26.7668 | 17.8445
| 12 | [6 empty] | 51.3 | 64.125 | 38.475 | 25.65 |  | 12 | 108342.4341 | 31.7996 | 12.2303 | 44.0299 | 55.0374 | 33.0224 | 22.0149
| 13 | [6 empty] | 51.3 | 64.125 | 38.475 | 25.65 |  | 13 | 46676.8078 | 32.656 | 15.4735 | 48.1296 | 60.162 | 36.0972 | 24.0648
| 14 | [6 empty] | 51.3 | 64.125 | 38.475 | 25.65 |  | 14 | 22787.7389 | 21.8072 | 11.4332 | 33.2403 | 41.5504 | 24.9303 | 16.6202
| 15 | [6 empty] | 51.3 | 64.125 | 38.475 | 25.65 |  | 15 | 54746.0029 | 21.9543 | 10.4391 | 32.3934 | 40.4918 | 24.2951 | 16.1967
| 16 | [6 empty] | 51.3 | 64.125 | 38.475 | 25.65 |  | 16 | 85267.8904 | 27.0269 | 11.6529 | 38.6798 | 48.3498 | 29.0099 | 19.3399
Ref: CEUS 2022 Report
And by applying FZ-CZ multipliers for converting FZ data to CZ data

## Weights
% of Floor Area per CZ and Vintage Bin - Schools | [7 empty] | % of floor area per CZ and vintage bin - School
Prototype | CZ | Vintage Bin | [5 empty] | Prototype | Vintage Bin | CZ
|  | Pre-1978 | 1978-1997 | 1998-2007 | 2008-2018 | Not available |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
School | 1 | 56.15% | 31.7% | 8.792% | 3.362% |  | 100% | School | Pre-1978 | 0.8977% | 2.109% | 7.223% | 3.762% | 0.6802% | 8.454% | 2.215% | 13.88% | 21.12% | 6.648% | 3.875% | 11.53% | 3.642% | 2.654% | 2.435% | 8.861%
| 2 | 87.57% | 7.179% | 3.84% | 1.407% |  | 100% |  | 1978-1997 | 1.19% | 0.406% | 5.368% | 2.321% | 1.254% | 4.186% | 4.469% | 6.134% | 12.49% | 9.593% | 5.841% | 18.78% | 9.188% | 2.138% | 5.702% | 10.94%
| 3 | 74.16% | 23.47% | 1.644% | 0.7184% |  | 100% |  | 1998-2007 | 0.4957% | 0.3262% | 0.5645% | 0.1754% | 0.1078% | 4.659% | 5.116% | 7.54% | 9.166% | 22.74% | 2.095% | 8.744% | 5.457% | 2.55% | 21.38% | 8.884%
| 4 | 77.84% | 20.45% | 1.029% | 0.6824% |  | 100% |  | 2008-2018 | 0.5003% | 0.3153% | 0.6512% | 0.307% | 0.091% | 5.236% | 16.82% | 6.944% | 6.633% | 20.93% | 1.281% | 6.701% | 6.453% | 4.605% | 5.248% | 17.28%
| 5 | 54.22% | 42.57% | 2.437% | 0.7789% |  | 100%
| 6 | 69.75% | 14.71% | 10.9% | 4.641% |  | 100% |  | Total | 0.88% | 1.326% | 5.361% | 2.66% | 0.6905% | 6.671% | 4.06% | 10.67% | 16.38% | 10.69% | 3.905% | 12.51% | 5.391% | 2.632% | 6.323% | 9.849%
| 7 | 30.03% | 25.8% | 19.67% | 24.5% |  | 100%
| 8 | 71.64% | 13.48% | 11.03% | 3.85% |  | 100%
| 9 | 70.99% | 17.88% | 8.734% | 2.395% |  | 100%
| 10 | 34.21% | 21.03% | 33.18% | 11.57% |  | 100%
| 11 | 54.62% | 35.07% | 8.374% | 1.94% |  | 100%
| 12 | 50.74% | 35.19% | 10.91% | 3.167% |  | 100%
| 13 | 37.18% | 39.95% | 15.8% | 7.078% |  | 100%
| 14 | 55.49% | 19.04% | 15.12% | 10.35% |  | 100%
| 15 | 21.19% | 21.14% | 52.76% | 4.908% |  | 100%
| 16 | 49.52% | 26.03% | 14.08% | 10.38% |  | 100%
| Statewide | 55.04% | 23.44% | 15.61% | 5.913% |  | 100%
Ref: CEUS 2022 dataset: School group
Background Data [To be deleted prior to publication]

## PV (hidden)
PV - SchoolRelocatable
TBD

## EV Charger (hidden)
EV Charger - SchoolRelocatable
TBD
Background Data [To be deleted prior to publication]

## Data (hidden)
Space Function
Aging Eye/Low-vision (Corridor Area)
Aging Eye/Low-vision (Dining)
Aging Eye/Low-vision (Lobby, Main Entry)
Aging Eye/Low-vision (Lounge/Waiting Area)
Aging Eye/Low-vision (Multipurpose Room)
Aging Eye/Low-vision (Religious Worship Area)
Aging Eye/Low-vision (Restroom)
Aging Eye/Low-vision (Stairwell)
Audience Seating Area
Auditorium Area
Auto Repair / Maintenance Area
Barber, Beauty Salon, Spa Area
Civic Meeting Place Area
Classroom, Lecture, Training, Vocational Areas
Concourse and Atria Area
Convention, Conference, Multipurpose and Meeting Area
Copy Room
Corridor Area
Dining Area (Bar/Lounge and Fine Dining)
Dining Area (Cafeteria/Fast Food)
Dining Area (Family and Leisure)
Electrical, Mechanical, Telephone Rooms
Exercise/Fitness Center and Gymnasium Areas
Financial Transaction Area
Healthcare Facility and Hospitals (Exam/Treatment Room)
Healthcare Facility and Hospitals (Imaging Room)
Healthcare Facility and Hospitals (Medical Supply Room)
Healthcare Facility and Hospitals (Nursery)
Healthcare Facility and Hospitals (Nurse's Station)
Healthcare Facility and Hospitals (Operating Room)
Healthcare Facility and Hospitals (Patient Room)
Healthcare Facility and Hospitals (Physical Therapy Room)
Healthcare Facility and Hospitals (Recovery Room)
Hotel Function Area
Kitchen/Food Preparation Area
Kitchenette or Residential Kitchen
Laboratory, Scientific
Laundry Area
Library (Reading Area)
Library (Stacks Area)
Lobby, Main Entry
Locker Room
Lounge, Breakroom, or Waiting Area
Manufacturing, Commercial & Industrial Work Area (Low Bay)
Manufacturing, Commercial & Industrial Work Area (High Bay)
Manufacturing, Commercial & Industrial Work Area (Precision)
Museum Area (Exhibition/Display)
Museum Area (Restoration Room)
Office Area (>250 square feet)
Office Area (<250 square feet)
Parking Garage Area (Parking Zone and Ramps)
Parking Garage Area (Daylight Adaptation Zones) (Note 2)
Pharmacy Area
Retail Sales Area (Grocery Sales)
Retail Sales Area (Retail Merchandise Sales)
Retail Sales Area (Fitting Room)
Religious Worship Area
Restrooms
Stairwell
Storage, Commercial/Industrial (Warehouse)
Storage, Commercial/Industrial (Refrigerated)
Storage, Commercial/Industrial (Shipping & Handling)
Storage (General)
Sports Arena - Playing Area (> 5,000 Spectators)
Sports Arena - Playing Area (2,000 - 5,000 Spectators)
Sports Arena - Playing Area (< 2,000 Spectators)
Sports Arena - Playing Area (Recreational)
Theater Area (Motion Picture)
Theater Area (Performance)
Transportation Function (Baggage Area)
Transportation Function (Ticketing Area)
Videoconferencing Studio
High-Rise Residential Living Spaces
Hotel/Motel Guest Room
All other
Attic
Reception Area
Elevator
Unoccupied-Exclude from Gross Floor Area