## Notes
Data Sources
Dataset | Dodge 2023
CEUS 2022
CBECS 2018
ComStock 2023
Prototype | CEC prototype (CBECC 2022.3.1) | https://bees.noresco.com/software2022.html
| PNNL prototype (90.1-2022) | https://www.energycodes.gov/prototype-building-models#Commercial
| DEER prototype (June 2023) | https://github.com/sound-data/DEER-Prototypes-EnergyPlus
Codes | Title 24, part 6, referred to as T24 (1986, 1992, 2001, 2007, 2013, 2016, 2019, 2022, 2025)
ASHRAE 90.1 (2022)
| CFR Title 10 (2009) | https://www.govinfo.gov/content/pkg/FR-2009-03-23/pdf/FR-2009-03-23.pdf
| CFR Title 10 ( 2013) | https://www.govinfo.gov/content/pkg/CFR-2013-title10-vol3/pdf/CFR-2013-title10-vol3-part431.pdf
| CFR Title 10 ( 2024) | https://www.govinfo.gov/content/pkg/CFR-2024-title10-vol3/pdf/CFR-2024-title10-vol3-part431-subpartF.pdf
Others | ACM (2013, 2019, 2022, 2025)
| Title 24, 2022 - Appendix 5.4A and Appendix 5.4B | https://www.energy.ca.gov/publications/2022/2022-nonresidential-and-multifamily-alternative-calculation-method-reference
| 2022 Reduced infiltration CASE report | https://title24stakeholders.com/wp-content/uploads/2020/10/2022-T24-Final-CASE-Report_Reduce-Infiltration.pdf
| 2019 Outdoor Lighting CASE Report | https://title24stakeholders.com/wp-content/uploads/2016/10/T24-2019-CASE-Study-Results-Report-Outdoor-Sources_Final_with-Attachments.pdf
| PNNL 20405, 2011 | https://www.pnnl.gov/main/publications/external/technical_reports/PNNL-20405.pdf
| Air leakage Memo, NORESCO, 2025 | https://2050partners.sharepoint.com/:w:/r/sites/CalBEMCollaborativeEfforts/_layouts/15/Doc.aspx?sourcedoc=%7B3BEF8F74-7FAC-44F2-A70C-D76617660066%7D&file=Infiltration_rate_report_14May2025-Short-Version.docx&action=default&mobileredirect=true
| Proposed Updates to Equipment Power Densities and Building Schedules for the 2028 Energy Code, referred to as "Plug load and schedules project with CEC, 2025" (Docket Number =25-BSTD-03 & TN=265693) | https://efiling.energy.ca.gov/GetDocument.aspx?tn=265693&DocumentContentId=102545
| PNNL 17056, 2007: Technical Support Document: The Development of the Advanced Energy Design Guide for Small Warehouse and Self-Storage Buildings | https://www.pnnl.gov/main/publications/external/technical_reports/PNNL-17056.pdf
| NEEA, CBSA-4-2019, "Commercial Building Stock Assessment 4 (2019) Final Report ", by CADMUS, Aaron James in 2020. | https://neea.org/wp-content/uploads/2025/03/CBSA-4-2019-Final-Report.pdf
Water Heater | ENERGY STAR certified commercial water heaters (gas storage input ≥76 kBtu/h; ES tank sizes) | ENERGY STAR product finder — gas
| ENERGY STAR commercial WH dataset (download) | ENERGY STAR dataset xmq6-bm79
| ENERGY STAR commercial WH eligibility (gas storage >75 kBtu/h) | ENERGY STAR key product criteria
| Grainger gas tank water heaters (sizes below ES commercial, e.g. 30–75 kBtu/h) | Grainger — gas tank WH
| Grainger electric tank water heaters (kW ladder, tank gallons) | Grainger — electric tank WH
| ES commercial electric = heat pumps only; not used for resistance tank list | ENERGY STAR — electric (HPWH)
Notes
Warehouse | A mixed use distribution warehouse with conditioned fine storage for temperature sensitive goods and a bulk storage for general inventory that only needs freeze protection.
Construction rate based on Dodge 2023
Warehouse (STC:3)
Year | Total floor area (k ft2) | Count
1967 | 5361.9 | 152
1968 | 8271 | 452
1969 | 13593.6 | 655
1970 | 14323.7 | 601
1971 | 13719.8 | 592
1972 | 16513.9 | 687
1973 | 27619.6 | 920
1974 | 26732 | 804
1975 | 13654.6 | 710
1976 | 19608.4 | 853
1977 | 29745.3 | 1055
1978 | 40044.4 | 1359
1979 | 40268.5 | 1053
1980 | 26862.2 | 851
1981 | 21498.2 | 812
1982 | 14017.9 | 606
1983 | 19364.4 | 880
1984 | 31271.7 | 1271
1985 | 44833.1 | 1461
1986 | 46291.2 | 1382
1987 | 46613.6 | 1265
1988 | 50555.2 | 1237
1989 | 48019.1 | 1233
1990 | 37809.8 | 1111
1991 | 20082.4 | 768
1992 | 11010.9 | 426
1993 | 7511.2 | 470
1994 | 11961.3 | 465
1995 | 13270.9 | 521
1996 | 20653.8 | 570
1997 | 27588.9 | 407
1998 | 41631.3 | 476
1999 | 48039.6 | 533
2000 | 52612.2 | 500
2001 | 40337.2 | 432
2002 | 33147.2 | 399
2003 | 30982.8 | 398
2004 | 29560.8 | 417
2005 | 27484.1 | 347
2006 | 25891.9 | 299
2007 | 25769.2 | 248
2008 | 20632.6 | 236
2009 | 5608 | 122
2010 | 2602.9 | 47
2011 | 3617.9 | 36
2012 | 8233.2 | 63
2013 | 17625.9 | 46
2014 | 13973.9 | 72
2015 | 29759.5 | 104
2016 | 25538.8 | 152
2017 | 27796.9 | 105
2018 | 32684.7 | 117
2019 | 30948.5 | 141
2020 | 34022.9 | 162
2021 | 53815 | 225
2022 | 41442.1 | 218
2023 | 10975.7 | 44

## Prototype
NORESCO, Updated September 2026
Warehouse
Characteristic | Value | Data Sources
Building Type | Warehouse
Building Category | Nonresidential
Version | v2-0
Vintages | 4 Vintages: Pre-1978 , 1978-1997 ,1998-2007 , 2008-2018 New Construction (2019+) | Based on the vintage bin analysis. A summary of the findings is presented in the following paper, with a link provided in the Notes tab: Yousefi, F., Athalye, R. (2025). “Determining Vintage Bins for Prototype Development: An Analysis of California Commercial Buildings.” ASHRAE Annual Conference.
Shape |  | Same as CBECC 2022
Total Floor Area (ft²) | 52,045 (330 ft * 150 ft plus 2,550 ft² floor , see Zones tab) The space above the office zone (lower-right zone, 2,550 ft²) is designated as storage and is part of the Fine Storage zone. | Same as CBECC 2022 (supported by Dodge 2023)
Aspect Ratio | 2.2 | Same as CBECC 2022
Number of Floors | 1
Roof type | Flat
WWR | 0.71% | Same as CBECC 2022
Shading Geometry | No shades
Floor to floor height (ft) | 28 | Same as CBECC 2022
Floor to ceiling height (ft) | 14 (office) | Same as CBECC 2022
Glazing sill height (ft) | 3 (Top of the window is 8 ft with 5 ft high glass) | Same as CBECC 2022
Existing public prototypes
| PNNL | CEC | CPUC Storage conditioned | CPUC Refrigerated Warehouse (not under warehouse)
Geometry
Roof area (ft²) | 49495.17 | 49495.29 | 499990.41 | 499990.41
Height (ft) | 28 | 28 | 48 | 48
People | 200 ft²/person Office | 0.005 person/ft² Office | 0.001 person/ft² North storage | 0.002
| 30 people Fine storage | 0.001 person/ft² Fine storage | 0.001 person/ft² Soth storage
| 69 people Bulk storage | 0.001 person/ft² Bulk storage
Lights (W/ft²) | 0.57 Office | 0.6 Office | 0.4 North storage
| 0.62 Fine storage | 0.4 Fine storage | 0.4 South storage
| 0.30 Bulk storage | 0.4 Bulk storage
Ext lights (W) | 119 Office | - | -
2,955 Fine storage
694 Bulk storage
Electric Equipment | 1,912 W Office | 1.5 W/ft² Office | 0.2 W/ft² North storage
|  | 0.2 W/ft² Fine storage | 0.2 W/ft² South storage
| 8,200 Bulk W storage | 0.2 W/ft² Bulk storage
Heating Sizing Factor | H&C: 1.2 | H&C:1 | H: 2.5 , C: 2.3
HVAC | Office: CAV no reheat, DX cooling coil: multi speed, Gas heating coil | Office (sys7or3b): VAV+DX cooling coil+DX heating coil +Electric Heating coil | MZ VAV Reheat + 1 Water cooling coil +1 Water heating coil+ 2 water heating coil for Reheat at terminal units, serving 2 zones
| Fine storage; CAV no reheat, DX cooling coil: multi speed, Gas heating coil | Fine storage (sys7or3a):VAV+DX cooling coil: Gas Heating coil | - Boiler
| Bulk storage: CAV+ Unit heater (Gas heating coil) | Bulk storage (sys9): CAV+Gas Heating coil | -Chiller
+ (DX coil:multi speed high temperature Radiant (Always Off))
Thermostat setpoint (F) | Office: 70H , 75C (setback: 60H , 85C) | Office: 70H , 75C (setback: 60H , 85C) | North: 70H, 75C (setback: 60H , 85C)
| Fine Storage: 60H, 80C | Fine Storage:70H , 75C (setback: 60H , 85C) | North: 70H, 75C (setback: 60H , 85C)
| Bulk storage: 50H | Bulk storage: 70H (setback: 60H)
ZoneVentilation:design flow rate | 80,000 cfm exhaust rate Bulk storage | - | -
2,000 cfm natural ventilation rate Bulk storage (=0.06*34500 Bulk area)
Design specification: Outdoor Air (Cfm/ft²) | 0.085 Office | 0.15 Office | 0.15 North storage
| 0.060 Fine storage | 0.15 Fine storage | 0.15 South storage
| 0.060 Bulk storage (for sizing only) | 0.15 Bulk storage
Airloop:HVAC | 2 units for Office and Fine storage | 3 units for 3 zones | 1 unit serving 2 zones

## Zones
Proposed Layout - Warehouse
Building | Space/Thermal Zone | Space Type [Primarily from: T24, 2022 Appendix 5.4A] - See Notes column | HVAC Zone | Schedule Category | Conditioned (Y/N) | Area Fraction | Area (ft²) | Volume (ft³) | Multipliers | Number of People | People (Persons/1,000 ft²) [T24, 2025,Table 120.1-A] | Notes
Warehouse | Office | Office Area (>250 square feet) | AHU_1 | Office | Y | 4.899% | 2549.75 | 35696.5 | 1 | 12.7487 | 5
Warehouse | FineStorage | Storage, Commercial/Industrial (Warehouse) | AHU_2 | FineStorage | Y | 28.82% | 14998.55 | 384262.9 | 1 | 14.9985 | 1
Warehouse | BulkStorage | Storage, Commercial/Industrial (Warehouse) | AHU_3 | BulkStorage | Y | 66.28% | 34496.73 | 965908.44 | 1 | 34.4967 | 1
Toal (1 Building) | Total (3 Space) | Total (2 space type) | Total (3 HVAC Zones) |  | Total (3 Conditioned zones) | 100% | 52045.03 | 1385867.84 |  | 62.244
N
Office
Fine Storage
Bulk Storage

## Envelope
Envelope - Warehouse
Element | Prototype | Assembly Type | Construction | Thermal properties | Vintage | Selected T24 | Note | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
External Wall | Warehouse | ExtWall_MetalBuilding_NonRes | Metal building: Metal surface + Continuous Insulation + Metal panel | U-factor IP | Pre 1978 | N/A | Using 1) DOE pre 1980 warehouse prototype U value of 0.301, and 2) a 5.1% cumulative wall renovation rate through 2028, based on the average annual rate from CBECS 2003 and 2012 projected over 48 years. | 0.29141 | 0.28876 | 0.29141 | 0.28876 | 0.28876 | 0.29141 | 0.29141 | 0.28876 | 0.28876 | 0.28876 | 0.28876 | 0.28876 | 0.28876 | 0.28876 | 0.28856 | 0.28876
[5 empty] | 1978-1997 | 1986 | . Minimum of the previous vintage and U values calculated from the 1986 code based on HDD and Degree North Latitude | 0.29141 | 0.28876 | 0.29141 | 0.28876 | 0.28876 | 0.29141 | 0.29141 | 0.28876 | 0.28876 | 0.28876 | 0.28876 | 0.28876 | 0.28876 | 0.28876 | 0.28856 | 0.28876
[5 empty] | 1998-2007 | 2001 | Table 1-H (Metal frame) | 0.182 | 0.182 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.113 | 0.061 | 0.113 | 0.061 | 0.061 | 0.113 | 0.113 | 0.061 | 0.061 | 0.061 | 0.061 | 0.061 | 0.061 | 0.061 | 0.057 | 0.061
[5 empty] | Existing |  | Weighted average of all 4 vintages | 0.21533 | 0.18737 | 0.25967 | 0.26208 | 0.22257 | 0.27016 | 0.25824 | 0.26639 | 0.26787 | 0.18225 | 0.21503 | 0.22085 | 0.2239 | 0.21265 | 0.16507 | 0.19564
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.098 | 0.053 | 0.098 | 0.053 | 0.053 | 0.098 | 0.098 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053
Roof | Warehouse | FlatRoof_WoodFramedAndOther_NonRes | Metal deck roof: Roof Membrane + Continuous Insulation + Metal Decking | U-factor IP | Pre 1978 | N/A | Considering 30 years for roof/ insulation replacement. | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 1978-1997 | 1992 |  | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 1998-2007 | 2001 | Table 1-H | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065
[5 empty] | Existing |  | Weighted average of all 4 vintages | 0.058997 | 0.059905 | 0.057335 | 0.057145 | 0.057472 | 0.077479 | 0.077548 | 0.07745 | 0.077563 | 0.064285 | 0.058707 | 0.058487 | 0.058226 | 0.05799 | 0.059543 | 0.058297
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038
Windows | Warehouse | FixedWindow_NonRes | Single Pane (CBECS 2018, ~ 50 % of warehouse that were built before 2000 are single pane) | U-factor IP | Pre 1978 | N/A | ASHRAE Handbook of Fundamentals for single pane (Table 4- CH15) & T24 2013 for double pane (50%-50%) | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74
[5 empty] | 1978-1997 | N/A |  | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74
|  |  | Double pane |  | 1998-2007 | 2001 | Table 1-H | 0.49 | 0.49 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36
[5 empty] | Existing |  | Weighted average of all 4 vintages | 0.57307 | 0.55826 | 0.74065 | 0.74894 | 0.75459 | 0.73441 | 0.74523 | 0.73288 | 0.73653 | 0.52548 | 0.60008 | 0.60949 | 0.61162 | 0.58075 | 0.50218 | 0.54682
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.34 | 0.36 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.36
|  |  | Single Pane (CBECS 2018, ~ 50 % of warehouse that were built before 2000 are single pane) | SHGC | Pre 1978 | N/A | ASHRAE Handbook of Fundamentals for single pane (Table 10-Ch15) & T24 2013 for double pane (50%-50%) | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52
[5 empty] | 1978-1997 | N/A |  | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52
|  |  | Double pane |  | 1998-2007 | 2001 | Table 1-H (Non north 0-10%) | 0.49 | 0.47 | 0.61 | 0.61 | 0.61 | 0.61 | 0.61 | 0.61 | 0.61 | 0.47 | 0.47 | 0.47 | 0.47 | 0.46 | 0.46 | 0.49
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
[5 empty] | Existing |  | Weighted average of all 4 vintages | 0.44395 | 0.4132 | 0.53 | 0.53546 | 0.55166 | 0.52158 | 0.53432 | 0.52008 | 0.52288 | 0.43296 | 0.45061 | 0.45783 | 0.46458 | 0.45966 | 0.40608 | 0.46043
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.22 | 0.25 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.25
Skylight | Warehouse | Skylight | Translucent | U-factor IP | Pre 1978 | 1992 | Table 1-I | 0.85 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
[5 empty] | 1978-1997 | 1992 |  | 0.85 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
|  |  | Plastic curb mounted |  | 1998-2007 | 2001 | Table 1-H | 0.87 | 1.1 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 0.87
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88
[5 empty] | Existing |  | Weighted average of all 4 vintages | 0.86325 | 1.1171 | 1.2896 | 1.2999 | 1.2793 | 1.2914 | 1.2924 | 1.2905 | 1.2942 | 1.1046 | 0.91522 | 0.91545 | 0.92473 | 0.96595 | 0.97655 | 0.86539
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88
|  |  | Translucent | SHGC | Pre 1978 | 1992 | Table 1-I | 0.81 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81
[5 empty] | 1978-1997 | 1992 |  | 0.81 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81
|  |  | Plastic curb mounted |  | 1998-2007 | 2001 | Table 1-H (For SSR 2.1-5%) | 0.58 | 0.62 | 0.65 | 0.65 | 0.65 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.58 | 0.58 | 0.58
[5 empty] | 2008-2018 | 2013 | There is no requirement in the code (considered same as 2001) | 0.58 | 0.62 | 0.65 | 0.65 | 0.65 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.58 | 0.58 | 0.58
[5 empty] | Existing |  | Weighted average of all 4 vintages | 0.68628 | 0.73085 | 0.80145 | 0.80871 | 0.73657 | 0.81732 | 0.78845 | 0.8192 | 0.82007 | 0.68246 | 0.72475 | 0.72918 | 0.72758 | 0.67829 | 0.62923 | 0.65166
[5 empty] | 2019+ | 2025 | There is no requirement in the code (considered same as 2001) | 0.58 | 0.62 | 0.65 | 0.65 | 0.65 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.58 | 0.58 | 0.58
Infiltration
|  |  | Building | Zones | Vintage | I_75 (cfm/ft2) 6-sided Infiltration rate @ 75 pa | Source | CZ1: I-design (cfm/ft²) (4-sided Infiltration rate at normal pressure) (Design flow rate approach and Flow/Exterior Wall Area calculation method)
|  | Infiltration | Warehouse |  | Pre 1978 | 1.1 | 2022 CASE report (Table 38) | CZ1: 0.5769
[5 empty] | 1978-1997 | 1.1 | 2022 CASE report (Table 38) | CZ1: 0.5769
[5 empty] | 1998-2007 | 1.1 | 2022 CASE report (Table 38) | CZ1: 0.5769
[5 empty] | 2008-2018 | 1 | 2022 CASE report (Table 38) & T24, 2008-2016 (Table 140.3-B) | CZ1: 0.5279
[5 empty] | Existing |  | Same as Pre 2008 because of their higher weights | CZ1: 0.5769
[5 empty] | 2019+ | 0.6 | 2022 CASE report (Table 38) & T24, 2025 (Table 140.3-B) | CZ1: 0.3147
Source: T24 air barrier requirements (all editions) , the standardized infiltration rate reported in the 2022 CASE report, and Dodge 2023 data
Infiltration_rate_report_14May2025-Short-Version.docx
Door infiltration
|  |  |  | Zone | Infiltration Rate | Source | Note
|  |  |  | Office | 374 cfm | PPNL, ASHRAE 90.1- 2022 Warehouse prototype | Office door Infiltration with maximum infiltration at 8 am, 13 pm, 18 pm.
|  |  |  | BulkStorage | 616 cfm (32*7+0.5+783*0.5) | PNNL 17056, 2007 | Loading dock doors infiltration: Assumptions: 7 doors each 8 ft * 10 ft 783 cfm per door when dock doors open 32 cfm per door ( or 0.4 cfm/ sf of door area ) when dock doors close Loading time from 8 am -12 pm One truck per hour with a 30 minutes of unloading time | CZ1: Technical Support Document: The Development of the Advanced Energy Design Guide for Small Warehouse and Self-Storage Buildings
0.36364
Pre-1978 exterior wall U value calculation:
External Wall | Warehouse | ExtWall_MetalBuilding_NonRes | Metal building: Metal surface + Continuous Insulation + Metal panel | U-value IP | Pre 1978 | N/A | ASHRAE 90.1, 2022 Table A3.2.3, R-0 | 1.18 | 1.18 | 1.18 | 1.18 | 1.18 | 1.18 | 1.18 | 1.18 | 1.18 | 1.18 | 1.18 | 1.18 | 1.18 | 1.18 | 1.18 | 1.18
[7 empty] | T24 2008 (U value): Metal building | 0.113 | 0.061 | 0.113 | 0.061 | 0.061 | 0.113 | 0.113 | 0.061 | 0.061 | 0.061 | 0.061 | 0.061 | 0.061 | 0.061 | 0.057 | 0.061
[7 empty] | DOE pre 1980 warehouse prototype LA (U value) (metal building with ~R2 insulation) | 0.301 | 0.301 | 0.301 | 0.301 | 0.301 | 0.301 | 0.301 | 0.301 | 0.301 | 0.301 | 0.301 | 0.301 | 0.301 | 0.301 | 0.301 | 0.301
[7 empty] | Renovation rate since 1980 (yearly renovation rate was calculated from CBECS 2003 and 2012 and then projected over 48 years) | CZ1: 5.1%
Background Data [To be deleted prior to publication]
T24, 2025
140.3 (a) 6 A. | Skylights shall, have an area no greater than 5 percent of the gross exterior roof area Skylight Roof Ratio (SRR).
140.3 (c) 4. | The total skylight area is at least 3% of the total floor area in the space within a horizontal distance of 0.7 times the average ceiling height from the edge of rough opening of skylights; or the product of the total skylight area and the average skylight visible transmittance is no less than 1.5 percent of the total floor area in the space within a horizontal distance of 0.7 times the average ceiling height from the edge of rough opening of skylights.
T24, 1986
External Wall | Warehouse | Metal Building | Stucco + Continuous Insulation + Metal Framing + Gypsum 5/8in | U factor | 1978-1997 | 1986 | low-rise office: Package A/ Heat Capacity was considered 10.0-14.99 (Btu/F/ft²) | 0.15083 | 0.15748 | 0.15748 | 0.14368 | 0.14368 | 0.21645 | 0.21645 | 0.21645 | 0.21645 | 0.21645 | 0.18622 | 0.18622 | 0.18622 | 0.15873 | 0.15873 | 0.15083 | These values are lower than the next code cycle.
For NEW NONRESIDENTIAL BUILDINGS OF OCCUPANCIES A, 5, E AND H:
HDD for each CZ in CA | <3500
weight of wall | <10 lb/ft²
TD eq (<10 lb/ft²) | 44 |  | U wall base on HDD | 0.39
MCF (<10 lb/ft²) | 1 |  | U wall base on CDD | 0.70455
Aow (ft²)= | 26880
Awall (ft²) | 26880 |  | U wall (Btu/hr-ft²-F) | 0.39
Awindows(ft²) ~ | 0
Min OTTV | 31 | Frame Fig 2-53E
Min Uow (HDD< 3500) | 0.39 | Frame Fig 2-53B
Position of the loading dock doors ( Right side of the image)

## HVAC System
HVAC system - Warehouse
Vintage | Space/Thermal Zone | Heating | Cooling | Air Distribution | Other Systems | Source
Existing | Office | Furnace (Gas) | DX (RTU) | CAV |  | CEUS 2022 + Engineering Judgement
| Fine Storage | Furnace (Gas) | DX (RTU) | CAV
| Bulk Storage | Unit Heater (Gas) (lower heating setpoint ) | None | CAV | Exhaust fan
New Construction | Office | HP | DX (RTU) | CAV |  | T24, 2025
| Fine Storage | HP | DX (RTU) | CAV
| Bulk Storage | Unit Heater (Gas) (lower heating setpoint) | None | CAV | Exhaust fan
Efficiency of HVAC system (Efficiency is capacity-dependent. The following table provides a general estimate of system efficiency based on preliminary simulations in one climate zone, or assuming cooling load based on rule of thumb)
Vintage | Upgrade/Installed year | Gas Furnace | DX Cooling | HP | Unit Heater | Source
Pre 1978 | 2008 | Thermal Efficiency of 80% | EER=9.0 when system <65 kBtu/h EER=9.7 when system >65 & <135 kBtu/h EER=9.5 when system >135 & <240 kBtu/h |  | 80% gas efficiency, no cooling | T24, 2008 for systems >65 kBtu/hr CFR 2009 for systems <65 kBtu/hr
1978-1997
1998-2007
2008-2018 | 2013 | Thermal Efficiency of 80% | EER=9.0 when system <65 kBtu/h EER=11.2 when system >65 & <135 kBtu/h EER=11 when system >135 & <240 kBtu/h |  | 80% gas efficiency, no cooling | 10 CFR 2013 (431.97, Table 1) / T24, 2025, ACM 2013
New Construction | 2025 |  |  | SEER2=13.4 / Cop=3.3, EER=11 when system <65 kBtu/h EER=11 when system >65 & <135 kBtu/h EER=10.6 when system >135 & <240 kBtu/h | 80% gas efficiency, no cooling | 10 CFR 2024 / T24, 2025, ACM 2025
Fan Power
Vintage | Approach | System | Total Static Pressure (TSP) (in w.c.) | Fan Efficiency [ACM 2025] | Motor Efficiency | Fan Power Index (W/cfm) | Data Source
Existing | PNNL 90.1-2011, TSP | CAV Office | 2.5 (system <7,437 cfm) | 0.65 | ASHRAE 90.1, 2004, Table 10.8 * |  | Fan power formula: PNNL 20405, 2010, section 5.2.2.5 TSP and fan efficiency: PNNL 20405, 2010, Table 5.11, 90.1-04ac values Motor efficiency: ASHRAE 90.1, 2004, Table 10.8
|  | CAV Fine Storage | 2.5 (system <7,437 cfm) 4.09 (system >7,437 cfm | 0.65
|  | Unit heater in Bulk Storage | 0.2 | 0.65
Brake horsepower (bhp) = (Supply cfm × TSP in w.c.) / (6356 × fan efficiency)
Fan power (w/cfm) = (bhp × 746) / ( supply cfm × motor efficiency )
New Construction | ACM 2025 | HP Office (system <5,000 cfm) | TSP = fan power × motor efficiency × fan efficiency × 6356 / 746 | 0.65 | 2025 ACM Table 12 ** | 0.744 (system <5,000 cfm in office space | Fan power index: [ACM 2025, Table 13] Motor efficiency: [ACM 2025, Table 12]
|  | HP Fine Storage, >10,000 cfm | TSP = fan power × motor efficiency × fan efficiency × 6356 / 746 |  |  | 0.676
|  | Unit heater in Bulk Storage | TSP = fan power × motor efficiency × fan efficiency × 6356 / 745 |  |  | 0.62 (5,000-10,000 cfm) 0.605 (>10,000 cfm)
* According to PNNL 20405 section 5.2.2.5, the full-load efficiency of the motor serving the fan is taken from ASHRAE 90.1, 2004, Table 10.8, based on motor nameplate and assuming enclosed motors operating at 1,800 rotations per minute (rpm) Motor nameplate size (bhp) = brake horsepower (bhp) × 1.1 ( using a 10% oversizing factor)
"** The full‑load efficiency of the motor serving the fan is taken from ACM 2025 Table 12 based on the cfm of the fan. Brake horsepower (bhp) = (Supply cfm from sizing run × fan power in W/cfm) / 746. Note: ACM System 6 VAV >10,000 cfm."

## Thermostat
Thermostat Setpoints - Warehouse
Space/Thermal Zone | Setpoint | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16 | Source
Office | Heating Setpoint (F) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | T24 2022 - Appendix 5.4B
| Heating Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
| Cooling Setpoint (F) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
| Cooling Setback (F) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
FineStorage | Heating Setpoint (F) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | T24 2022 - Appendix 5.4B
| Heating Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
| Cooling Setpoint (F) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
| Cooling Setback (F) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
BulkStorage | Heating Setpoint (F)* | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | PNNL ASHRAE 90.1 2022, Warehouse prototype
* Bulk storage is defined as a general inventory space that only needs freeze protection.

## Ventilation
Outdoor Airflow Rate - Warehouse
Space/Thermal Zone | Number of People | Floor Area (ft²) | cfm/person [T24, 2025, Equation 120.1-F and Table 120.1-A] | cfm/ft² [T24, 2025, Equation 120.1-F and Table 120.1-A] | Required Exhaust Rate [T24, 2025, Table 120.1-B – minimum exhaust rates] | Total cfm Driven by People | Total cfm Driven by Area | Total cfm Driven by Exhaust | Total cfm | Notes
Office | 12.7487 | 2549.75 | 15 | 0.15 | - | 191.2312 | 382.4625 | - | 382.4625
FineStorage | 14.9985 | 14998.55 | 15 | 0.15 | - | 224.9783 | 2249.7825 | - | 2249.7825
BulkStorage | 34.4967 | 34496.73 | 15 | 0.15 | - | 517.451 | 5174.5095 | - | 5174.5095 | This amount of OA cfm appear low. May be updated with further research.
Fine storage is defined for normal inventory that doesn't require an extra exhaust rate based on the space functions in T24, Part6, 2025, Table 120.1 B.

## Water Heater
Water Heater - Warehouse
Vintage | WH Type | Efficiency | Number of WH | Tank Volume (gal) | Tank Loss | Source
Existing | Electric resistance WH | 1 | 1 | See table below for CZ-specific values: Climate Zone Water Heater Sizing and Loss Coefficients, Storage Volume column (col G) | See table below: Climate Zone Water Heater Sizing and Loss Coefficients, Standby Loss column (col H) | See table below for sources: Climate Zone Water Heater Sizing and Loss Coefficients
New Construction | Electric resistance WH | 1 | 1 | See table below for CZ-specific values: Climate Zone Water Heater Sizing and Loss Coefficients, Storage Volume column (col G) | See table below: Climate Zone Water Heater Sizing and Loss Coefficients, Standby Loss column (col H) | See table below for sources: Climate Zone Water Heater Sizing and Loss Coefficients
Peak Hot Water Consumption
Space Name | Baseline WH Type [T24, 2022, Appendix 5.4A , sheet: "2022 SpaceFuncData-Input"] | Total Area (ft²) | Number of People | Hot Water Usage Specification (gal/hr per person) [T24, 2022, Appendix 5.4A , sheet: "2022 SpaceFuncData-Input"] | Peak Hot Water Usage (gal/hr) | Peak Hot Water Usage (gal/min) | Note
Office | Electric | 2549.75 | 12.7487 | 0.18 | 2.2948 | 0.038246 | For space types marked with an asterisk (the ‘*’ symbol), the water‑heater type is listed as electric in Appendix 5.4A, sheet ‘2022 SpaceFuncData‑Input.’ However, we modified the value based on CEUS data, which indicates that gas is the primary fuel type.
FineStorage | Electric | 14998.55 | 14.9985 | 0.18 | 2.6997 | 0.044996
BulkStorage | Electric | 34496.73 | 34.4967 | 0.18 | 6.2094 | 0.10349
Total | Gas storage |  |  |  | 0 |  | Minimum peak hot water usage is 75 gal according to ACM 2025
Total | Electric resistance |  |  |  | 75
Design supply temperature (°F) | 135 | CEC-400-2022-009-CMF-REV2-AP5.4B
WH system factor | 0.6 | 2025 ACM §5.9.2 Rated Capacity
Water mass conversion (lb/gal) | 8.2877 | 2025 ACM §5.9.2 Rated Capacity
Reheat multiplier | 0.4 | 2025 ACM §5.9.2 Storage Volume
Climate Zone Water Heater Sizing and Loss Coefficients
Climate Zone | Minimum Monthly Mains Temp (°F) [T24 2022 - Appendix 5.4B] | Heat Output (Btu/hr) [ACM, 2025, 5.9.2: Rated capacity section] | WH Capacity (Btu/hr) [ACM, 2025, 5.9.2: Rated capacity section] | Required Energy Input (Btu/hr) | Storage Volume (gal) | Standby Loss [Title 20, §1605.1 Table F-4; Appendix B: Water Heating Calculation Method] |  | Off/On Cycle Loss Coefficient to Ambient Temp |  | Source/Note
CZ01 | 47.9 | 54139.4002 | 32483.6401 | 34121 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F | Required Energy Input: vendor/available catalog size (Market data table). Storage Volume: standard/available catalog tank size (Market data table).
CZ02 | 50.8 | 52336.8255 | 31402.0953 | 34121 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F
CZ03 | 52.2 | 51466.617 | 30879.9702 | 34121 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F
CZ04 | 52.7 | 51155.8282 | 30693.4969 | 30709 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F
CZ05 | 51.6 | 51839.5635 | 31103.7381 | 34121 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F
CZ06 | 56.8 | 48607.3605 | 29164.4163 | 30709 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F
CZ07 | 58.4 | 47612.8365 | 28567.7019 | 30709 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F
CZ08 | 58.4 | 47612.8365 | 28567.7019 | 30709 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F
CZ09 | 57.6 | 48110.0985 | 28866.0591 | 30709 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F
CZ10 | 57.1 | 48420.8872 | 29052.5323 | 30709 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F
CZ11 | 50.5 | 52523.2987 | 31513.9792 | 34121 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F
CZ12 | 51.4 | 51963.879 | 31178.3274 | 34121 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F
CZ13 | 51.7 | 51777.4057 | 31066.4434 | 34121 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F
CZ14 | 50.1 | 52771.9297 | 31663.1578 | 34121 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F
CZ15 | 63.2 | 44629.2645 | 26777.5587 | 27297 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F
CZ16 | 41.4 | 58179.654 | 34907.7924 | 40946 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F
Market data
Catalog gas input (Btu/h) | Input source | Elec resistance tank (kW) | Elec resistance (Btu/h) | Catalog gas tank (gal) | Tank source | Elec tank (gal) | Elec tank source | Sources and links → Note tab
60000 | Grainger | 1.5 | 5118 | 34 | ENERGY STAR | 6 | Grainger
75100 | Grainger | 2 | 6824 | 35 | Grainger | 10 | Grainger
76000 | Both | 3 | 10236 | 48 | Grainger | 15 | Grainger
80000 | Grainger | 4.5 | 15355 | 50 | Both | 20 | Grainger
99900 | ENERGY STAR | 6 | 20473 | 55 | ENERGY STAR | 28 | Grainger
100000 | Both | 8 | 27297 | 60 | ENERGY STAR | 30 | Grainger
120000 | ENERGY STAR | 9 | 30709 | 65 | Both | 36 | Grainger
125000 | Both | 10 | 34121 | 72 | Grainger | 40 | Grainger
130000 | Both | 12 | 40946 | 75 | Both | 47
145000 | ENERGY STAR | 12.1 | 41287 | 76 | Grainger | 50
150000 | ENERGY STAR | 18 | 61419 | 80 | Both | 65
156000 | Grainger | 24 | 81891 | 82 | Grainger | 80
160000 | Both | 27 | 92128 | 85 | Grainger | 85
175000 | ENERGY STAR | 36 | 122837 | 90 | Both | 105
180000 | Grainger | 54 | 184256 | 91 | Grainger | 120
199000 | ENERGY STAR |  |  | 100 | Both
199900 | Both |  |  | 110 | ENERGY STAR
200000 | ENERGY STAR |  |  | 119 | Both
250000 | Both |  |  | 125 | ENERGY STAR
251000 | ENERGY STAR
270000 | Grainger
285000 | ENERGY STAR
300000 | Both
320000 | ENERGY STAR
360000 | Grainger
398000 | ENERGY STAR
399000 | ENERGY STAR
399900 | Both
499900 | Grainger
550000 | Grainger
715000 | Grainger

## Interior Lights
Interior Lighting - Warehouse
Space Type | New Construction |  |  | Existing |  |  | Notes
| LPD (W/ft²) | Additional LPD for Portable Lighting (W/ft²) | Source | LPD (W/ft²) | Additional LPD for Portable Lighting (W/ft²) | Source
Office Area (>250 square feet) | 0.6 | 0.1 | T24, 2025, Table 140.6-C (Area category method) | 0.75 |  | T24, 2016, Table 140.6-C (Area category method) LPD of "All other spaces" is considered for storage space | It is assumed that 50% of the additional allowance lighting is in use.
Storage, Commercial/Industrial (Warehouse) | 0.4 |  |  | 0.5
Background Data [To be deleted prior to publication]
Existing | Whole Building | All other building | 0.4 |  | T24, 2019, Table 140.6 B
| Area Category | 0 | 0.65 |  | T24, 2019, Table 140.6-C
|  | 0 | 0.4
|  | 0 | 0.4
Existing | Whole Building | All other building | 0.5 |  | T24, 2016, Table 140.6 B
| Area Category | ZONE1 OFFICE | 0.75 |  | T24, 2016, Table 140.6-C
|  | ZONE2 FINE STORAGE | 0.5
|  | ZONE3 BULK STORAGE | 0.5
Existing | Whole Building | All other building | 0.6 |  | T24, 2013, Table 140.6 B
| Area Category | ZONE1 OFFICE | 0.75 |  | T24, 2013, Table 140.6-C
|  | ZONE2 FINE STORAGE | 0.6
|  | ZONE3 BULK STORAGE | 0.6

## Equipment
Equipment - Warehouse
Space Type | Plug Load Power Density (W/ft²) | Destratification Fan Load Power Density (W/ft²) | Forklift Load Power Density (W/ft²) | Source
Office Area (>250 square feet) | 0.7 |  |  | Plug load and schedules project with CEC, 2025
Storage, Commercial/Industrial (Warehouse) | 0.2 | 0.09 | 0.7 | Plug load: T24 2022 - Appendix 5.4A: "Space Use Data-T24N-2023" Destratification: Electricity usage of destratification fans. Assumptions: 2 ACH (Bulk Storage: 32,197 cfm (965,908*2/60) FineStorage:12808 cfm (384,263*2/60)) , 3 HVLS fans each ~15,000 cfm and 1.5 kw for each: Total 0.09 w/sf https://continentalfan.com/wp-content/uploads/2022/12/Destratification_Fans_Wholesale_Ventilation_Products.pdf? Forklift: Electricity usage for charging forklift machines/robots, distributed to both storage spaces. Assumption: 5 chargers each 10 K , 0.7 diversity
Storage, Commercial/Industrial (Warehouse) |  |  |  | Electricity usage of destratification fans. Assumptions: 2 ACH (Bulk Storage: 32,197 cfm (965,908*2/60) FineStorage:12808 cfm (384,263*2/60)) , 3 HVLS fans each ~15,000 cfm and 1.5 kw for each: Total 0.09 w/sf https://continentalfan.com/wp-content/uploads/2022/12/Destratification_Fans_Wholesale_Ventilation_Products.pdf? | https://continentalfan.com/destratification-fan-application-guide/?utm
Storage, Commercial/Industrial (Warehouse) |  |  |  | Electricity usage for charging forklift machines/robots, distributed to both storage spaces. Assumption: 5 chargers each 10 K , 0.7 diversity | U.S. Department of Energy, Better Buildings, "Battery Charging Basics for Forklifts" Pacific Northwest National Laboratory (PNNL), "Warehouse Energy Use: Characterization and Opportunities" Class I–III electric forklift chargers typically draw 4–10 kW each. Fast/Opportunity chargers may draw 10–20 kW, but 4–8 kW is most common. | (From DOE BB resources / charger efficiency studies) : "Industrial battery chargers for Class I–III forklifts commonly draw 4 to 8 kW during bulk charging."
Background Data [To be deleted prior to publication]

## Ext Lighting
Exterior Lighting - Warehouse
Motion Controlled Luminaires (W) | Non-motion Controlled Luminaires (W) | Total (W) | Source
751.5569 | 1380.4315 | 2131.9884 | T24, 2022
Exterior Lighting
Items (Assume LZ2) | Assumptions [2019 Outdoor Lighting CASE Report & PNNL 90.1-2010 TSD] |  | Unit | Lighting Power Allowance [T24, 2025, Table 140.7-A & 140.7-B] | Unit | Exterior Lighting Power (W)
IWA (Initial Wattage Allowance) |  |  |  | 200 | (W) | 200
Parking area | 400 ft² for every parking space 1 parking space per 830 ft² of gross building area | 25081.9422 | (ft²) | 0.019 | (W/ft²) | 476.5569
Building Entrance | 5 building entrance (1 per 10,000 ft² footprint) | 5 | (count) | 15 | (W/ea) | 75
Hardscape Ornamental Light | 0.1 ft² per 1 ft² of gross building area for hardscape ornamental light | 5204.503 | (ft²) | 0.007 | (W/ft²) | 36.4315
Building façade | 0.1 W per 1 ft² of facade area Façade Area = Perimeter × 0.5 × 28 ft (30 ft is the max height that is lit) * The 0.5 factor assumes that only half of the perimeter walls are lit. -Formula is developed based on the 2019 Outdoor Lighting CASE report | 13440 | (ft²) | 0.1 | (W/ft²) | 1344
Motion controlled Luminaires | [5 empty] | 751.5569
Non-motion-controlled Luminaires | [5 empty] | 1380.4315
TOTAL | [5 empty] | 2131.9884
*Developed based on 2019 Outdoor Lighting CASE Report
Perimeter (ft) | 960
Total floor area (ft²) | 52045.03
Floors | 1

## Schedules
Schedules - Warehouse
Zone | Schedule Category | Schedule | Source | Type | Hour
[5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Fine storage | FineStorage | Occupancy | T24 2022 - Appendix 5.4B, [Warehouse] (Start and end hours of weekday schedule has been shifted to stay align with the plug load project with CEC) with Saturday Occupied. | Weekday | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.85 | 0.85 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.85 | 0.85 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fine storage | FineStorage | Lights | T24 2022 - Appendix 5.4B, [Warehouse] (Start and end hours of weekday schedule has been shifted to stay align with the plug load project with CEC) with Saturday Occupied. | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.45 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.3 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.45 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.3 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Fine storage | FineStorage | ElecEquipment | Plug load and schedules project with CEC, 2025 (weekday) *New weekday schedule starts at 6 and ends at 17 instead of 8-18 in the Appendix 5.4B with Saturday Occupied. T24 2022 - Appendix 5.4B (weekend) | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.65 | 0.25 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.65 | 0.25 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Fine storage | FineStorage | HVACAvail | T24 2022 - Appendix 5.4B, [Warehouse] (Start and end hours of weekday schedule has been shifted to stay align with the plug load project with CEC) with Saturday Occupied. | Weekday | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fine storage | FineStorage | ServiceHotWater | T24 2022 - Appendix 5.4B, [Warehouse] (Start and end hours of weekday schedule has been shifted to stay align with the plug load project with CEC) with Saturday Occupied. | Weekday | 0.02 | 0.02 | 0.02 | 0.05 | 0.07 | 0.1 | 0.3 | 0.36 | 0.36 | 0.36 | 0.36 | 0.46 | 0.57 | 0.43 | 0.4 | 0.3 | 0.18 | 0.18 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
|  |  |  | Saturday | 0.02 | 0.02 | 0.02 | 0.05 | 0.07 | 0.1 | 0.3 | 0.36 | 0.36 | 0.36 | 0.36 | 0.46 | 0.57 | 0.43 | 0.4 | 0.3 | 0.18 | 0.18 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
|  |  |  | Sunday | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.04 | 0.04 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
Fine storage | FineStorage | Infiltration |  | Weekday | bar: Hour 1 to Hour 24
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
Fine storage | FineStorage | HtgSetpt | T24 2022 - Appendix 5.4B, [Warehouse] with Saturday Occupied. | Weekday | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  |  | Saturday | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  |  | Sunday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Fine storage | FineStorage | ClgSetpt | T24 2022 - Appendix 5.4B, [Warehouse] with Saturday Occupied. | Weekday | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
|  |  |  | Saturday | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
|  |  |  | Sunday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
BulkStorage
Bulk storage | BulkStorage | Occupancy | T24 2022 - Appendix 5.4B, [Warehouse] (Start and end hours of weekday schedule has been shifted to stay align with the plug load project with CEC) with Saturday Occupied. | Weekday | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.85 | 0.85 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.85 | 0.85 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bulk storage | BulkStorage | Lights | T24 2022 - Appendix 5.4B, [Warehouse] (Start and end hours of weekday schedule has been shifted to stay align with the plug load project with CEC) with Saturday Occupied. | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.45 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.3 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.45 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.3 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Bulk storage | BulkStorage | ElecEquipment | Plug load and schedules project with CEC, 2025 (weekday) *New weekday schedule starts at 6 and ends at 17 instead of 8-18 in the Appendix 5.4B with Saturday Occupied. T24 2022 - Appendix 5.4B (Sunday) | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.65 | 0.25 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.65 | 0.25 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Bulk storage | BulkStorage | HVACAvail | Developed based on Unit Heater | Weekday | bar: Hour 1 to Hour 24
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
Bulk storage | BulkStorage | ServiceHotWater | T24 2022 - Appendix 5.4B, [Warehouse] (Start and end hours of weekday schedule has been shifted to stay align with the plug load project with CEC) with Saturday Occupied. | Weekday | 0.02 | 0.02 | 0.02 | 0.05 | 0.07 | 0.1 | 0.3 | 0.36 | 0.36 | 0.36 | 0.36 | 0.46 | 0.57 | 0.43 | 0.4 | 0.3 | 0.18 | 0.18 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
|  |  |  | Saturday | 0.02 | 0.02 | 0.02 | 0.05 | 0.07 | 0.1 | 0.3 | 0.36 | 0.36 | 0.36 | 0.36 | 0.46 | 0.57 | 0.43 | 0.4 | 0.3 | 0.18 | 0.18 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
|  |  |  | Sunday | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.04 | 0.04 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
Bulk storage | BulkStorage | Infiltration |  | Weekday | bar: Hour 1 to Hour 24
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
Bulk storage | BulkStorage | HtgSetpt | PNNL ASHRAE 90.1 2022, Warehouse prototype | Weekday | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
|  |  |  | Saturday | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
|  |  |  | Sunday | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
Bulk storage | BulkStorage | ForkliftEquipment | with Saturday Occupied. | Weekday | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Saturday | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Bulk storage | BulkStorage | DoorInfiltration |  | Weekday | 0.36364 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 1 | 1 | 1 | 1 | 1 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36
|  |  |  | Saturday | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 1 | 1 | 1 | 1 | 1 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36
|  |  |  | Sunday | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36
Office
Office | Office | Occupancy | T24 2022 - Appendix 5.4B, [Office] Updated based on Plug load and schedules project with CEC, 2025 | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
Office | Office | Lights | T24 2022 - Appendix 5.4B, [Office] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.35 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Office | Office | ElecEquipment | Plug load and schedules project with CEC, 2025 | Weekday | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.74 | 0.87 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.5 | 0.45 | 0.45 | 0.45
|  |  |  | Saturday | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43
|  |  |  | Sunday | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43
Office | Office | HVACAvail | T24 2022 - Appendix 5.4B, [Office] Updated based on Plug load and schedules project with CEC, 202 | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Office | Office | ServiceHotWater | T24 2022 - Appendix 5.4B, [Office] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.12 | 0.14 | 0.07 | 0.07 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05
|  |  |  | Sunday | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04
Office | Office | Infiltration |  | Weekday | bar: Hour 1 to Hour 24
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
Office | Office | HtgSetpt | Developed based on HVACAvail and Thermostat setpoints | Weekday | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
|  |  |  | Saturday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  |  | Sunday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Office | Office | ClgSetpt | Developed based on HVACAvail and Thermostat setpoints | Weekday | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
|  |  |  | Saturday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
|  |  |  | Sunday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
Office | Office | DoorInfiltration | PNNL ASHRAE 90.1 2022, Warehouse prototype | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0.131 | 1 | 0.131 | 0.131 | 0.131 | 0.131 | 1 | 0.131 | 0.131 | 0.131 | 0.131 | 1 | 0.131 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Other
| Building | ExtLightingNonMotionCtrl |  | Weekday | bar: Hour 1 to Hour 24
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
| Building | ExtLightingMotionCtrl |  | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Office | Building | FunctionalAreaPeopleActivityLevel | Based on Activity level schedules in CEC Prototypes | Weekday | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
|  |  |  | Saturday | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
|  |  |  | Sunday | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
FineStorage and Bulk Storage | Building | SaleStoragePeopleActivityLevel | Based on Activity level schedules in CEC Prototypes | Weekday | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8
|  |  |  | Saturday | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8
|  |  |  | Sunday | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8
Background Data [To be deleted prior to publication] | bar: Hour 1 to Hour 2
Plug load and schedules project with CEC, 2025 ( July 2025)
The analysis of warehouse schedules indicated that, on weekdays, warehouses tend to begin operating earlier in the day, and end operating earlier than the current NMACM schedules. Therefore, a shift in the schedule is proposed as shown in Figure 5. No changes are proposed to the Saturday or Sunday schedules.
#VALUE!

## Weights
% of Floor Area per CZ and Vintage Bin - Warehouse | [6 empty] | % of Floor Area per CZ and Vintage Bin - Warehouse
Prototype | CZ | Vintage Bin |  |  |  |  | Prototype | Vintage Bin | CZ
|  | Pre-1978 | 1978-1997 | 1998-2007 | 2008-2018 |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
Warehouse | 1 | 17.7% | 28.51% | 28.83% | 24.96% | 100% | Warehouse | Pre-1978 | 0.556% | 1.28% | 6.41% | 3.478% | 0.2315% | 11.64% | 1.908% | 24.86% | 24.97% | 3.309% | 1.851% | 8.955% | 2.033% | 3.138% | 0.6987% | 4.678% | 100%
| 2 | 27.9% | 18.29% | 17.49% | 36.32% | 100% |  | 1978-1997 | 0.5797% | 0.5433% | 4.714% | 2.376% | 0.2% | 5.341% | 1.724% | 10.46% | 11.2% | 13.24% | 4.275% | 16.11% | 4.983% | 3.774% | 7.476% | 13% | 100%
| 3 | 33.77% | 38.35% | 23.69% | 4.192% | 100% |  | 1998-2007 | 0.519% | 0.4601% | 2.578% | 1.226% | 0.3973% | 1.911% | 0.9834% | 3.619% | 3.86% | 26.8% | 2.068% | 8.083% | 2.763% | 5.4% | 15.35% | 23.98% | 100%
| 4 | 36.77% | 38.8% | 22.61% | 1.812% | 100% |  | 2008-2018 | 0.9829% | 2.089% | 0.9975% | 0.2148% | 0.097% | 1.216% | 0.2837% | 2.619% | 2.135% | 26.03% | 4.103% | 13.72% | 3.302% | 3.255% | 22.8% | 16.15% | 100%
| 5 | 17.66% | 23.56% | 52.88% | 5.9% | 100%
| 6 | 48.12% | 34.09% | 13.77% | 4.008% | 100% |  | Total | 0.6174% | 0.9019% | 3.732% | 1.859% | 0.2577% | 4.757% | 1.28% | 9.717% | 9.97% | 17.94% | 3.015% | 11.57% | 3.378% | 4.125% | 11.25% | 15.62% | 100%
| 7 | 29.3% | 40.89% | 26.34% | 3.475% | 100%
| 8 | 50.31% | 32.69% | 12.77% | 4.227% | 100%
| 9 | 49.24% | 34.13% | 13.28% | 3.359% | 100%
| 10 | 3.626% | 22.4% | 51.23% | 22.75% | 100%
| 11 | 12.07% | 43.06% | 23.53% | 21.34% | 100%
| 12 | 15.21% | 42.25% | 23.95% | 18.59% | 100%
| 13 | 11.83% | 44.79% | 28.05% | 15.33% | 100%
| 14 | 14.96% | 27.78% | 44.89% | 12.37% | 100%
| 15 | 1.221% | 20.18% | 46.81% | 31.79% | 100%
| 16 | 5.887% | 25.27% | 52.63% | 16.21% | 100%
| Statewide | 19.66% | 30.36% | 34.29% | 15.68% | 100%
Ref: CEUS 2022 dataset: Warehouse group
And converted FZ level data to CZ level

## PV (hidden)
PV - Warehouse
TBD

## EV Charger (hidden)
EV Charger - Warehouse
TBD

## Data (hidden)
Space Function | Electric Equipment Load Intensity | Electric Equipment Load Intensity | LPD
Aging Eye/Low-vision (Corridor Area) |  |  | 2013 | 2016 | 2019 | 2025
Aging Eye/Low-vision (Dining)
Aging Eye/Low-vision (Lobby, Main Entry)
Aging Eye/Low-vision (Lounge/Waiting Area)
Aging Eye/Low-vision (Multipurpose Room)
Aging Eye/Low-vision (Religious Worship Area)
Aging Eye/Low-vision (Restroom)
Aging Eye/Low-vision (Stairwell)
Audience Seating Area
Auditorium Area
Auto Repair / Maintenance Area
Barber, Beauty Salon, Spa Area
Civic Meeting Place Area
Classroom, Lecture, Training, Vocational Areas
Concourse and Atria Area
Convention, Conference, Multipurpose and Meeting Area
Copy Room
Corridor Area
Dining Area (Bar/Lounge and Fine Dining)
Dining Area (Cafeteria/Fast Food)
Dining Area (Family and Leisure)
Electrical, Mechanical, Telephone Rooms
Exercise/Fitness Center and Gymnasium Areas
Financial Transaction Area
Healthcare Facility and Hospitals (Exam/Treatment Room)
Healthcare Facility and Hospitals (Imaging Room)
Healthcare Facility and Hospitals (Medical Supply Room)
Healthcare Facility and Hospitals (Nursery)
Healthcare Facility and Hospitals (Nurse's Station)
Healthcare Facility and Hospitals (Operating Room)
Healthcare Facility and Hospitals (Patient Room)
Healthcare Facility and Hospitals (Physical Therapy Room)
Healthcare Facility and Hospitals (Recovery Room)
Hotel Function Area
Kitchen/Food Preparation Area
Kitchenette or Residential Kitchen
Laboratory, Scientific
Laundry Area
Library (Reading Area)
Library (Stacks Area)
Lobby, Main Entry
Locker Room
Lounge, Breakroom, or Waiting Area
Manufacturing, Commercial & Industrial Work Area (Low Bay)
Manufacturing, Commercial & Industrial Work Area (High Bay)
Manufacturing, Commercial & Industrial Work Area (Precision)
Museum Area (Exhibition/Display)
Museum Area (Restoration Room)
Office Area (>250 square feet)
Office Area (<250 square feet)
Parking Garage Area (Parking Zone and Ramps)
Parking Garage Area (Daylight Adaptation Zones)
Pharmacy Area
Retail Sales Area (Grocery Sales)
Retail Sales Area (Retail Merchandise Sales)
Retail Sales Area (Fitting Room)
Religious Worship Area
Restrooms
Stairwell
Storage, Commercial/Industrial (Warehouse)
Storage, Commercial/Industrial (Refrigerated)
Storage, Commercial/Industrial (Shipping & Handling)
Storage (General)
Sports Arena - Playing Area (> 5,000 Spectators)
Sports Arena - Playing Area (2,000 - 5,000 Spectators)
Sports Arena - Playing Area (< 2,000 Spectators)
Sports Arena - Playing Area (Recreational)
Theater Area (Motion Picture)
Theater Area (Performance)
Transportation Function (Baggage Area)
Transportation Function (Ticketing Area)
Videoconferencing Studio
High-Rise Residential Living Spaces
Hotel/Motel Guest Room
All other
Attic
Reception Area
Elevator
Plenum
IT Room (EPD 12)
Computer Room (EPD 20)
Server Room (EPD 45)

## Energy Usage
CalBEM Energy Consumption - Warehouse | [11 empty] | Energy Consumption - Warehouse
Prototype | CZ | CalBEM Electricity EUI (KBTU/ft²) | CalBEM Gas EUI (KBTU/ft²) | CalBEM Total EUI (KBTU/ft²) | New Construction Electricity EUI (KBTU/ft²) | New Construction Gas EUI (KBTU/ft²) | New Construction Total EUI (KBTU/ft²) | National Average | Acceptable Range (25% Higher) | Acceptable Range (25% Lower) | National Average Acceptable EUI Range | Prototype | CZ | Total Floorspace (Thousand of ft²) | Electric Energy Intensity (kWh/ft²) | Annual Gas Intensity (kWh/ft²) | CEUS 2023 Total EUI (kBtu/ft²) | Acceptable Range (25% Higher) | Acceptable Range (25% Lower) | CEUS 2022 Acceptable EUI Range
Warehouse | 1 | [6 empty] | 35.5 | 44.375 | 26.625 | 17.75 | Warehouse | 1 | 10688 | 28.6447 | 3.4243 | 32.069 | 40.0863 | 24.0518 | 16.0345
| 2 | [6 empty] | 29.9 | 37.375 | 22.425 | 14.95 |  | 2 | 15367 | 15.0199 | 4.5354 | 19.5553 | 24.4442 | 14.6665 | 9.7777
| 3 | [6 empty] | 28.1 | 35.125 | 21.075 | 14.05 |  | 3 | 68713 | 25.3064 | 7.5783 | 32.8847 | 41.1058 | 24.6635 | 16.4423
| 4 | [6 empty] | 30.9 | 38.625 | 23.175 | 15.45 |  | 4 | 34199 | 25.8828 | 6.747 | 32.6299 | 40.7873 | 24.4724 | 16.3149
| 5 | [6 empty] | 27.1 | 33.875 | 20.325 | 13.55 |  | 5 | 5266 | 22.4114 | 23.7245 | 46.1359 | 57.6699 | 34.6019 | 23.0679
| 6 | [6 empty] | 25.1 | 31.375 | 18.825 | 12.55 |  | 6 | 81916 | 13.5332 | 4.462 | 17.9952 | 22.494 | 13.4964 | 8.9976
| 7 | [6 empty] | 24.9 | 31.125 | 18.675 | 12.45 |  | 7 | 21820 | 21.6537 | 3.547 | 25.2007 | 31.5009 | 18.9005 | 12.6004
| 8 | [6 empty] | 26.5 | 33.125 | 19.875 | 13.25 |  | 8 | 167070 | 12.6086 | 4.8064 | 17.415 | 21.7687 | 13.0612 | 8.7075
| 9 | [6 empty] | 27.3 | 34.125 | 20.475 | 13.65 |  | 9 | 170729 | 13.6239 | 4.3726 | 17.9965 | 22.4956 | 13.4974 | 8.9982
| 10 | [6 empty] | 28.4 | 35.5 | 21.3 | 14.2 |  | 10 | 302672 | 15.0574 | 2.0697 | 17.1271 | 21.4089 | 12.8453 | 8.5635
| 11 | [6 empty] | 32.8 | 41 | 24.6 | 16.4 |  | 11 | 52236 | 29.1088 | 5.051 | 34.1597 | 42.6997 | 25.6198 | 17.0799
| 12 | [6 empty] | 31 | 38.75 | 23.25 | 15.5 |  | 12 | 201422 | 26.64 | 3.6095 | 30.2495 | 37.8118 | 22.6871 | 15.1247
| 13 | [6 empty] | 32.5 | 40.625 | 24.375 | 16.25 |  | 13 | 58241 | 29.1206 | 2.8962 | 32.0168 | 40.021 | 24.0126 | 16.0084
| 14 | [6 empty] | 33.7 | 42.125 | 25.275 | 16.85 |  | 14 | 70031 | 17.8629 | 2.7744 | 20.6373 | 25.7966 | 15.478 | 10.3186
| 15 | [6 empty] | 33.7 | 42.125 | 25.275 | 16.85 |  | 15 | 189094 | 10.0452 | 1.9605 | 12.0057 | 15.0071 | 9.0043 | 6.0028
| 16 | [6 empty] | 37.6 | 47 | 28.2 | 18.8 |  | 16 | 265379 | 21.4715 | 2.3093 | 23.7808 | 29.726 | 17.8356 | 11.8904
Ref: CEUS 2022 Report
And converted FZ level data to CZ level
Background Data [To be deleted prior to publication]