## Notes
Data Sources
Dataset | Dodge 2023
CEUS 2022
CBECS 2018
ComStock 2023
Prototype | CEC Hospital prototype (CBECC 2022.3.1) | https://bees.noresco.com/software2022.html
| PNNL Hospital prototype (90.1-2022 2019, 2013) | https://www.energycodes.gov/prototype-building-models#Commercial
| DEER Hospital prototype (June 2024) | https://github.com/sound-data/DEER-Prototypes-EnergyPlus
Codes | Title 24, part 6, referred to as T24 (1984, 2001, 2007, 2013, 2016, 2022, 2025)
ASHRAE 90.1 (2022)
ASHRAE 62.1 (2022)
CFR Title 10 (2008, 2010, 2025)
ASHRAE 170/OSHPD
2022 California Mechanical Code (Title 24, Part 4)
ACM 2022
T24 2022 - Appendix 5.4A and Appendix 5.4B
https://www.energy.ca.gov/publications/2022/2022-nonresidential-and-multifamily-alternative-calculation-method-reference
Others | 2022 Reduced infiltration CASE report | https://title24stakeholders.com/wp-content/uploads/2020/10/2022-T24-Final-CASE-Report_Reduce-Infiltration.pdf
| 2019 Outdoor Lighting CASE Report | https://title24stakeholders.com/wp-content/uploads/2016/10/T24-2019-CASE-Study-Results-Report-Outdoor-Sources_Final_with-Attachments.pdf
| PNNL 20405, 2010 | https://www.pnnl.gov/main/publications/external/technical_reports/PNNL-20405.pdf
| Air leakage Memo, NORESCO, 2025 | https://2050partners.sharepoint.com/:w:/r/sites/CalBEMCollaborativeEfforts/Shared%20Documents/Working%20Group%201%20-%20Streamlined%20Process/D%20-%20Complexity%20of%20Compliance/Prototype%20Unification/Project%20Development/Phase%202%20(Collect%20Inputs)%20Development/NR/Air%20Leakage%20Memo/Infiltration_rate_report_14May2025-Short-Version.docx?d=w3bef8f747fac44f2a70cd76617660066&csf=1&web=1&e=wh5Dm4
| 2019 High Efficiency Fume Hoods in Laboratory Spaces CASE Report | https://title24stakeholders.com/wp-content/uploads/2017/09/2019-T24-CASE-Report_Fume-Hoods_Final_September-2017.pdf?
Construction Rate
Notes
Hospital | A hospital, as defined across CEC, PNNL, and CPUC prototypes, is a large, full-service inpatient healthcare facility that operates 24/7, providing acute medical care, surgical services, and diagnostic treatment. It includes patient rooms, operating suites, labs, and support areas, and is typically served by 100% outdoor air HVAC systems with strict ventilation and pressurization controls.
EIA, 2018 CBECS | On average, hospitals were 264,800 square feet per building, but outpatient health care buildings averaged 13,700 square feet.
Source | https://www.eia.gov/consumption/commercial/

## Prototype
NORESCO, Updated August 2025
Hospital
Characteristic | Value | Data Sources
Building Type | Hospital
Building Category | Nonresidential
Vintages | 4 Vintages: Pre-1978 , 1978-1997 ,1998-2007 , 2008-2018 New Construction (2019+) | Based on the vintage bin analysis | NonRes-Vintage bins-Draft Report-30Nov2023-Final.docx
Shape |  | The analysis uses prototype geometry originally developed by PNNL. The CEC prototypes also adopt this geometry as a foundation.
Total Floor Area (ft²) | 241500 (230 ft x 175 ft for each floor) | Same as CEC and PNNL
Aspect Ratio | 1.31 | Same as CEC and PNNL
Number of Floors | 5 (plus basement) | Same as CEC and PNNL
Roof type | Flat roof | Same as CEC and PNNL
WWR | North: 12%, East: 13%, South: 15%, West: 24% Average Total: 16% | Same as CEC and PNNL
Shading Geometry | No Shades | Same as CEC and PNNL
Floor to floor height (feet) | Ground floor: 8 ft Upper floors: 14 ft | Same as CEC and PNNL
Floor to ceiling height (feet) | No ceiling; plenum is modeled | Same as CEC and PNNL
Glazing sill height (feet) | 3 ft (4 ft high windows) | Same as CEC and PNNL
Above grade wall area (ft²) | 56720
Gross wall area (ft²) | 63203
Roof area (ft²) | 40254
Underground Gross Wall Area (ft²) | 6482

## Zones
Proposed Layout - Hospital
Space Type | Space/Thermal Zone | HVAC System Name / AHU Name | Schedule Category | Conditioned (Y/N) | Area Fraction | Area (ft²) | Volume (ft³) | Multipliers | Total Area (ft²) | Number of People | People (Persons/1,000 ft²) [T24, 2025,Table 120.1-A] | Note
Office Area (>250 square feet) | Basement | VAV 1 | Office | Yes | 16.67% | 40253.93 | 322126.45 | 1 | 40253.93 | 201.2696 | 5
Corridor Area | Corridor_flr_1 | VAV 1 | Health | Yes | 2.536% | 6125.6 | 85784.61 | 1 | 6125.6 | 30.628 | 5
Corridor Area | Corridor_flr_2 | VAV 1 | Health | Yes | 2.536% | 6125.6 | 85784.61 | 1 | 6125.6 | 30.628 | 5
Corridor Area | Corridor_flr_5 | VAV 2 | Health | Yes | 2.236% | 5400.53 | 75630.51 | 1 | 5400.53 | 27.0026 | 5
Corridor Area | Corridor_nw_flr_3 | VAV 2 | Health | Yes | 2.526% | 6100.6 | 85434.47 | 1 | 6100.6 | 30.503 | 5
Corridor Area | Corridor_nw_flr_4 | VAV 2 | Health | Yes | 2.526% | 6100.6 | 85434.47 | 1 | 6100.6 | 30.503 | 5
Corridor Area | Corridor_se_flr_3 | VAV 2 | Health | Yes | 2.526% | 6100.6 | 85434.47 | 1 | 6100.6 | 30.503 | 5
Corridor Area | Corridor_se_flr_4 | VAV 2 | Health | Yes | 2.526% | 6100.6 | 85434.47 | 1 | 6100.6 | 30.503 | 5
Dining Area (Cafeteria/Fast Food) | Dining_flr_5 | VAV 2 | Restaurant | Yes | 3.106% | 7500.73 | 105042.38 | 1 | 7500.73 | 247.5241 | 33
Healthcare Facility and Hospitals (Exam/Treatment Room) | Er_exam1_mult4_flr_1 | VAV ER | Health24/7 | Yes | 0.4969% | 300.03 | 4201.7 | 4 | 1200.12 | 1.5001 | 5 | Table 120.1-A- 2025 T24-Misc-All Other
Healthcare Facility and Hospitals (Exam/Treatment Room) | Er_exam3_mult4_flr_1 | VAV ER | Health24/7 | Yes | 0.4969% | 300.03 | 4201.7 | 4 | 1200.12 | 1.5001 | 5
Healthcare Facility and Hospitals (Nurse's Station) | Er_nursestn_lobby_flr_1 | VAV 1 | Health24/7 | Yes | 5.507% | 13301.3 | 186275.15 | 1 | 13301.3 | 66.5065 | 5
Healthcare Facility and Hospitals (Exam/Treatment Room) | Er_trauma1_flr_1 | VAV ER | Health24/7 | Yes | 0.1242% | 300.03 | 4201.7 | 1 | 300.03 | 1.5001 | 5
Healthcare Facility and Hospitals (Exam/Treatment Room) | Er_trauma2_flr_1 | VAV ER | Health24/7 | Yes | 0.1242% | 300.03 | 4201.7 | 1 | 300.03 | 1.5001 | 5
Healthcare Facility and Hospitals (Exam/Treatment Room) | Er_triage_mult4_flr_1 | VAV ER | Health24/7 | Yes | 0.4969% | 300.03 | 4201.7 | 4 | 1200.12 | 1.5001 | 5
Healthcare Facility and Hospitals (Recovery Room) | Icu_flr_2 | VAV ICU | Health24/7 | Yes | 2.754% | 6652.36 | 93161.52 | 1 | 6652.36 | 33.2618 | 5 | Intensive Care Unit, for lighting we can go with the general lighting for the patient room but for other EPD and ventilation refer to the CA mechanical code
Healthcare Facility and Hospitals (Nurse's Station) | Icu_nursestn_lobby_flr_2 | VAV 1 | Health24/7 | Yes | 2.981% | 7199.26 | 100820.51 | 1 | 7199.26 | 35.9963 | 5
Healthcare Facility and Hospitals (Recovery Room) | Ic_patroom1_mult5_flr_2 | VAV ICU | Health24/7 | Yes | 0.4658% | 225.02 | 3151.27 | 5 | 1125.1 | 1.1251 | 5
Healthcare Facility and Hospitals (Recovery Room) | Ic_patroom2_flr_2 | VAV ICU | Health24/7 | Yes | 0.1242% | 300.03 | 4201.7 | 1 | 300.03 | 1.5001 | 5
Healthcare Facility and Hospitals (Recovery Room) | Ic_patroom3_mult6_flr_2 | VAV ICU | Health24/7 | Yes | 0.559% | 225.02 | 3151.27 | 6 | 1350.12 | 1.1251 | 5
Kitchen/Food Preparation Area | Kitchen_flr_5 | CAV Kitchen | Kitchen | Yes | 4.141% | 10000.98 | 140056.5 | 1 | 10000.98 | 30.0029 | 3
Laboratory, Scientific | Lab_flr_3 | VAV Laboratory | Health | Yes | 1.18% | 2850.28 | 39916.1 | 1 | 2850.28 | 14.2514 | 5 | Change it back to 5 same as CEC and PNNL
Laboratory, Scientific | Lab_flr_4 | VAV Laboratory | Health | Yes | 1.18% | 2850.28 | 39916.1 | 1 | 2850.28 | 14.2514 | 5
Lobby, Main Entry | Lobby_records_flr_1 | VAV 1 | Health | Yes | 6.573% | 15876.28 | 222335.92 | 1 | 15876.28 | 523.9172 | 33
Healthcare Facility and Hospitals (Nurse's Station) | Nursestn_lobby_flr_3 | VAV 2 | Health24/7 | Yes | 4.037% | 9750.95 | 136555.09 | 1 | 9750.95 | 48.7548 | 5
Healthcare Facility and Hospitals (Nurse's Station) | Nursestn_lobby_flr_4 | VAV 2 | Health24/7 | Yes | 4.037% | 9750.95 | 136555.09 | 1 | 9750.95 | 48.7548 | 5
Healthcare Facility and Hospitals (Nurse's Station) | Nursestn_lobby_flr_5 | VAV 2 | Health24/7 | Yes | 4.638% | 11201.09 | 156863.28 | 1 | 11201.09 | 56.0054 | 5
Office Area (>250 square feet) | Office1_flr_5 | VAV 2 | Office | Yes | 0.3106% | 750.27 | 10507.01 | 1 | 750.27 | 3.7513 | 5
Office Area (<250 square feet) | Office1_mult5_flr_1 | VAV 1 | Office | Yes | 0.3105% | 150.01 | 2100.85 | 5 | 750.05 | 0.75005 | 5
Office Area (>250 square feet) | Office2_mult5_flr_5 | VAV 2 | Office | Yes | 1.553% | 750.07 | 10502.39 | 5 | 3750.35 | 3.7504 | 5
Office Area (>250 square feet) | Office3_flr_5 | VAV 2 | Office | Yes | 0.3106% | 750.07 | 10504.24 | 1 | 750.07 | 3.7504 | 5
Office Area (<250 square feet) | Office4_mult6_flr_5 | VAV 2 | Office | Yes | 0.3727% | 150.01 | 2100.85 | 6 | 900.06 | 0.75005 | 5
Healthcare Facility and Hospitals (Operating Room) | Or1_flr_2 | VAV OR | Health | Yes | 0.2484% | 600.06 | 8403.39 | 1 | 600.06 | 3.0003 | 5
Healthcare Facility and Hospitals (Operating Room) | Or2_mult5_flr_2 | VAV OR | Health | Yes | 1.242% | 600.06 | 8403.39 | 5 | 3000.3 | 3.0003 | 5
Healthcare Facility and Hospitals (Operating Room) | Or3_flr_2 | VAV OR | Health | Yes | 0.2484% | 600.06 | 8403.39 | 1 | 600.06 | 3.0003 | 5
Healthcare Facility and Hospitals (Operating Room) | Or4_flr_2 | VAV OR | Health | Yes | 0.9938% | 2400.23 | 33613.56 | 1 | 2400.23 | 12.0011 | 5
Healthcare Facility and Hospitals (Nurse's Station) | Or_nursestn_lobby_flr_2 | VAV 1 | Health24/7 | Yes | 4.513% | 10901.06 | 152661.59 | 1 | 10901.06 | 54.5053 | 5
Healthcare Facility and Hospitals (Patient Room) | Patroom1_mult10_flr_3 | VAV Patient Room | Patient24/7 | Yes | 0.9317% | 225.02 | 3151.27 | 10 | 2250.2 | 1.1251 | 5
Healthcare Facility and Hospitals (Patient Room) | Patroom1_mult10_flr_4 | VAV Patient Room | Patient24/7 | Yes | 0.9317% | 225.02 | 3151.27 | 10 | 2250.2 | 1.1251 | 5
Healthcare Facility and Hospitals (Patient Room) | Patroom2_flr_3 | VAV Patient Room | Patient24/7 | Yes | 0.1553% | 375.04 | 5252.12 | 1 | 375.04 | 1.8752 | 5
Healthcare Facility and Hospitals (Patient Room) | Patroom2_flr_4 | VAV Patient Room | Patient24/7 | Yes | 0.1553% | 375.04 | 5252.12 | 1 | 375.04 | 1.8752 | 5
Healthcare Facility and Hospitals (Patient Room) | Patroom3_mult10_flr_3 | VAV Patient Room | Patient24/7 | Yes | 0.9007% | 217.54 | 3046.5 | 10 | 2175.4 | 1.0877 | 5
Healthcare Facility and Hospitals (Patient Room) | Patroom3_mult10_flr_4 | VAV Patient Room | Patient24/7 | Yes | 0.9007% | 217.54 | 3046.5 | 10 | 2175.4 | 1.0877 | 5
Healthcare Facility and Hospitals (Patient Room) | Patroom4_flr_3 | VAV Patient Room | Patient24/7 | Yes | 0.1553% | 375.04 | 5252.12 | 1 | 375.04 | 1.8752 | 5
Healthcare Facility and Hospitals (Patient Room) | Patroom4_flr_4 | VAV Patient Room | Patient24/7 | Yes | 0.1553% | 375.04 | 5252.12 | 1 | 375.04 | 1.8752 | 5
Healthcare Facility and Hospitals (Patient Room) | Patroom5_mult10_flr_3 | VAV Patient Room | Patient24/7 | Yes | 0.9317% | 225.02 | 3151.27 | 10 | 2250.2 | 1.1251 | 5
Healthcare Facility and Hospitals (Patient Room) | Patroom5_mult10_flr_4 | VAV Patient Room | Patient24/7 | Yes | 0.9317% | 225.02 | 3151.27 | 10 | 2250.2 | 1.1251 | 5
Healthcare Facility and Hospitals (Patient Room) | Patroom6_flr_3 | VAV Patient Room | Patient24/7 | Yes | 0.1242% | 300.03 | 4201.7 | 1 | 300.03 | 1.5001 | 5
Healthcare Facility and Hospitals (Patient Room) | Patroom6_flr_4 | VAV Patient Room | Patient24/7 | Yes | 0.1242% | 300.03 | 4201.7 | 1 | 300.03 | 1.5001 | 5
Healthcare Facility and Hospitals (Patient Room) | Patroom7_mult10_flr_3 | VAV Patient Room | Patient24/7 | Yes | 0.9007% | 217.54 | 3046.5 | 10 | 2175.4 | 1.0877 | 5
Healthcare Facility and Hospitals (Patient Room) | Patroom7_mult10_flr_4 | VAV Patient Room | Patient24/7 | Yes | 0.9007% | 217.54 | 3046.5 | 10 | 2175.4 | 1.0877 | 5
Healthcare Facility and Hospitals (Patient Room) | Patroom8_flr_3 | VAV Patient Room | Patient24/7 | Yes | 0.1242% | 300.03 | 4201.7 | 1 | 300.03 | 1.5001 | 5
Healthcare Facility and Hospitals (Patient Room) | Patroom8_flr_4 | VAV Patient Room | Patient24/7 | Yes | 0.1242% | 300.03 | 4201.7 | 1 | 300.03 | 1.5001 | 5
Healthcare Facility and Hospitals (Physical Therapy Room) | Phystherapy_flr_3 | VAV 2 | Health | Yes | 2.174% | 5250.51 | 73529.66 | 1 | 5250.51 | 26.2526 | 5
Healthcare Facility and Hospitals (Imaging Room) | Radiology_flr_4 | VAV 2 | Health | Yes | 2.174% | 5250.51 | 73529.66 | 1 | 5250.51 | 26.2526 | 5
Total (12 Space types) | Total ( 162 spaces) | Total ( Thermal Zones) |  | Total ( 162 Conditioned zones) |  |  |  |  | 241524.4 | 1705.1352
Occupancy rate of the patient rooms: | 55%
Source: A report published by California Health Care Foundation, 2022
https://www.chcf.org/wp-content/uploads/2022/07/CAHospitalsAlmanac2022QRG.pdf?utm_source=chatgpt.com
Background Data [To be deleted prior to publication]
Background Data [To be deleted prior to publication]
N

## Envelope
Envelope - Hospital
Element | Prototype | Assembly Type | Construction | Thermal Properties | Vintage | Selected T24 | Note | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
External Wall | Hospital | ExtWall_MetalFramed_NonRes | Metal frame + insulation + gypsum board (Same as CEC and DEER. PNNL has Mass wall)) | U-factor IP | Pre 1978 | N/A | ASHRAE 90.1,2022 Table A3.3.3.1, 3.5", R-0 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352
[5 empty] | 1978-1997 | 1986 | Copied from High-rise office alternative requirements (Table 2-53W): Package A with heat capacity around 10 (Btu/F-ft²) | 0.213 | 0.227 | 0.227 | 0.217 | 0.256 | 0.256 | 0.256 | 0.256 | 0.256 | 0.256 | 0.238 | 0.238 | 0.238 | 0.208 | 0.208 | 0.213
[5 empty] | 1998-2007 | 2001 | Table 1-H | 0.182 | 0.182 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.098 | 0.062 | 0.082 | 0.062 | 0.062 | 0.098 | 0.098 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.06 | 0.055 | 0.071 | 0.055 | 0.055 | 0.06 | 0.06 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055
Roof | Hospital | FlatRoof_WoodFramedAndOther_NonRes | Built-up Roof (Metal Decking Roof) Roof membrane + roof insulation + metal decking (Same as PNNL and DEER-Metal roof- CEC has wood-framed roof) | U-factor IP | Pre 1978 | N/A | Considering 30 years for roof/ insulation replacement. | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 1978-1997 | 1992 |  | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 1998-2007 | 2001 | Table 1-H | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.049 | 0.039 | 0.039 | 0.039 | 0.049 | 0.075 | 0.067 | 0.067 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038
Windows | Hospital | FixedWindow_NonRes | Single pane | U-factor IP | Pre 1978 | N/A | ASHRAE Handbook of Fundamentals (Table 4-Ch15) for single pane & T24, 2013 for double pane(33%-67%)* | 0.61976 | 0.61976 | 0.61976 | 0.61976 | 0.61976 | 0.61976 | 0.61976 | 0.61976 | 0.61976 | 0.61976 | 0.61976 | 0.61976 | 0.61976 | 0.61976 | 0.61976 | 0.61976
[5 empty] | 1978-1997 | N/A |  | 0.61976 | 0.61976 | 0.61976 | 0.61976 | 0.61976 | 0.61976 | 0.61976 | 0.61976 | 0.61976 | 0.61976 | 0.61976 | 0.61976 | 0.61976 | 0.61976 | 0.61976 | 0.61976
|  |  | Double pane |  | 1998-2007 | 2001 | Table 1-H | 0.49 | 0.49 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.34 | 0.36 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.36
| Hospital | FixedWindow_NonRes | Single pane | SHGC | Pre 1978 | N/A | ASHRAE Handbook of Fundamentals (Table 10-Ch15) for single pane & T24, 2013 for double pane(33%-67%)* | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282
[5 empty] | 1978-1997 | N/A |  | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282
|  |  | Double pane |  | 1998-2007 | 2001 | Table 1-H - WWR:10-20% / SHGC non-north | 0.43 | 0.36 | 0.55 | 0.55 | 0.55 | 0.61 | 0.61 | 0.61 | 0.61 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.43
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.22 | 0.25 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.25
Infiltration
[5 empty] | Vintage | I_75 6-sdied Infiltration rate @ 75 pa | Note | CZ1: I-design (cfm/ft²) (4-sided Infiltration rate at normal pressure) (Design flow rate approach and Flow/Exterior Wall Area calculation method)
|  |  |  | Infiltration | Pre 1978 | 1.1 | 2022 CASE report (Table 38) | CZ1: 0.3121
[5 empty] | 1978-1997 | 1.1 | 2022 CASE report (Table 38) | CZ1: 0.3121
[5 empty] | 1998-2007 | 1.1 | 2022 CASE report (Table 38) | CZ1: 0.3121
[5 empty] | 2008-2018 | 1 | 2022 CASE report (Table 38) & T24, 2008-2016 (Table 140.3-B)--Air barrier is required in CZ 10-16 | CZ1: 0.2856
[5 empty] | 2019+ | 0.6 | 2022 CASE report (Table 38) & T24, 2025 (Table 140.3-B)-Air barrier is required in all CZs | CZ1: 0.1703
Source: Title 24 air barrier requirements (all editions) and the standardized infiltration rate reported in the 2022 CASE report and Dodge 2023 data
|  |  |  | Air Leakage Memo: |  | Infiltration_rate_report_14May2025-Short-Version.docx

## HVAC System
HVAC system - Hospital
Vintage | Zones | Heating | Cooling | Air Distribution | Other Systems | Source | Note
Existing | Kitchen | Gas Boiler | Chiller | CAV | CAV exhaust system with rooftop makeup air units, no energy recovery and no Demand Control | CEUS 2022(Other system based on T24 and Engineering judgement)
| All other conditioned zones | Gas Boiler | Chiller | CAV + Hydronic Reheat |  | CEUS 2022(Other system based on T24 and Engineering judgement)
New Construction | Kitchen | Gas Boiler | Chiller | VAV | A VAV dedicated MAU with tempered outside air, with exhaust hood and demand control ventilation | T24 2025 ACM 2025, Table 2 and 3 | System 13 a - Built-up kitchen MAU
| All other conditioned zones (ER, ICU, Labs, OR, Patient Rms) | Gas Boiler | Chiller | VAV + Hydronic Reheat |  | T24 2025 ACM 2025, Table 2 and 3 | System 6 – VAV
Efficiency of HVAC system (Efficiency is capacity-dependent. The following Table provides a general estimate of system efficiency based on what we saw in the existing prototype runs, or assuming cooling load based on rule of thumb)
| Upgrade/Installed year | Water Cooled Chiller | Gas Boiler | Heat Rejection (Cooling Tower) | Sources | Note
Pre 1978 | 2008 | Water Cooled, Electrically Operated, Centrifugal--≥ 300 tons and < 600 tons - 5.55 COP 5.90 IPLV | n/a | Axial fan Open-circuit cooling tower--95°F entering water 85°F leaving water 75°F entering air wb--≥ 38.2 gpm/hp | T24, 2008, Table 112-D (for chiller COP) – Table 112-G (for boiler thermal efficiency)
1978-1997
1998-2007
2008-2018 | 2013 | Water Cooled, Electrically Operated, Centrifugal--≥ 300 tons and < 600 tons --≤ 0.576 kW/ton ≤ 0.549 IPLV (Path A) | 82% Ec | Axial fan Open-circuit cooling tower--95°F entering water 85°F leaving water 75°F entering air wb--≥ 42.1 gpm/hp | T24, 2013 , Table 110.2-D (for chiller COP) - Table 110.2-J (for Boiler thermal efficiency)
New Construction | 2025 | Water Cooled, Electrically Operated, Centrifugal--≥ 300 tons and < 400 ton--≤ 0.560 kW/ton ≤ 0.520 IPLV (Path A) | Gas-Fired Boiler > 2,500,000 Btu/h and ≤10,000,000 Btu/h-- 85% Ec | Axial fan Open-circuit cooling tower--95°F entering water 85°F leaving water 75°F entering air wb--≥ 42.1 gpm/hp | T24, 2025 , Table 110.2-D (for chiller COP) - Table 110.2-J (for Boiler thermal efficiency)
* Ec = combustion efficiency
Fan power
Vintage | Approach | System | Total Static Pressure (TSP) in w.c. [PNNL 20405, 2010, Table 5.11] | Fan Efficiency [ACM, 2025] | Fan Motor and Drive Efficiency [ACM 2025, Table 13] | W/cfm [ACM 2025, Table 14 and 15] | Data Source | Note
Existing | PNNL TSP | Kitchen System CAVMAU | 4.09 | 0.65 | 0.9 |  | ACM 2025, PNNL 2010 TSD
|  | All Other Zones-FPFC (on/off) | 1.33
Brake horse power (bhp)=(Supply cfm*TSP in w.c.)/(6356*Fan efficiency)
Fan power (w/cfm) = bhp/motor and drive efficiency *746
New Construction | ACM 2025 | Kitchen System - VAVMAU System 6-VAV, >10,000 cfm | 4.7201 | 0.65 | 0.9 | 0.947 | 2025 ACM
|  | All Other Zones System 6-VAV, >10,000 cfm | 4.7201 |  |  | 0.947
Fan total eff (E+ input) = 0.65 x Motor_eff
TSP (E+ input) in w.c. = Motor_eff/746 x (6356 x Fan_eff) x W/cfm
Fan_eff=0.65
Background Data [To be deleted prior to publication]
CEUS 2022 data | Heating |  |  |  | Cooling |  | Air Distribution | Water Heater
| Floorspace Heated | Primary Heating | Fuel Type |  | Floorspace Cooled | Primary Cooling | Primary Air Dis | Fuel Type
|  | The default is the floorspace method unless otherwise specified | Elec | Gas |  | The default is the floorspace method unless otherwise specified | The default is the floorspace method unless otherwise specified | Elec | Gas
Health Care | 99% | Floorspace method: | 17% | 81% | 98% | Floorspace method: | Floorspace method: | 10% | 85%
|  | Boiler/ Hydronic (43.9%) |  |  |  | Central Plant (Chiller) (43.5%) | Single Duct CAV (53.4%)
|  | Package System / Heat Pump (40.8%) |  |  |  | Package System / Heat Pump (40.7%) | Fan Coil/Unit Ventilator (21.3%)
|  | Site method: |  |  |  | Site method: | Site method:
|  | Boiler/ Hydronic (6.8%) |  |  |  | Central Plant (Chiller) (6.5%) | Single Duct CAV (91.4%)
|  | Package System / Heat Pump (72.1%) |  |  |  | Package System / Heat Pump (71.5%) | Fan Coil/Unit Ventilator (5.7%)

## Ventilation
Outdoor Airflow Rate - Hospital
Space Type | Space/Thermal Zone | Number of People | Floor Area (ft²) | cfm/person [T24, 2025, Equation 120.1-F and Table 120.1-A] | cfm/ft² [T24, 2025, Equation 120.1-F and Table 120.1-A] | Required exhaust rate (cfm/ft) [T24, 2025, Table 120.1-B – minimum exhaust rates] | Min OA Ventilation Requirement (cfm/ft) [Table 4-A, 2022 California Mechanical Code] | Total cfm driven by people | Total cfm driven by area | Total cfm driven by exhaust | Total cfm | Note
Office Area (>250 square feet) | Basement | 201.2696 | 40253.93 | 15 | 0.15 |  | 0 | 3019.0447 | 6038.0895 |  | 6038.0895 |  | Outdoor Airflow Rate - Hospital
Corridor Area | Corridor_flr_1 | 30.628 | 6125.6 | 15 | 0.15 |  | 0 | 459.42 | 918.84 |  | 918.84 |  | Space Type | Total Area (ft²) | Min. occupancy load (persons/1000 ft²) | Total Number of Occupants | cfm/ft² (Table 120.1-A – Minimum Ventilation Rates) | Required Exhaust Rate-cfm/ft² (Table 120.1-B – Minimum Exhaust Rates) | Min OA Ventilation Requirement-ACH-(Table 4-A, 2022 California Mechanical Code) | Min OA Ventilation Requirement-cfm/ft²-(Table 4-A, 2022 California Mechanical Code) | cfm
Corridor Area | Corridor_flr_2 | 30.628 | 6125.6 | 15 | 0.15 |  | 0 | 459.42 | 918.84 |  | 918.84 |  | Office Area (>250 square feet) | 45504.62 | 5 | 227.5231 | 0.15 | 0 |  |  | 6825.693
Corridor Area | Corridor_flr_5 | 27.0026 | 5400.53 | 15 | 0.15 |  | 0 | 405.0397 | 810.0795 |  | 810.0795 |  | Corridor Area | 42054.13 | 5 | 210.2706 | 0.15 | 0 |  |  | 6308.1195
Corridor Area | Corridor_nw_flr_3 | 30.503 | 6100.6 | 15 | 0.15 |  | 0 | 457.545 | 915.09 |  | 915.09 |  | Dining Area (Cafeteria/Fast Food) | 7500.73 | 33 | 247.5241 | 0.15 | 0 |  |  | 3712.8614
Corridor Area | Corridor_nw_flr_4 | 30.503 | 6100.6 | 15 | 0.15 |  | 0 | 457.545 | 915.09 |  | 915.09 |  | Healthcare Facility and Hospitals (Exam/Treatment Room) | 4200.42 | 5 | 21.0021 |  | 0 | 2 | 0.46667 | 1960.196
Corridor Area | Corridor_se_flr_3 | 30.503 | 6100.6 | 15 | 0.15 |  | 0 | 457.545 | 915.09 |  | 915.09 |  | Healthcare Facility and Hospitals (Nurse's Station) | 62104.61 | 5 | 310.5231 |  | 0 | 2 | 0.46667 | 32119.1513 | *Negative pressure
Corridor Area | Corridor_se_flr_4 | 30.503 | 6100.6 | 15 | 0.15 |  | 0 | 457.545 | 915.09 |  | 915.09 |  | Healthcare Facility and Hospitals (Recovery Room) | 9427.61 | 5 | 47.1381 |  | 0 | 2 | 0.46667 | 4399.5513 | *Positive, No recirculation
Dining Area (Cafeteria/Fast Food) | Dining_flr_5 | 247.5241 | 7500.73 | 15 | 0.15 |  | 0 | 3712.8614 | 1125.1095 |  | 3712.8614 |  | Laboratory, Scientific | 0 | 5 | 0 |  | 1 | 2 | 0.46667 | 3000 | *Negative pressure
Healthcare Facility and Hospitals (Exam/Treatment Room) | Er_exam1_mult4_flr_1 | 1.5001 | 1200.12 | 15 | 0 |  | 0.46667 | 22.5022 | 560.056 |  | 560.056 |  | Healthcare Facility and Hospitals (Operating Room) | 6600.65 | 5 | 33.0033 |  |  | 4 | 0.93333 | 6160.6067
Healthcare Facility and Hospitals (Exam/Treatment Room) | Er_exam3_mult4_flr_1 | 1.5001 | 1200.12 | 15 | 0 |  | 0.46667 | 22.5022 | 560.056 |  | 560.056 |  | Healthcare Facility and Hospitals (Physical Therapy Room) | 5250.51 | 5 | 26.2525 |  |  | 2 | 0.46667 | 2450.238
Healthcare Facility and Hospitals (Nurse's Station) | Er_nursestn_lobby_flr_1 | 66.5065 | 13301.3 | 15 | 0 |  | 0.46667 | 997.5975 | 6207.2733 |  | 6207.2733 |  | Healthcare Facility and Hospitals (Imaging Room) | 5250.51 | 5 | 26.2525 |  |  | 2 | 0.46667 | 2450.238
Healthcare Facility and Hospitals (Exam/Treatment Room) | Er_trauma1_flr_1 | 1.5001 | 300.03 | 15 | 0 |  | 0.7 | 22.5022 | 210.021 |  | 210.021 |  | Healthcare Facility and Hospitals (Patient Room) | 20402.68 | 5 | 102.0134 |  |  | 2 | 0.46667 | 9521.2507
Healthcare Facility and Hospitals (Exam/Treatment Room) | Er_trauma2_flr_1 | 1.5001 | 300.03 | 15 | 0 |  | 0.7 | 22.5022 | 210.021 |  | 210.021 |  | Lobby, Main Entry | 15876.28 | 33 | 523.9172 | 0.15 |  |  |  | 7858.7586
Healthcare Facility and Hospitals (Exam/Treatment Room) | Er_triage_mult4_flr_1 | 1.5001 | 1200.12 | 15 | 0 | 3.0805 | 0.46667 | 22.5022 | 560.056 | 3697 | 3697 | According to CEC model, exhaust required | Kitchen/Food Preparation Area | 10000.98 | 3 | 30.0029 | 0.15 | 0.7 |  |  | 7000.686
Healthcare Facility and Hospitals (Recovery Room) | Icu_flr_2 | 33.2618 | 6652.36 | 15 | 0 |  | 0.46667 | 498.927 | 3104.4347 |  | 3104.4347 |  | Total | 234173.73 |  | 1805.423 |  |  |  |  | 93767.3505
Healthcare Facility and Hospitals (Nurse's Station) | Icu_nursestn_lobby_flr_2 | 35.9963 | 7199.26 | 15 | 0 |  | 0.46667 | 539.9445 | 3359.6547 |  | 3359.6547
Healthcare Facility and Hospitals (Recovery Room) | Ic_patroom1_mult5_flr_2 | 1.1251 | 1125.1 | 15 | 0 |  | 0.46667 | 16.8765 | 525.0467 |  | 525.0467
Healthcare Facility and Hospitals (Recovery Room) | Ic_patroom2_flr_2 | 1.5001 | 300.03 | 15 | 0 |  | 0.46667 | 22.5022 | 140.014 |  | 140.014
Healthcare Facility and Hospitals (Recovery Room) | Ic_patroom3_mult6_flr_2 | 1.1251 | 1350.12 | 15 | 0 |  | 0.46667 | 16.8765 | 630.056 |  | 630.056
Kitchen/Food Preparation Area | Kitchen_flr_5 | 30.0029 | 10000.98 | 15 | 0.15 | 0.7 |  | 450.0441 | 1500.147 | 7000.686 | 7000.686 | Exhaust required according to Code
Laboratory-General Health | Lab_flr_3 | 14.2514 | 2850.28 | 15 | 0 | 1 | 0.46667 | 213.771 | 1330.1307 | 2850.28 | 4350.28 | Exhaust required according to Code Per ASHRAE 62.1: Table 6.5-General Lab Exhaust
Laboratory-General Health | Lab_flr_4 | 14.2514 | 2850.28 | 15 | 0 | 1 | 0.46667 | 213.771 | 1330.1307 | 2850.28 | 4350.28 | Exhaust required according to Code Per ASHRAE 62.1: Table 6.5-General Lab Exhaust
Lobby, Main Entry | Lobby_records_flr_1 | 523.9172 | 15876.28 | 15 | 0.15 |  | 0 | 7858.7586 | 2381.442 | 0 | 7858.7586
Healthcare Facility and Hospitals (Nurse's Station) | Nursestn_lobby_flr_3 | 48.7548 | 9750.95 | 15 | 0 | 0.46672 | 0.46667 | 731.3212 | 4550.4433 | 4551 | 4551 | According to CEC Model
Healthcare Facility and Hospitals (Nurse's Station) | Nursestn_lobby_flr_4 | 48.7548 | 9750.95 | 15 | 0 | 0.46672 | 0.46667 | 731.3212 | 4550.4433 | 4551 | 4551 | According to CEC Model
Healthcare Facility and Hospitals (Nurse's Station) | Nursestn_lobby_flr_5 | 56.0054 | 11201.09 | 15 | 0 |  | 0.46667 | 840.0817 | 5227.1753 | 0 | 5227.1753
Office Area (>250 square feet) | Office1_flr_5 | 3.7513 | 750.27 | 15 | 0.15 |  | 0 | 56.2702 | 112.5405 | 0 | 112.5405
Office Area (>250 square feet) | Office1_mult5_flr_1 | 0.75005 | 750.05 | 15 | 0.15 |  | 0 | 11.2508 | 112.5075 | 0 | 112.5075
Office Area (>250 square feet) | Office2_mult5_flr_5 | 3.7504 | 3750.35 | 15 | 0.15 |  | 0 | 56.2553 | 562.5525 | 0 | 562.5525
Office Area (>250 square feet) | Office3_flr_5 | 3.7504 | 750.07 | 15 | 0.15 |  | 0 | 56.2553 | 112.5105 | 0 | 112.5105
Office Area (>250 square feet) | Office4_mult6_flr_5 | 0.75005 | 900.06 | 15 | 0.15 |  | 0 | 11.2508 | 135.009 | 0 | 135.009
Healthcare Facility and Hospitals (Operating Room) | Or1_flr_2 | 3.0003 | 600.06 | 15 | 0 |  | 0.93333 | 45.0045 | 560.056 | 0 | 560.056
Healthcare Facility and Hospitals (Operating Room) | Or2_mult5_flr_2 | 3.0003 | 3000.3 | 15 | 0 |  | 0.93333 | 45.0045 | 2800.2799 | 0 | 2800.2799
Healthcare Facility and Hospitals (Operating Room) | Or3_flr_2 | 3.0003 | 600.06 | 15 | 0 |  | 0.93333 | 45.0045 | 560.056 | 0 | 560.056
Healthcare Facility and Hospitals (Operating Room) | Or4_flr_2 | 12.0011 | 2400.23 | 15 | 0 |  | 0.93333 | 180.0172 | 2240.2146 | 0 | 2240.2146
Healthcare Facility and Hospitals (Nurse's Station) | Or_nursestn_lobby_flr_2 | 54.5053 | 10901.06 | 15 | 0 |  | 0.46667 | 817.5795 | 5087.1613 | 0 | 5087.1613
Healthcare Facility and Hospitals (Patient Room) | Patroom1_mult10_flr_3 | 1.1251 | 2250.2 | 15 | 0 |  | 0.46667 | 16.8765 | 1050.0933 | 0 | 1050.0933
Healthcare Facility and Hospitals (Patient Room) | Patroom1_mult10_flr_4 | 1.1251 | 2250.2 | 15 | 0 |  | 0.46667 | 16.8765 | 1050.0933 | 0 | 1050.0933
Healthcare Facility and Hospitals (Patient Room) | Patroom2_flr_3 | 1.8752 | 375.04 | 15 | 0 |  | 0.46667 | 28.128 | 175.0187 | 0 | 175.0187
Healthcare Facility and Hospitals (Patient Room) | Patroom2_flr_4 | 1.8752 | 375.04 | 15 | 0 |  | 0.46667 | 28.128 | 175.0187 | 0 | 175.0187
Healthcare Facility and Hospitals (Patient Room) | Patroom3_mult10_flr_3 | 1.0877 | 2175.4 | 15 | 0 |  | 0.46667 | 16.3155 | 1015.1867 | 0 | 1015.1867
Healthcare Facility and Hospitals (Patient Room) | Patroom3_mult10_flr_4 | 1.0877 | 2175.4 | 15 | 0 |  | 0.46667 | 16.3155 | 1015.1867 | 0 | 1015.1867
Healthcare Facility and Hospitals (Patient Room) | Patroom4_flr_3 | 1.8752 | 375.04 | 15 | 0 |  | 0.46667 | 28.128 | 175.0187 | 0 | 175.0187
Healthcare Facility and Hospitals (Patient Room) | Patroom4_flr_4 | 1.8752 | 375.04 | 15 | 0 |  | 0.46667 | 28.128 | 175.0187 | 0 | 175.0187
Healthcare Facility and Hospitals (Patient Room) | Patroom5_mult10_flr_3 | 1.1251 | 2250.2 | 15 | 0 |  | 0.46667 | 16.8765 | 1050.0933 | 0 | 1050.0933
Healthcare Facility and Hospitals (Patient Room) | Patroom5_mult10_flr_4 | 1.1251 | 2250.2 | 15 | 0 |  | 0.46667 | 16.8765 | 1050.0933 | 0 | 1050.0933
Healthcare Facility and Hospitals (Patient Room) | Patroom6_flr_3 | 1.5001 | 300.03 | 15 | 0 |  | 0.46667 | 22.5022 | 140.014 | 0 | 140.014
Healthcare Facility and Hospitals (Patient Room) | Patroom6_flr_4 | 1.5001 | 300.03 | 15 | 0 |  | 0.46667 | 22.5022 | 140.014 | 0 | 140.014
Healthcare Facility and Hospitals (Patient Room) | Patroom7_mult10_flr_3 | 1.0877 | 2175.4 | 15 | 0 |  | 0.46667 | 16.3155 | 1015.1867 | 0 | 1015.1867
Healthcare Facility and Hospitals (Patient Room) | Patroom7_mult10_flr_4 | 1.0877 | 2175.4 | 15 | 0 |  | 0.46667 | 16.3155 | 1015.1867 | 0 | 1015.1867
Healthcare Facility and Hospitals (Patient Room) | Patroom8_flr_3 | 1.5001 | 300.03 | 15 | 0 |  | 0.46667 | 22.5022 | 140.014 | 0 | 140.014
Healthcare Facility and Hospitals (Patient Room) | Patroom8_flr_4 | 1.5001 | 300.03 | 15 | 0 |  | 0.46667 | 22.5022 | 140.014 | 0 | 140.014
Healthcare Facility and Hospitals (Physical Therapy Room) | Phystherapy_flr_3 | 26.2526 | 5250.51 | 15 | 0 | 0.13999 | 0.46667 | 393.7883 | 2450.238 | 735 | 2450.238 | According to CEC Model
Healthcare Facility and Hospitals (Imaging Room) | Radiology_flr_4 | 26.2526 | 5250.51 | 15 | 0 |  | 0.46667 | 393.7883 | 2450.238 | 0 | 2450.238
Total (12 Space types) | Total ( 162 spaces) | 1705.1352 | 241524.4 | [7 empty] | 99856.498
**The CPUC Hospital prototype does not include any exhaust fans modeled in any of the spaces.
Exhaust Hood
Type of hood | Space | Max Exhaust Flow Rate (cfm/ft) [T24, 2025, Table 140.9-C] | Hood length (ft) | Hood Exhaust Rate (cfm) | Note | Source
Type I , wall-mounted canopy hoods | Kitchen/Food Preparation Area | 210 | 33.3366 | 7000.686 |  | T 24 2025, Table 140.9-C
Fume Hood | Laboratory-General Health | 250 | 6 | 1500 | ~1 fume hood per 2,500–3,000 ft² for hospital/clinical-type labs | 2019 High Efficiency Fume Hoods in Laboratory Spaces CASE Report
Fume Hood | Laboratory-General Health | 250 | 6 | 1500
*Efficiency of exhaust fan is 50% (according to ACM, 2025,section 5.7.3)
Background Data [To be deleted prior to publication]

## Thermostat
Thermostat Setpoints - Hospital
Setpoint | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16 | Source | Note
Health Heating Setpoint (F) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | T24 2022 - Appendix 5.4B | CEC and PNNL Healthcare-Hospital prototypes use the same setpoints without setbacks; however, the DEER model applies a 10° F setback from midnight to 5:00 AM.
Health Heating Setback (F) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
Health Cooling Setpoint (F) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
Health Cooling Setback (F) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
Kitchen Heating Setpoint (F) | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | PNNL 09.1, 2022 Restaurant prototype
Kitchen Heating Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Kitchen Cooling Setpoint (F) | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79
Kitchen Cooling Setback (F) | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86
UnOccupied Heating Setpoint (F) | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | T24 2022 - Appendix 5.4B
UnOccupied Heating Setback (F) | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66
UnOccupied Cooling Setpoint (F) | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79
UnOccupied Cooling Setback (F) | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79
Background Data [To be deleted prior to publication] | bar: CZ1 to CZ4
| Heating |  |  | Cooling
| Weekday | Saturday | Sunday | Weekday | Ssturday | Sunday
DEER | CZ1: 0:00 to 5:00; CZ2: 0:00 to 5:00; CZ3: 0:00 to 24:00; CZ4: 0:00 to 5:00; CZ5: 0:00 to 5:00; CZ6: 0:00 to 24:00
| 15.56 | 15.56 | 15.56 | 29.22 | 29.22 | 29.22
| 5:00 to 24:00 | 5:00 to 19:00 |  | 5:00 to 24:00 | 5:00 to 19:00
| 21.11 | 21.11 |  | 23.88 | 23.88
T24, Appendix JA5-4 : Occupant Controlled Smart Thermostat (OCST)
Kitchen Heating Setpoint (F) | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | PNNL 09.1, 2022 Restaurant prototype
Kitchen Heating Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Kitchen Cooling Setpoint (F) | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79
Kitchen Cooling Setback (F) | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86

## Water Heater
Water Heater - Hospital
Vintage | WH Type | Efficiency | Tank Volume (gal) | Tank Loss |  | Note
Existing | Gas | 0.8 | 143.773 | 1542.3745 | (Btu/hr)
New Construction | Gas | 0.8 | 143.773 | 1542.3745 | (Btu/hr)
Peak Hot Water Consumption
Space Name | Baseline WH Type [CEUS 2022] | Total Area (ft²) | Number of People | Hot Water Usage Specification (gal/hr per person) [T24, 2022, Appendix 5.4A , sheet: "2022 SpaceFuncData-Input"] | Peak Hot Water Usage (gal/hr) | Peak Hot Water Usage (gal/min)
Basement | Gas | 40253.93 | 201.2696 | 0.18 | 36.2285 | 0.60381
Corridor_flr_1 | Gas | 6125.6 | 30.628 | 0 | 0 | 0
Corridor_flr_2 | Gas | 6125.6 | 30.628 | 0 | 0 | 0
Corridor_flr_5 | Gas | 5400.53 | 27.0026 | 0 | 0 | 0
Corridor_nw_flr_3 | Gas | 6100.6 | 30.503 | 0 | 0 | 0
Corridor_nw_flr_4 | Gas | 6100.6 | 30.503 | 0 | 0 | 0
Corridor_se_flr_3 | Gas | 6100.6 | 30.503 | 0 | 0 | 0
Corridor_se_flr_4 | Gas | 6100.6 | 30.503 | 0 | 0 | 0
Dining_flr_5 | Gas | 7500.73 | 247.5241 | 0.578 | 143.0689 | 2.3845
Er_exam1_mult4_flr_1 | Gas | 300.03 | 1.5001 | 0.24 | 0.36004 | 0.0060006
Er_exam3_mult4_flr_1 | Gas | 300.03 | 1.5001 | 0.24 | 0.36004 | 0.0060006
Er_nursestn_lobby_flr_1 | Gas | 13301.3 | 66.5065 | 0.24 | 15.9616 | 0.26603
Er_trauma1_flr_1 | Gas | 300.03 | 1.5001 | 0.24 | 0.36004 | 0.0060006
Er_trauma2_flr_1 | Gas | 300.03 | 1.5001 | 0.24 | 0.36004 | 0.0060006
Er_triage_mult4_flr_1 | Gas | 300.03 | 1.5001 | 0.24 | 0.36004 | 0.0060006
Icu_flr_2 | Gas | 6652.36 | 33.2618 | 0.24 | 7.9828 | 0.13305
Icu_nursestn_lobby_flr_2 | Gas | 7199.26 | 35.9963 | 0.24 | 8.6391 | 0.14399
Ic_patroom1_mult5_flr_2 | Gas | 225.02 | 1.1251 | 0.24 | 0.27002 | 0.0045004
Ic_patroom2_flr_2 | Gas | 300.03 | 1.5001 | 0.24 | 0.36004 | 0.0060006
Ic_patroom3_mult6_flr_2 | Gas | 225.02 | 1.1251 | 0.24 | 0.27002 | 0.0045004
Kitchen_flr_5 | Gas | 10000.98 | 30.0029 | 0.578 | 17.3417 | 0.28903
Lab_flr_3 | Gas | 2850.28 | 14.2514 | 0.18 | 2.5653 | 0.042754
Lab_flr_4 | Gas | 2850.28 | 14.2514 | 0.18 | 2.5653 | 0.042754
Lobby_records_flr_1 | Gas | 15876.28 | 523.9172 | 0.09 | 47.1526 | 0.78588
Nursestn_lobby_flr_3 | Gas | 9750.95 | 48.7548 | 0.24 | 11.7011 | 0.19502
Nursestn_lobby_flr_4 | Gas | 9750.95 | 48.7548 | 0.24 | 11.7011 | 0.19502
Nursestn_lobby_flr_5 | Gas | 11201.09 | 56.0054 | 0.24 | 13.4413 | 0.22402
Office1_flr_5 | Gas | 750.27 | 3.7513 | 0.18 | 0.67524 | 0.011254
Office1_mult5_flr_1 | Gas | 150.01 | 0.75005 | 0.18 | 0.13501 | 0.0022501
Office2_mult5_flr_5 | Gas | 750.07 | 3.7504 | 0.18 | 0.67506 | 0.011251
Office3_flr_5 | Gas | 750.07 | 3.7504 | 0.18 | 0.67506 | 0.011251
Office4_mult6_flr_5 | Gas | 150.01 | 0.75005 | 0.18 | 0.13501 | 0.0022501
Or1_flr_2 | Gas | 600.06 | 3.0003 | 0.24 | 0.72007 | 0.012001
Or2_mult5_flr_2 | Gas | 600.06 | 3.0003 | 0.24 | 0.72007 | 0.012001
Or3_flr_2 | Gas | 600.06 | 3.0003 | 0.24 | 0.72007 | 0.012001
Or4_flr_2 | Gas | 2400.23 | 12.0011 | 0.24 | 2.8803 | 0.048005
Or_nursestn_lobby_flr_2 | Gas | 10901.06 | 54.5053 | 0.24 | 13.0813 | 0.21802
Patroom1_mult10_flr_3 | Gas | 225.02 | 1.1251 | 0.24 | 0.27002 | 0.0045004
Patroom1_mult10_flr_4 | Gas | 225.02 | 1.1251 | 0.24 | 0.27002 | 0.0045004
Patroom2_flr_3 | Gas | 375.04 | 1.8752 | 0.24 | 0.45005 | 0.0075008
Patroom2_flr_4 | Gas | 375.04 | 1.8752 | 0.24 | 0.45005 | 0.0075008
Patroom3_mult10_flr_3 | Gas | 217.54 | 1.0877 | 0.24 | 0.26105 | 0.0043508
Patroom3_mult10_flr_4 | Gas | 217.54 | 1.0877 | 0.24 | 0.26105 | 0.0043508
Patroom4_flr_3 | Gas | 375.04 | 1.8752 | 0.24 | 0.45005 | 0.0075008
Patroom4_flr_4 | Gas | 375.04 | 1.8752 | 0.24 | 0.45005 | 0.0075008
Patroom5_mult10_flr_3 | Gas | 225.02 | 1.1251 | 0.24 | 0.27002 | 0.0045004
Patroom5_mult10_flr_4 | Gas | 225.02 | 1.1251 | 0.24 | 0.27002 | 0.0045004
Patroom6_flr_3 | Gas | 300.03 | 1.5001 | 0.24 | 0.36004 | 0.0060006
Patroom6_flr_4 | Gas | 300.03 | 1.5001 | 0.24 | 0.36004 | 0.0060006
Patroom7_mult10_flr_3 | Gas | 217.54 | 1.0877 | 0.24 | 0.26105 | 0.0043508
Patroom7_mult10_flr_4 | Gas | 217.54 | 1.0877 | 0.24 | 0.26105 | 0.0043508
Patroom8_flr_3 | Gas | 300.03 | 1.5001 | 0.24 | 0.36004 | 0.0060006
Patroom8_flr_4 | Gas | 300.03 | 1.5001 | 0.24 | 0.36004 | 0.0060006
Phystherapy_flr_3 | Gas | 5250.51 | 26.2526 | 0.24 | 6.3006 | 0.10501
Radiology_flr_4 | Gas | 5250.51 | 26.2526 | 0.24 | 6.3006 | 0.10501
Total |  | 214116.18 | 1705.1352 |  | 359.4326 | 5.9905
Water Heater Capacity, Tank Capacity, and Tank Loss
WH Type | Peak Hot Water Usage (gal/hr) | Heat Output (Btu/hr) [ACM, 2025, 5.9.2: Rated capacity section] | WH Capacity (Btu/hr) [ACM, 2025, 5.9.2: Rated capacity section] | Required Energy Input (Btu/hr) | Storage Volume (gal) | Standby Loss |  | Off/On Cycle Loss Coefficient to Ambient Temp (Btu/h-F) | Source
Gas Storage WH | 359.4326 | 238309.5455 | 142985.7273 | 178732.1591 | 143.773 | 1542.3745 | Btu/hr | 23.0205 | Standby loss equation: Title 20, §1605.1 Table F-4 WH capacity equation: ACM, 2025, 5.9.2: Rated capacity section)
Electric resistance WH | 0 | 0 | 0 | 0 | 0 |  | %hr | 0
Total | 359.4326 | 238309.5455 | 142985.7273 | 178732.1591 | 143.773
Design supply temperature (F) | 135 | Ref: T24 2022 - Appendix 5.4B |  |  | Standby Loss for Existing | 1542.3745 | Btu/hr | 23.0205
Cold Water supply temperature (F) | 55 | Ref: ACM, 2025, 5.9.2: Rated capacity section
WH system factor | 0.6 | Ref: ACM, 2025, 5.9.2: Rated capacity section
Reheat multiplier | 0.4
* The 0.40 multiplier is a storage sizing factor used to account for the fact that the water heater doesn't need to store the full peak hour demand—it can reheat water during that time. This factor assumes that the heater will recover part of the hot water used during the peak hour, so only 40% of the peak hour demand needs to be stored at any given moment.
**For Gas Water Heater: UA(Btu/h-°F)​=Q˙​SL​ (Btu/h)/ΔT (∘F)​
Ambient temp | 68
Delta T | 67
** For Electric Water Heater: UA(Btu/h-°F)​= 0.0834 *SL​ (%/hr)*V gal
Background Data [To be deleted prior to publication]
Peak Hot Water Consumption
Space Type | Baseline WH Type [T24, 2022, Appendix 5.4A , sheet: "2022 SpaceFuncData-Input"] | Total Area (ft²) | Number of People | Hot Water Usage Specification (gal/hr per person) [T24, 2022, Appendix 5.4A , sheet: "2022 SpaceFuncData-Input"] | Peak Hot Water Usage (gal/hr) | Peak Hot Water Usage (gal/min)
Office Area (>250 square feet) | Electric | 45504.62 | 227.5231 | 0.18 | 40.9542 | 0.68257
Corridor Area | Electric | 42054.13 | 210.2706 | 0 | 0 | 0
Dining Area (Cafeteria/Fast Food) | Gas | 7500.73 | 247.5241 | 0.578 | 143.0689 | 2.3845
Healthcare Facility and Hospitals (Exam/Treatment Room) | Electric | 4200.42 | 21.0021 | 0.24 | 5.0405 | 0.084008
Healthcare Facility and Hospitals (Nurse's Station) | Gas | 62104.61 | 310.5231 | 0.24 | 74.5255 | 1.2421
Healthcare Facility and Hospitals (Recovery Room) | Gas | 9427.61 | 47.1381 | 0.24 | 11.3131 | 0.18855
Laboratory, Scientific | Gas | 0 | 0 | 0.18 | 0 | 0
Healthcare Facility and Hospitals (Operating Room) | Gas | 6600.65 | 33.0033 | 0.24 | 7.9208 | 0.13201
Healthcare Facility and Hospitals (Physical Therapy Room) | Electric | 5250.51 | 26.2525 | 0.24 | 6.3006 | 0.10501
Healthcare Facility and Hospitals (Imaging Room) | Gas | 5250.51 | 26.2525 | 0.24 | 6.3006 | 0.10501
Healthcare Facility and Hospitals (Patient Room) | Gas | 20402.68 | 102.0134 | 0.24 | 24.4832 | 0.40805
Lobby, Main Entry | Electric | 15876.28 | 523.9172 | 0.09 | 47.1526 | 0.78588
Kitchen/Food Preparation Area | Gas | 10000.98 | 30.0029 | 0.578 | 17.3417 | 0.28903
Total |  | 234173.73 | 1805.423 |  | 384.4017 | 6.4067

## Ext Lighting
Exterior Lighting - Hospital
Motion Controlled Luminaires (W) | Non-motion Controlled Luminaires (W) | Total (W) | Source
8349.061 | 1383.959 | 9733.02 | T24, 2022 & 2025 2019 Outdoor Lighting CASE report PNNL 90.1-2010 TSD
Exterior Lighting
Items (Assume LZ2) | Assumptions [2019 Outdoor Lighting CASE Report & PNNL 90.1-2010 TSD] |  | Unit | Lighting Power Allowance [T24, 2025, Table 140.7-A & 140.7-B] | Unit | Exterior Lighting Power (W)
IWA (Initial Wattage Allowance) |  |  |  | 200 | (W) | 200
Parking area | 400 ft² for every parking space 1 parking space per 830 ft² of gross building area | 386198 | (ft²) | 0.019 | (W/ft²) | 7337.762
Building Entrance | 14 building entrance per PNNL Model | 10 | (count) | 15 | (W/ea) | 150
Hardscape Ornamental Light | 0.1 ft² per 1 ft² of gross building area for hardscape ornamental light | 24137 | (ft²) | 0.007 | (W/ft²) | 168.959
Building façade | 0.1 W per 1 ft² of facade area Façade Area = Perimeter × 0.5 × 28 ft (30 ft is the max height that is lit) * The 0.5 factor assumes that only half of the perimeter walls are lit. -Formula ia developed based on the 2019 Outdoor Lighting CASE report | 12150 | (ft²) | 0.1 | (W/ft²) | 1215
Non-sales canopy |  | 4827 | (ft²) | 0.137 | (W/ft²) | 661.299
Motion Controlled Luminaires (W) | [5 empty] | 8349.061
Non-motion-controlled Luminaires | [5 empty] | 1383.959
Total | [5 empty] | 9733.02
Total floor area (ft²) | 241500 (230 ft x 175 ft for each floor)
Perimeter | 810
Floors | 3
Background Data [To be deleted prior to publication]

## Interior Lights
Interior Lighting - Hospital
Space Type | New Construction |  |  | Existing
| LPD (W/ft²) | Additional LPD for PorTable Lighting (W/ft²) | Source | LPD (W/ft²) | Additional LPD for PorTable Lighting (W/ft²) | Source
Office Area (>250 square feet) | 0.6 |  | T24, 2025, Table 140.6-C (Area category method) | 0.65 |  | T24, 2019, Table 140.6-C (Area category method)
Corridor Area | 0.4 |  |  | 0.6
Dining Area (Cafeteria/Fast Food) | 0.45 |  |  | 0.4
Healthcare Facility and Hospitals (Exam/Treatment Room) | 1.15 |  |  | 1.15
Healthcare Facility and Hospitals (Nurse's Station) | 0.85 |  |  | 0.75
Healthcare Facility and Hospitals (Recovery Room) | 0.9 |  |  | 0.9
Laboratory, Scientific | 0.9 |  |  | 1
Healthcare Facility and Hospitals (Operating Room) | 1.9 |  |  | 1.9
Healthcare Facility and Hospitals (Physical Therapy Room) | 0.75 |  |  | 0.85
Healthcare Facility and Hospitals (Imaging Room) | 0.6 |  |  | 1
Healthcare Facility and Hospitals (Patient Room) | 0.7 |  |  | 0.55
Lobby, Main Entry | 0.7 |  |  | 0.85
Kitchen/Food Preparation Area | 0.95 |  |  | 0.95
Office Area (<250 square feet) | 0.65 |  |  | 0.7

## Equipment
Equipment - Hospital
Spaces | Plug load Power Density (W/ft²) | Gas Power Density (Btu/hr-ft²) | Refrigeration Power Density (W/ft²) | Source | Note
Office Area (>250 square feet) | 0.7 |  |  | T24 2022 - Appendix 5.4A | Plug load and schedules project with CEC, 2025
Corridor Area | 0
Dining Area (Cafeteria/Fast Food) | 0.5 |  | 0.25 |  | CEC: Refrig Load = 0.25 w/ft²
Healthcare Facility and Hospitals (Exam/Treatment Room) | 1.5 | 1.1259 |  |  | Appendix 5.4A: Gas equipment=1.1259 Btu/h-ft²--CEC model (Hospital) has the Gas equipment for 3.59 Btu/h-ft²
Healthcare Facility and Hospitals (Nurse's Station) | 2 |  |  |  | PNNL has EPD=2 for Nurse station
Healthcare Facility and Hospitals (Recovery Room) | 1.5
Laboratory, Scientific | 2 |  |  |  | Appendix 5.4A: Gas equipment=13 Btu/h-ft²--CEC model (Hospital) has the Gas equipment for 51.7 Btu/h-ft²
Healthcare Facility and Hospitals (Operating Room) | 11 |  |  |  | PNNL has EPD=11 for Operating room--CEC: Gas equipment=3.62 Btu/h-ft²
Healthcare Facility and Hospitals (Physical Therapy Room) | 1.5
Healthcare Facility and Hospitals (Imaging Room) | 10 |  |  |  | PNNL has EPD=10 for Imaging room
Healthcare Facility and Hospitals (Patient Room) | 1.5
Lobby, Main Entry | 0.5
Kitchen/Food Preparation Area | 1.5 | 17.54 | 1.12 |  | Appendix 5.4A: Gas equipment=17.53768 --CEC model (Hospital) has the Gas equipment for 35.4 Btu/h-ft²) -- Btu/h-ft² CEC: Refrig Load = 1.12 W/ft²
Office Area (<250 square feet) | 0.7
Elevator
Vintage | No. of Elevators | Cab Lighting Power Limit | Lighting Shutoff | Cab Fan Control | Fan Power Limit | Regenerative Drive Threshold | Design load (w) | Note
Existing | 6 | 1.65 | n/a | n/a | n/a | n/a | 58131.4 | Design Load based on PNNL ASHRAE 90.1 2013 Hospital prototype
New Construction | 6 | ≤ 0.6 W/ft² of cab floor area- Exempt (covered process) | Automatic shut‑off after ≤ 5 min no‑occupancy | When the elevator cab is stopped and unoccupied with doors closed for over 15 minutes, the cab interior lighting and ventilation fans shall be switched off until elevator cab operation resumes. | ≤ 0.33 W per cfm of fan airflow | n/a | 35089.21 | Design Load based on PNNL ASHRAE 90.1 2022 Hospital prototype --- per T24 2025 §120.6 (f)
Assumptions for elevators:
One elevator for approximately 50,000 square feet in use.
For every two floors or two and a half floors, one more elevator was added.
An in-use rate of 70% for the floor area was assumed, based on engineering judgment.
Calculated number of Elevators: |  | 6 | Same as PNNL assumptions
Calculate Elevator load (kw)based on ACM 2022: |  | 60 | 30 kw is PNNL ASHRE 90.1 2022 elevator load (Lift,light and Fan)--CEC Model has 80K for the elevator load.
ACM 2022 suggestion for elevator load (kw): |  | 10
Elevator load will be defined as exterior load not equipment load (Same as PNNL ASHRAE 90.1 Large Hotel prototype).
Elevator Load= Elevator Lift+ Elevator Light | 2022 | 2019 | 2013
Elevator Lift (W) | 34667.95 | 57630.4 | 57630.4
Elevator Fan | 421.26 | 501 | 501
Elevator Light | 0.7 W/ft² | 1.5 w/ft² | 1.65 w/ft²
based on PNNL ASHRAE 90.1 Hospital prototype | 35089.21 | 58131.4 | 58131.4
Background Data [To be deleted prior to publication]

## Schedules
Schedules - Hospital
Zone | Schedule Category | Schedule | Source | Type | Hour
[5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | PNNL
All the zones | Health | Occupancy | T24 2022 - Appendix 5.4B, [Health] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0 | 0 |  | 0.349 | 0.349 | 0.349 | 0.349 | 0.349 | 0.349 | 0.349 | 0.682 | 0.877 | 0.877 | 0.877 | 0.877 | 0.877 | 0.877 | 0.877 | 0.877 | 0.584 | 0.584 | 0.584 | 0.584 | 0.584 | 0.584 | 0.524 | 0.349
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 |  | 0.349 | 0.349 | 0.349 | 0.349 | 0.349 | 0.349 | 0.349 | 0.487 | 0.633 | 0.633 | 0.633 | 0.633 | 0.633 | 0.633 | 0.633 | 0.633 | 0.633 | 0.633 | 0.349 | 0.349 | 0.349 | 0.349 | 0.349 | 0.349
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.262 | 0.262 | 0.262 | 0.262 | 0.262 | 0.262 | 0.262 | 0.262 | 0.349 | 0.349 | 0.349 | 0.349 | 0.349 | 0.349 | 0.349 | 0.349 | 0.262 | 0.262 | 0.262 | 0.262 | 0.262 | 0.262 | 0.262 | 0.262
All the zones | Health | Lights | T24 2022 - Appendix 5.4B, [Health] | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.45 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1
|  |  |  | Saturday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
All the zones | Health | ElecEquipment | T24 2022 - Appendix 5.4B, [Health] | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 |  | 0.349 | 0.349 | 0.349 | 0.349 | 0.349 | 0.349 | 0.349 | 0.682 | 0.877 | 0.877 | 0.877 | 0.877 | 0.877 | 0.877 | 0.877 | 0.877 | 0.584 | 0.584 | 0.584 | 0.584 | 0.584 | 0.584 | 0.524 | 0.349
|  |  |  | Saturday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 |  | 0.349 | 0.349 | 0.349 | 0.349 | 0.349 | 0.349 | 0.349 | 0.487 | 0.633 | 0.633 | 0.633 | 0.633 | 0.633 | 0.633 | 0.633 | 0.633 | 0.633 | 0.633 | 0.349 | 0.349 | 0.349 | 0.349 | 0.349 | 0.349
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 |  | 0.262 | 0.262 | 0.262 | 0.262 | 0.262 | 0.262 | 0.262 | 0.262 | 0.349 | 0.349 | 0.349 | 0.349 | 0.349 | 0.349 | 0.349 | 0.349 | 0.262 | 0.262 | 0.262 | 0.262 | 0.262 | 0.262 | 0.262 | 0.262
All the zones | Health | ServiceHotWater | T24 2022 - Appendix 5.4B, [Health] | Weekday | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.17 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.18 | 0.18 | 0.18 | 0.1 | 0.01 | 0.01
|  |  |  | Saturday | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.2 | 0.28 | 0.3 | 0.3 | 0.24 | 0.24 | 0.23 | 0.23 | 0.23 | 0.1 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
|  |  |  | Sunday | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
All the zones | Health | GasEquipment | T24 2022 - Appendix 5.4B, [Health] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.75 | 0.2 | 0.1 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
All the zones | Health | Refrigeration | T24 2022 - Appendix 5.4B, [Health] | Weekday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Saturday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Sunday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
Perimeter zones under Health category | Health | Infiltration | T24 2022 - Appendix 5.4B, [Health] | Weekday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1
|  |  |  | Saturday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1
|  |  |  | Sunday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
All the zones | Health | HVACAvail | T24 2022 - Appendix 5.4B, [Health] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
All the zones | Health | HtgSetpt |  | Weekday | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
|  |  |  | Saturday | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
|  |  |  | Sunday | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
All the zones | Health | ClgSetpt |  | Weekday | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
|  |  |  | Saturday | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
|  |  |  | Sunday | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
Health24/7 |  | Other
All the zones | Health24/7 | Occupancy | PNNL 2022 Hospital prototype | Weekday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4
|  |  |  | Saturday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
|  |  |  | Sunday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
All the zones | Health24/7 | Lights | PNNL 2022 Hospital prototype | Weekday | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45
|  |  |  | Saturday | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45
|  |  |  | Sunday | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45
All the zones | Health24/7 | ElecEquipment | PNNL 2022 Hospital prototype | Weekday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4
|  |  |  | Saturday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.8 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
|  |  |  | Sunday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
All the zones | Health24/7 | ServiceHotWater | PNNL 2022 Hospital prototype | Weekday | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 0.3
|  |  |  | Saturday | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
|  |  |  | Sunday | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
All the zones | Health24/7 | GasEquipment | CEC Hospital Update with changing 0 to 0.1 Or PNNL Gas Equip that is similar Elec? | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.75 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.75 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 |  | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4
|  |  |  | Saturday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 |  | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.8 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
|  |  |  | Sunday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 |  | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
All the zones | Health24/7 | Infiltration | Based on occupancy | Weekday | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  |  | Saturday | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  |  | Sunday | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
All the zones | Health24/7 | HVACAvail | PNNL 2022 Hospital prototype | Weekday | bar: Hour 1 to Hour 24
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
All the zones | Health24/7 | HtgSetpt |  | Weekday | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
|  |  |  | Saturday | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
|  |  |  | Sunday | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
All the zones | Health24/7 | ClgSetpt |  | Weekday | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
|  |  |  | Saturday | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
|  |  |  | Sunday | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
Patient24/7 (Differ only at lights from Health24/7) |  | Other
All the zones | Patient24/7 | Occupancy | PNNL 2022 Hospital prototype | Weekday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4
|  |  |  | Saturday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
|  |  |  | Sunday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
All the zones | Patient24/7 | Lights | PNNL 2022 Hospital prototype Modified by changing night load from 0.45 to 0.05 (almost off) | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.45 | 0.45 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.3 | 0.05 | 0.05 | Weekday | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.45 | 0.45 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.45 | 0.45 | 0.45 | 0.3 | 0.05 | 0.05 | Saturday | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.45 | 0.45 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.3 | 0.05 | 0.05 | AllOtherDays (incl. Sunday & Holidays) | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45
All the zones | Patient24/7 | ElecEquipment | PNNL 2022 Hospital prototype | Weekday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4
|  |  |  | Saturday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.8 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
|  |  |  | Sunday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
All the zones | Patient24/7 | ServiceHotWater | PNNL 2022 Hospital prototype | Weekday | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 0.3
|  |  |  | Saturday | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
|  |  |  | Sunday | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
All the zones | Patient24/7 | Infiltration | Based on occupancy | Weekday | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  |  | Saturday | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  |  | Sunday | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
All the zones | Patient24/7 | HVACAvail | PNNL 2022 Hospital prototype | Weekday | bar: Hour 1 to Hour 24
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
All the zones | Patient24/7 | HtgSetpt |  | Weekday | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
|  |  |  | Saturday | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
|  |  |  | Sunday | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
All the zones | Patient24/7 | ClgSetpt |  | Weekday | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
|  |  |  | Saturday | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
|  |  |  | Sunday | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
Unoccupied |  | Other
All the zones | Unoccupied | Occupancy |  | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
All the zones | Unoccupied | Lights |  | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weekday | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Saturday | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AllOtherDays (incl. Sunday & Holidays) | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45
All the zones | Unoccupied | ElecEquipment |  | Weekday | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
|  |  |  | Saturday | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
|  |  |  | Sunday | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
All the zones | Unoccupied | ServiceHotWater |  | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
All the zones | Unoccupied | Infiltration | Based on occupancy | Weekday | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  |  | Saturday | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  |  | Sunday | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
All the zones | Unoccupied | HVACAvail |  | Weekday | bar: Hour 1 to Hour 24
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
All the zones | Unoccupied | HtgSetpt |  | Weekday | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66
|  |  |  | Saturday | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66
|  |  |  | Sunday | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66
All the zones | Unoccupied | ClgSetpt |  | Weekday | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79
|  |  |  | Saturday | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79
|  |  |  | Sunday | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79
Office
Office | Office | Occupancy | T24 2022 - Appendix 5.4B, [Office] Updated base on Plug load and schedules project with CEC, 2025 | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
Office | Office | Lights | T24 2022 - Appendix 5.4B, [Office] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.35 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Office | Office | ElecEquipment | Plug load and schedules project with CEC, 2025 | Weekday | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.74 | 0.87 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.5 | 0.45 | 0.45 | 0.45
|  |  |  | Saturday | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43
|  |  |  | Sunday | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43
Office | Office | HVACAvail | T24 2022 - Appendix 5.4B, [Office] Updated base on Plug load and schedules project with CEC, 202 | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Office | Office | ServiceHotWater | T24 2022 - Appendix 5.4B, [Office] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.12 | 0.14 | 0.07 | 0.07 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05
|  |  |  | Sunday | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04
Office | Office | Infiltration | T24 2022 - Appendix 5.4B, [Office] Updated base on Plug load and schedules project with CEC, 202 | Weekday | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
Office | Office | HtgSetpt | Honeywell-INNCOM e7 Thermostat User Guide & Engineering Judgement | Weekday | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
|  |  |  | Saturday | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
|  |  |  | Sunday | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
Office | Office | ClgSetpt | Honeywell-INNCOM e7 Thermostat User Guide & Engineering Judgement | Weekday | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
|  |  |  | Saturday | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
|  |  |  | Sunday | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
Restaurant
Dining and Café | Restaurant | Occupancy | PNNL,ASHRAE 90.1, 2022 Fast Food Restaurant prototype (It has higher occupancy rate during morning compared to T24 2022 - Appendix 5.4B) | Weekday | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.4 | 0.4 | 0.4 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.8 | 0.8 | 0.8 | 0.5 | 0.35 | 0.2
|  |  |  | Saturday | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.4 | 0.2 | 0.45 | 0.5 | 0.5 | 0.35 | 0.3 | 0.3 | 0.3 | 0.7 | 0.9 | 0.7 | 0.65 | 0.55 | 0.35
|  |  |  | Sunday | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.3 | 0.2 | 0.25 | 0.35 | 0.55 | 0.65 | 0.7 | 0.35 | 0.2 | 0.2
Dining and Café | Restaurant | Lights | T24 2022 - Appendix 5.4B, [Restaurant] Updated based on the equipment schedule from the plug load and schedule project with CEC | Weekday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.3 | 0.67 | 0.73 | 0.75 | 0.85 | 0.85 | 0.85 | 0.83 | 0.72 | 0.65 | 0.67 | 0.75 | 0.85 | 0.85 | 0.85 | 0.75 | 0.57 | 0.3
|  |  |  | Saturday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.3 | 0.67 | 0.73 | 0.75 | 0.85 | 0.85 | 0.85 | 0.83 | 0.72 | 0.65 | 0.67 | 0.75 | 0.85 | 0.85 | 0.85 | 0.75 | 0.57 | 0.3
|  |  |  | Sunday | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.67 | 0.73 | 0.75 | 0.85 | 0.85 | 0.85 | 0.83 | 0.72 | 0.65 | 0.67 | 0.75 | 0.85 | 0.85 | 0.85 | 0.75 | 0.57 | 0.3
Dining and Café | Restaurant | ElecEquipment | Plug load and schedules project with CEC, 2025 | Weekday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.3 | 0.72 | 0.78 | 0.8 | 0.9 | 0.9 | 0.9 | 0.88 | 0.77 | 0.7 | 0.72 | 0.8 | 0.9 | 0.9 | 0.9 | 0.8 | 0.62 | 0.3
|  |  |  | Saturday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.3 | 0.72 | 0.78 | 0.8 | 0.9 | 0.9 | 0.9 | 0.88 | 0.77 | 0.7 | 0.72 | 0.8 | 0.9 | 0.9 | 0.9 | 0.8 | 0.62 | 0.3
|  |  |  | Sunday | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.72 | 0.78 | 0.8 | 0.9 | 0.9 | 0.9 | 0.88 | 0.77 | 0.7 | 0.72 | 0.8 | 0.9 | 0.9 | 0.9 | 0.8 | 0.62 | 0.3
Dining and Café | Restaurant | Refrigeration | T24 2022 - Appendix 5.4B, [Restaurant] | Weekday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Saturday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Sunday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
Dining and Café | Restaurant | HVACAvail | T24 2022 - Appendix 5.4B, [Restaurant] Updated based on the adopted PNNL occupancy | Weekday | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Saturday | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Sunday | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Dining and Café | Restaurant | ServiceHotWater | T24 2022 - Appendix 5.4B, [Restaurant] Updated based on the adopted PNNL occupancy | Weekday | 0.2 | 0 | 0 | 0 | 0 | 0.6 | 0.6 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25
|  |  |  | Saturday | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3
|  |  |  | Sunday | 0.25 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2
Dining and Café | Restaurant | Infiltration | T24 2022 - Appendix 5.4B, [Restaurant] Updated based on the adopted PNNL occupancy | Weekday | 0.25 | 0 | 0 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  |  | Saturday | 0.25 | 0 | 0 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  |  | Sunday | 0.25 | 0 | 0 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Dining and Café | Restaurant | HtgSetpt | T24 2022 - Appendix 5.4B, [Restaurant] | Weekday | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
|  |  |  | Saturday | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
|  |  |  | Sunday | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
Dining and Café | Restaurant | ClgSetpt | T24 2022 - Appendix 5.4B, [Restaurant] | Weekday | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
|  |  |  | Saturday | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
|  |  |  | Sunday | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
Kitchen
Kitchen | Kitchen | occupancy | PNNL,ASHRAE 90.1, 2022 Fast Food Restaurant prototype (It has higher occupancy rate during morning compared to T24 2022 - Appendix 5.4B) | Weekday | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.4 | 0.4 | 0.4 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.8 | 0.8 | 0.8 | 0.5 | 0.35 | 0.2
|  |  |  | Saturday | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.4 | 0.2 | 0.45 | 0.5 | 0.5 | 0.35 | 0.3 | 0.3 | 0.3 | 0.7 | 0.9 | 0.7 | 0.65 | 0.55 | 0.35
|  |  |  | Sunday | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.3 | 0.2 | 0.25 | 0.35 | 0.55 | 0.65 | 0.7 | 0.35 | 0.2 | 0.2
Kitchen | Kitchen | Lights | T24 2022 - Appendix 5.4B, [Restaurant] Updated based on the equipment schedule from the plug load and schedule project with CEC | Weekday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.3 | 0.67 | 0.73 | 0.75 | 0.85 | 0.85 | 0.85 | 0.83 | 0.72 | 0.65 | 0.67 | 0.75 | 0.85 | 0.85 | 0.85 | 0.75 | 0.57 | 0.3
|  |  |  | Saturday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.3 | 0.67 | 0.73 | 0.75 | 0.85 | 0.85 | 0.85 | 0.83 | 0.72 | 0.65 | 0.67 | 0.75 | 0.85 | 0.85 | 0.85 | 0.75 | 0.57 | 0.3
|  |  |  | Sunday | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.67 | 0.73 | 0.75 | 0.85 | 0.85 | 0.85 | 0.83 | 0.72 | 0.65 | 0.67 | 0.75 | 0.85 | 0.85 | 0.85 | 0.75 | 0.57 | 0.3
Kitchen | Kitchen | ElecEquipment | Plug load and schedules project with CEC, 2025 | Weekday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.3 | 0.72 | 0.78 | 0.8 | 0.9 | 0.9 | 0.9 | 0.88 | 0.77 | 0.7 | 0.72 | 0.8 | 0.9 | 0.9 | 0.9 | 0.8 | 0.62 | 0.3
|  |  |  | Saturday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.3 | 0.72 | 0.78 | 0.8 | 0.9 | 0.9 | 0.9 | 0.88 | 0.77 | 0.7 | 0.72 | 0.8 | 0.9 | 0.9 | 0.9 | 0.8 | 0.62 | 0.3
|  |  |  | Sunday | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.72 | 0.78 | 0.8 | 0.9 | 0.9 | 0.9 | 0.88 | 0.77 | 0.7 | 0.72 | 0.8 | 0.9 | 0.9 | 0.9 | 0.8 | 0.62 | 0.3
Kitchen | Kitchen | HVACAvail | T24 2022 - Appendix 5.4B , [Restaurant] Updated based on the adopted PNNL occupancy | Weekday | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Saturday | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Sunday | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Kitchen | Kitchen | ServiceHotWater | T24 2022 - Appendix 5.4B, [Restaurant] Updated based on the adopted PNNL occupancy | Weekday | 0.2 | 0 | 0 | 0 | 0 | 0.6 | 0.6 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25
|  |  |  | Saturday | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3
|  |  |  | Sunday | 0.25 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2
Kitchen | Kitchen | Infiltration | T24 2022 - Appendix 5.4B, [Restaurant] Updated based on the adopted PNNL occupancy | Weekday | 0.25 | 0 | 0 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  |  | Saturday | 0.25 | 0 | 0 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  |  | Sunday | 0.25 | 0 | 0 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Kitchen | Kitchen | ExhaustHoodEqualOrLessThan5000cfm | T24 2022 - Appendix 5.4B, [Restaurant] Updated based on the adopted PNNL occupancy | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
Kitchen | Kitchen | ExhaustHoodGreaterThan 5000cfm | T24 2022 - Appendix 5.4B, [Restaurant] Updated based on the adopted PNNL occupancy | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 0.5 | 1 | 0.5 | 1 | 0.5 | 1 | 0.5 | 1 | 0.5 | 1 | 0.5 | 1 | 0.5 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 0.5 | 1 | 0.5 | 1 | 0.5 | 1 | 0.5 | 1 | 0.5 | 1 | 0.5 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 0.5 | 1 | 0.5 | 1 | 0.5 | 1 | 0.5 | 1 | 0.5 | 1 | 0.5 | 0 | 0 | 0 | 0 | 0
Kitchen | Kitchen | Refrigeration | T24 2022 - Appendix 5.4B, [Restaurant] | Weekday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Saturday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Sunday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
Kitchen | Kitchen | GasEquipment | T24 2022 - Appendix 5.4B, [Restaurant] Updated based on the equipment schedule from the plug load and schedule project with CEC | Weekday | 0.5 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.75 | 0.75 | 0.75 | 0.9 | 0.9 | 0.9 | 0.9 | 0.75 | 0.5 | 0.5
|  |  |  | Saturday | 0.5 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.75 | 0.75 | 0.75 | 0.9 | 0.9 | 0.9 | 0.9 | 0.75 | 0.75 | 0.5
|  |  |  | Sunday | 0.5 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.75 | 0.75 | 0.75 | 0.9 | 0.9 | 0.9 | 0.9 | 0.75 | 0.5 | 0.5
Kitchen | Kitchen | HtgSetpt | Thermostat Setpoints of PNNL 09.1, 2022 Restaurant prototype and HVAC availability schedule of CEC Restaurant prototype | Weekday | 60 | 60 | 60 | 60 | 60 | 66 | 60 | 66 | 60 | 66 | 60 | 66 | 60 | 66 | 60 | 66 | 60 | 66 | 60 | 60 | 60 | 60 | 60 | 60
|  |  |  | Saturday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 66 | 60 | 66 | 60 | 66 | 60 | 66 | 60 | 66 | 60 | 66 | 60 | 60 | 60 | 60 | 60 | 60
|  |  |  | Sunday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 66 | 60 | 66 | 60 | 66 | 60 | 66 | 60 | 66 | 60 | 66 | 60 | 60 | 60 | 60 | 60 | 60
Kitchen | Kitchen | ClgSetpt | Thermostat Setpoints of PNNL 09.1, 2022 Restaurant prototype and HVAC availability schedule of CEC Restaurant prototype | Weekday | 86 | 86 | 86 | 86 | 86 | 79 | 86 | 79 | 86 | 79 | 86 | 79 | 86 | 79 | 86 | 79 | 86 | 79 | 86 | 86 | 86 | 86 | 86 | 86
|  |  |  | Saturday | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 79 | 86 | 79 | 86 | 79 | 86 | 79 | 86 | 79 | 86 | 79 | 86 | 86 | 86 | 86 | 86 | 86
|  |  |  | Sunday | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 79 | 86 | 79 | 86 | 79 | 86 | 79 | 86 | 79 | 86 | 79 | 86 | 86 | 86 | 86 | 86 | 86
Other |  | Other
| Building | Elevator | T24 2022 - Appendix 5.4B, [Health] Modified ( 0to 0.02 ) | Weekday | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.75 | 1 | 1 | 1 | 0.75 | 1 | 1 | 1 | 1 | 1 | 0.52 | 0.52 | 0.52 | 0.28 | 0.02 | 0.02
|  |  |  | Saturday | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.46 | 0.7 | 0.7 | 0.7 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.25 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
|  |  |  | Sunday | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
| Building | ExtLightingNonMotionCtrl | PNNL Hospital Prototype (2022) | Weekday | bar: Hour 1 to Hour 24
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
| Building | ExtLightingMotionCtrl | PNNL Hospital Prototype (2022) Modified to 0 for 11 pm to 5 am during weekday and 12 am to 5 am during weekend | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Office, Exam Room,Nurse Station, Recovery Room,Operating Room. Patient Room,Physical Therapy, Imaging Room, Lab | Building | FunctionalAreaPeopleActivityLevel | CEC Hospital Prototype | Weekday | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
|  |  |  | Saturday | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
|  |  |  | Sunday | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
Corridor, Lobby | Building | CommonAreaPeopleActivityLevel | CEC Hospital Prototype | Weekday | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5
|  |  |  | Saturday | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5
|  |  |  | Sunday | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5
Dining | Building | DiningAreaPeopleActivityLevel | CEC Hospital Prototype | Weekday | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2
|  |  |  | Saturday | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2
|  |  |  | Sunday | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2
Kitchen | Building | KitchenPeopleActivityLevel | CEC Hospital Prototype | Weekday | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8
|  |  |  | Saturday | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8
|  |  |  | Sunday | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8
Background Data [To be deleted prior to publication] | bar: Hour 1 to Hour 2

## Energy Usage
CalBEM Energy Consumption - Hospital | [11 empty] | Energy Consumption - Hospital
Prototype | CZ | CalBEM Electricity EUI (KBTU/ft²) | CalBEM Gas EUI (KBTU/ft²) | CalBEM Total EUI (KBTU/ft²) | New Construction Electricity EUI (KBTU/ft²) | New Construction Gas EUI (KBTU/ft²) | New Construction Total EUI (KBTU/ft²) | National Average | Acceptable Range (25% Higher) | Acceptable Range (25% Lower) | National Average Acceptable EUI Range | Prototype | CZ | Total Floorspace (Thousand of ft²) | CEUS 2023 Electricity EUI (kBtu/ft²) | CEUS 2023 Gas EUI (kBtu/ft²) | CEUS 2023 Total EUI (kBtu/ft²) | Acceptable Range (25% Higher) | Acceptable Range (25% Lower) | CEUS 2022 Acceptable EUI Range
Hospital | 1 | 70.3242 | 38.7616 | 109.0858 | 42.9782 | 51.87 | 94.8482 | 200.3 | 250.375 | 150.225 | 100.15 | Hospital | 1 | 7059 | 70.9802 | 51.1577 | 122.1379 | 152.6724 | 91.6034 | 61.069
| 2 | 79.336 | 37.5983 | 116.9342 | 47.2227 | 46.5726 | 93.7953 | 201.2 | 251.5 | 150.9 | 100.6 |  | 2 | 14514 | 45.6312 | 53.4755 | 99.1067 | 123.8834 | 74.33 | 49.5533
| 3 | 76.6817 | 33.3599 | 110.0415 | 45.3499 | 44.0713 | 89.4212 | 198.6 | 248.25 | 148.95 | 99.3 |  | 3 | 56689 | 53.4877 | 48.1605 | 101.6482 | 127.0603 | 76.2362 | 50.8241
| 4 | 83.7293 | 36.7665 | 120.4958 | 49.9437 | 46.1227 | 96.0664 | 206.8 | 258.5 | 155.1 | 103.4 |  | 4 | 29372 | 54.7559 | 50.1593 | 104.9152 | 131.1441 | 78.6864 | 52.4576
| 5 | 78.1843 | 34.3645 | 112.5488 | 45.9842 | 43.167 | 89.1512 | 198.3 | 247.875 | 148.725 | 99.15 |  | 5 | 5067 | 39.8282 | 24.8165 | 64.6447 | 80.8058 | 48.4835 | 32.3223
| 6 | 80.3527 | 26.8669 | 107.2196 | 48.6488 | 36.6229 | 85.2717 | 203.5 | 254.375 | 152.625 | 101.75 |  | 6 | 32891 | 54.9321 | 75.4764 | 130.4085 | 163.0106 | 97.8064 | 65.2042
| 7 | 79.9184 | 25.3371 | 105.2555 | 49.2997 | 35.9367 | 85.2364 | 205 | 256.25 | 153.75 | 102.5 |  | 7 | 31754 | 74.8437 | 45.4861 | 120.3298 | 150.4123 | 90.2474 | 60.1649
| 8 | 86.5402 | 28.9718 | 115.512 | 51.8295 | 36.5554 | 88.3849 | 210.8 | 263.5 | 158.1 | 105.4 |  | 8 | 50355 | 56.5439 | 86.9115 | 143.4554 | 179.3193 | 107.5916 | 71.7277
| 9 | 87.0605 | 29.677 | 116.7375 | 51.3758 | 37.713 | 89.0888 | 209.8 | 262.25 | 157.35 | 104.9 |  | 9 | 72118 | 45.2257 | 63.3727 | 108.5983 | 135.7479 | 81.4488 | 54.2992
| 10 | 86.0043 | 28.1172 | 114.1215 | 52.8601 | 38.2187 | 91.0788 | 213.4 | 266.75 | 160.05 | 106.7 |  | 10 | 55175 | 66.7723 | 63.834 | 130.6063 | 163.2578 | 97.9547 | 65.3031
| 11 | 84.2256 | 33.4555 | 117.6811 | 52.5844 | 46.6386 | 99.223 | 215.5 | 269.375 | 161.625 | 107.75 |  | 11 | 20961 | 67.7136 | 42.2205 | 109.9341 | 137.4176 | 82.4506 | 54.967
| 12 | 80.4518 | 34.0467 | 114.4985 | 49.4601 | 44.6424 | 94.1025 | 209.5 | 261.875 | 157.125 | 104.75 |  | 12 | 93863 | 69.3375 | 42.635 | 111.9726 | 139.9657 | 83.9794 | 55.9863
| 13 | 82.1957 | 29.6013 | 111.797 | 53.881 | 42.946 | 96.827 | 218.3 | 272.875 | 163.725 | 109.15 |  | 13 | 30306 | 75.5934 | 48.3022 | 123.8956 | 154.8695 | 92.9217 | 61.9478
| 14 | 89.3331 | 33.8993 | 123.2324 | 52.6566 | 45.283 | 97.9396 | 215.8 | 269.75 | 161.85 | 107.9 |  | 14 | 13400 | 63.1769 | 77.509 | 140.6859 | 175.8574 | 105.5144 | 70.3429
| 15 | 93.347 | 23.0556 | 116.4026 | 60.8365 | 35.5397 | 96.3762 | 238.3 | 297.875 | 178.725 | 119.15 |  | 15 | 24206 | 61.2178 | 63.6567 | 124.8745 | 156.0932 | 93.6559 | 62.4373
| 16 | 80.6018 | 38.8414 | 119.4432 | 46.5753 | 53.7864 | 100.3617 | 204.9 | 256.125 | 153.675 | 102.45 |  | 16 | 57915 | 72.2681 | 64.3832 | 136.6513 | 170.8142 | 102.4885 | 68.3257
Ref: CEUS 2022 Report
And converted FZ level data to CZ level
Background Data [To be deleted prior to publication]

## Weights
% of Floor Area per CZ and Vintage Bin - Hospital | [8 empty] | % of Floor Area per CZ and Vintage Bin - Hospital
Prototype | CZ | Vintage Bin | [6 empty] | Prototype | Vintage Bin | CZ
|  | Pre-1978 | 1978-1997 | 1998-2007 | 2008-2018 | Not available |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
Hospital | 1 | 36% | 16% | 16.6% | 26.2% | 5.3% | 100.1% |  | Hospital | Pre-1978 | 1.12% | 2.919% | 6.82% | 3.63% | 0.2223% | 7.73% | 4.831% | 12.28% | 18.69% | 7.763% | 3.037% | 13.22% | 4.041% | 2.362% | 2.829% | 8.496% | 100%
| 2 | 45.6% | 19% | 14.6% | 17.6% | 3.2% | 100% |  |  | 1978-1997 | 0.6987% | 1.71% | 13.06% | 6.671% | 1.602% | 4.795% | 8.381% | 6.421% | 7.967% | 12.06% | 2.998% | 14.9% | 2.586% | 2.144% | 5.385% | 8.62% | 100%
| 3 | 27.3% | 37.1% | 20.3% | 9.6% | 5.6% | 99.9% |  |  | 1998-2007 | 1.392% | 2.529% | 13.72% | 6.786% | 2.012% | 5.679% | 5.253% | 8.754% | 7.182% | 4.738% | 4.439% | 20.74% | 6.305% | 1.896% | 0.3351% | 8.248% | 100%
| 4 | 28% | 36.6% | 19.4% | 9.8% | 6.2% | 100% |  |  | 2008-2018 | 2.316% | 3.191% | 6.827% | 3.602% | 0.3474% | 1.198% | 3.303% | 1.018% | 5.246% | 10.97% | 5.645% | 22.56% | 9.719% | 2.003% | 5.748% | 16.3% | 100%
| 5 | 10% | 50.9% | 33.4% | 5.5% | 0.3% | 100.1% |  |  | Not available | 0.8497% | 1.057% | 7.312% | 4.143% | 0.03257% | 4.342% | 0.5391% | 9.096% | 15.21% | 12.32% | 2.277% | 10.04% | 8.941% | 3.187% | 9.693% | 10.97% | 100%
| 6 | 53.3% | 23.5% | 14.5% | 2.9% | 5.8% | 100% |  |  | Total | 1.185% | 2.437% | 9.518% | 4.932% | 0.8508% | 5.522% | 5.332% | 8.454% | 12.11% | 9.263% | 3.519% | 15.76% | 5.088% | 2.25% | 4.064% | 9.723% | 100%
| 7 | 34.5% | 42.5% | 13.9% | 8.3% | 0.7% | 99.9%
| 8 | 55.3% | 20.5% | 14.6% | 1.6% | 7.9% | 99.9%
| 9 | 58.8% | 17.8% | 8.4% | 5.8% | 9.2% | 100%
| 10 | 31.9% | 35.2% | 7.2% | 15.9% | 9.7% | 99.9%
| 11 | 32.9% | 23.1% | 17.8% | 21.5% | 4.7% | 100%
| 12 | 32% | 25.6% | 18.6% | 19.2% | 4.7% | 100.1%
| 13 | 30.3% | 13.8% | 17.5% | 25.6% | 12.9% | 100.1%
| 14 | 40% | 25.8% | 11.9% | 12% | 10.4% | 100.1%
| 15 | 26.5% | 35.9% | 1.2% | 19% | 17.5% | 100.1%
| 16 | 33.3% | 24% | 12% | 22.5% | 8.3% | 100.1%
| Statewide | 39.6% | 29% | 14.9% | 9.8% | 6.8% | 100.1%
Ref: CEUS 2022 dataset
% of Floor Area per CZ and Vintage Bin -
Prototype | CZ | Vintage Bin
|  | Pre-1978 | 1978-1997 | 1998-2007 | 2008-2018 | Not available
Hospital | 1 | 37.97% | 16.88% | 17.51% | 27.64% | 0% | 100% | 99.82%
| 2 | 47.11% | 19.63% | 15.08% | 18.18% | 0% | 100% | 99.9%
| 3 | 28.95% | 39.34% | 21.53% | 10.18% | 0% | 100% | 99.58%
| 4 | 29.85% | 39.02% | 20.68% | 10.45% | 0% | 100% | 99.62%
| 5 | 10.02% | 51% | 33.47% | 5.511% | 0% | 100% | 100.1%
| 6 | 56.58% | 24.95% | 15.39% | 3.079% | 0% | 100% | 99.66%
| 7 | 34.78% | 42.84% | 14.01% | 8.367% | 0% | 100% | 99.89%
| 8 | 60.11% | 22.28% | 15.87% | 1.739% | 0% | 100% | 99.27%
| 9 | 64.76% | 19.6% | 9.251% | 6.388% | 0% | 100% | 99.15%
| 10 | 35.37% | 39.02% | 7.982% | 17.63% | 0% | 100% | 98.95%
| 11 | 34.52% | 24.24% | 18.68% | 22.56% | 0% | 100% | 99.78%
| 12 | 33.54% | 26.83% | 19.5% | 20.13% | 0% | 100% | 99.88%
| 13 | 34.75% | 15.83% | 20.07% | 29.36% | 0% | 100% | 98.45%
| 14 | 44.59% | 28.76% | 13.27% | 13.38% | 0% | 100% | 99.03%
| 15 | 32.08% | 43.46% | 1.453% | 23% | 0% | 100% | 97.06%
| 16 | 36.27% | 26.14% | 13.07% | 24.51% | 0% | 100% | 99.42%
| Statewide | 42.44% | 31.08% | 15.97% | 10.5% | 0% | 100% | 99.64%

## PV (hidden)
PV - Hospital
TBD

## EV Charger (hidden)
EV Charger - Hospital
TBD
Background Data [To be deleted prior to publication]

## Data (hidden)
Space Function | Electric Equipment Load Intensity | Electric Equipment Load Intensity | LPD
Aging Eye/Low-vision (Corridor Area) |  |  | 2013 | 2016 | 2019 | 2025
Aging Eye/Low-vision (Dining)
Aging Eye/Low-vision (Lobby, Main Entry)
Aging Eye/Low-vision (Lounge/Waiting Area)
Aging Eye/Low-vision (Multipurpose Room)
Aging Eye/Low-vision (Religious Worship Area)
Aging Eye/Low-vision (Restroom)
Aging Eye/Low-vision (Stairwell)
Audience Seating Area
Auditorium Area
Auto Repair / Maintenance Area
Barber, Beauty Salon, Spa Area
Civic Meeting Place Area
Classroom, Lecture, Training, Vocational Areas
Concourse and Atria Area
Convention, Conference, Multipurpose and Meeting Area
Copy Room
Corridor Area
Dining Area (Bar/Lounge and Fine Dining)
Dining Area (Cafeteria/Fast Food)
Dining Area (Family and Leisure)
Electrical, Mechanical, Telephone Rooms
Exercise/Fitness Center and Gymnasium Areas
Financial Transaction Area
Healthcare Facility and Hospitals (Exam/Treatment Room)
Healthcare Facility and Hospitals (Imaging Room)
Healthcare Facility and Hospitals (Medical Supply Room)
Healthcare Facility and Hospitals (Nursery)
Healthcare Facility and Hospitals (Nurse's Station)
Healthcare Facility and Hospitals (Operating Room)
Healthcare Facility and Hospitals (Patient Room)
Healthcare Facility and Hospitals (Physical Therapy Room)
Healthcare Facility and Hospitals (Recovery Room)
Hotel Function Area
Kitchen/Food Preparation Area
Kitchenette or Residential Kitchen
Laboratory, Scientific
Laundry Area
Library (Reading Area)
Library (Stacks Area)
Lobby, Main Entry
Locker Room
Lounge, Breakroom, or Waiting Area
Manufacturing, Commercial & Industrial Work Area (Low Bay)
Manufacturing, Commercial & Industrial Work Area (High Bay)
Manufacturing, Commercial & Industrial Work Area (Precision)
Museum Area (Exhibition/Display)
Museum Area (Restoration Room)
Office Area (>250 square feet)
Office Area (<250 square feet)
Parking Garage Area (Parking Zone and Ramps)
Parking Garage Area (Daylight Adaptation Zones)
Pharmacy Area
Retail Sales Area (Grocery Sales)
Retail Sales Area (Retail Merchandise Sales)
Retail Sales Area (Fitting Room)
Religious Worship Area
Restrooms
Stairwell
Storage, Commercial/Industrial (Warehouse)
Storage, Commercial/Industrial (Refrigerated)
Storage, Commercial/Industrial (Shipping & Handling)
Storage (General)
Sports Arena - Playing Area (> 5,000 Spectators)
Sports Arena - Playing Area (2,000 - 5,000 Spectators)
Sports Arena - Playing Area (< 2,000 Spectators)
Sports Arena - Playing Area (Recreational)
Theater Area (Motion Picture)
Theater Area (Performance)
Transportation Function (Baggage Area)
Transportation Function (Ticketing Area)
Videoconferencing Studio
High-Rise Residential Living Spaces
Hotel/Motel Guest Room
All other
Attic
Reception Area
Elevator
Plenum
IT Room (EPD 12)
Computer Room (EPD 20)
Server Room (EPD 45)