## Notes
Data Sources
Dataset | Dodge 2023
CEUS 2022
ComStock 2023
Prototype | CEC Laboratory prototype (CBECC 2022.3.1) | https://bees.noresco.com/software2022.html
| DEER Manufacturing-BioTech prototype (June 2024) | https://github.com/sound-data/DEER-Prototypes-EnergyPlus
Codes | Title 24, part 6, referred to as T24 (1984, 2001, 2007, 2013, 2016, 2022, 2025)
ASHRAE 90.1 (2022)
CFR Title 10 (2008, 2010, 2025)
ACM 2022
| T24 2022 - Appendix 5.4A and Appendix 5.4B | https://www.energy.ca.gov/publications/2022/2022-nonresidential-and-multifamily-alternative-calculation-method-reference
Other | 2022 Reduced infiltration CASE report | https://title24stakeholders.com/wp-content/uploads/2020/10/2022-T24-Final-CASE-Report_Reduce-Infiltration.pdf
| 2019 Outdoor Lighting CASE Report | https://title24stakeholders.com/wp-content/uploads/2016/10/T24-2019-CASE-Study-Results-Report-Outdoor-Sources_Final_with-Attachments.pdf
| 2019 High Efficiency Fume Hoods in Laboratory Spaces CASE Report | https://title24stakeholders.com/wp-content/uploads/2017/09/2019-T24-CASE-Report_Fume-Hoods_Final_September-2017.pdf?
| PNNL 20405, 2010 | file:///N:/Prj_SUS/2023/S23668%20SCE%20CA%20Prototypes%20Development/Technical/NR/0_Input%20data/Lighting/PNNL-20405.pdf
| Air leakage Memo, NORESCO, 2025 | Infiltration_rate_report_14May2025-Short-Version.docx
| Proposed Updates to Equipment Power Densities and Building Schedules for the 2028 Energy Code, referred to as "Plug load and schedules project with CEC, 2025" (Docket Number =25-BSTD-03 & TN=265693) | https://efiling.energy.ca.gov/GetDocument.aspx?tn=265693&DocumentContentId=102545
Construction Rate
Notes
2025 T24 | Laboratory is a space or room where hazardous materials are used for activities such as testing, analysis, instruction, research, or developmental activities. Laboratory Suite is a Group L occupancy space within a building or structure, which may include multiple laboratories, offices, storage, equipment rooms or similar support functions. Laboratory, Scientific Area is a room or area where research, experiments, and measurement in medical and physical sciences are performed requiring examination of fine details. The area may include workbenches, countertops, scientific instruments, and associated floor spaces. Scientific laboratory does not refer to film, computer, and other laboratories where scientific experiments are not performed.

## Prototype
NORESCO, Updated August 2025
Laboratory
Characteristic | Value | Data Sources
Building Type | Laboratory
Building Category | Nonresidential
Vintages | 4 Vintages: Pre-1978 , 1978-1997 ,1998-2007 , 2008-2018 New Construction (2019+) | Based on the vintage bin analysis | NonRes-Vintage bins-Draft Report-30Nov2023-Final.docx
Shape | #VALUE! | The analysis uses prototype geometry originally developed by CEC.
Total Floor Area (ft²) | 53633 | Same as CEC
Aspect Ratio | 1.5 | Same as CEC
Number of Floors | 3 | Same as CEC
Roof type | Flat | Same as CEC
WWR | 33% | Same as CEC
Shading Geometry | No Shades | Same as CEC
Floor to floor height (feet) | 13 | Same as CEC
Floor to ceiling height (feet) | 9 (4 ft above-ceiling plenum) | Same as CEC
Glazing sill height (feet) | 3.35 ft (top of the window is 7.64 ft high with 4.29 ft high glass) | Same as CEC
Above grade wall area (ft²) | 21287.4627
Gross wall area (ft²) | 21287.4627
Roof area (ft²) | 17875.9489
Underground Gross Wall Area (ft²) | 0
Existing prototypes:
DEER Manufacturing-BioTech model |  | PNNL | CEC Lab Model
#VALUE! |  | n/a | #VALUE!
Total Floor Area (ft²) |  | 0 | 53633

## Zones
Proposed Layout - Laboratory
Space Type | Space/Thermal Zone | HVAC System Name/AHU Name | Schedule Category | Conditioned (Y/N) | Area Fraction | Area (ft²) | Volume (ft³) | Multipliers | Number of People | People (Persons/1,000 ft²) [T24, 2025,Table 120.1-A]
Laboratory, Scientific | Core_bottom | AHU-1 | Lab | Yes | 19.74% | 10587.74 | 95294.29 | 1 | 264.6935 | 25
Laboratory, Scientific | Core_mid | AHU-2 | Lab | Yes | 19.74% | 10587.74 | 95294.29 | 1 | 264.6935 | 25
Laboratory, Scientific | Core_top | AHU-3 | Lab | Yes | 19.74% | 10587.74 | 95294.29 | 1 | 264.6935 | 25
Plenum | Firstfloor_plenum | n/a | n/a | No | 33.33% | 17877.68 | 71514.2 | 1 | 0 | 0
Plenum | Midfloor_plenum | n/a | n/a | No | 33.33% | 17877.68 | 71514.2 | 1 | 0 | 0
Office Area (>250 square feet) | Perimeter_bot_zn_1 | AHU-1 | Office | Yes | 4.162% | 2231.98 | 20088.81 | 1 | 11.1599 | 5
Office Area (>250 square feet) | Perimeter_bot_zn_2 | AHU-1 | Office | Yes | 2.635% | 1413.04 | 12717.98 | 1 | 7.0652 | 5
Office Area (>250 square feet) | Perimeter_bot_zn_3 | AHU-1 | Office | Yes | 4.162% | 2231.98 | 20088.81 | 1 | 11.1599 | 5
Office Area (>250 square feet) | Perimeter_bot_zn_4 | AHU-1 | Office | Yes | 2.634% | 1412.94 | 12717.05 | 1 | 7.0647 | 5
Laboratory, Scientific | Perimeter_mid_zn_1 | AHU-2 | Lab | Yes | 4.162% | 2231.98 | 20088.81 | 1 | 55.7995 | 25
Laboratory, Scientific | Perimeter_mid_zn_2 | AHU-2 | Lab | Yes | 2.635% | 1413.04 | 12717.98 | 1 | 35.326 | 25
Laboratory, Scientific | Perimeter_mid_zn_3 | AHU-2 | Lab | Yes | 4.162% | 2231.98 | 20088.81 | 1 | 55.7995 | 25
Laboratory, Scientific | Perimeter_mid_zn_4 | AHU-2 | Lab | Yes | 2.634% | 1412.94 | 12717.05 | 1 | 35.3235 | 25
Office Area (>250 square feet) | Perimeter_top_zn_1 | AHU-3 | Office | Yes | 4.162% | 2231.98 | 20088.81 | 1 | 11.1599 | 5
Office Area (>250 square feet) | Perimeter_top_zn_2 | AHU-3 | Office | Yes | 2.635% | 1413.04 | 12717.98 | 1 | 7.0652 | 5
Office Area (>250 square feet) | Perimeter_top_zn_3 | AHU-3 | Office | Yes | 4.162% | 2231.98 | 20088.81 | 1 | 11.1599 | 5
Office Area (>250 square feet) | Perimeter_top_zn_4 | AHU-3 | Office | Yes | 2.634% | 1412.94 | 12717.05 | 1 | 7.0647 | 5
Plenum | Topfloor_plenum | n/a | n/a | No | 33.33% | 17877.68 | 71514.2 | 1 | 0 | 0
Total (2 Space types) | Total ( 18 spaces) | Total ( Thermal Zones) |  | Total (15 Conditioned zones) |  | 53633.04 |  |  | 1049.2284
Background Data [To be deleted prior to publication]
N

## Envelope
Envelope - Laboratory
Element | Prototype | Assembly Type | Construction | Thermal properties | Vintage | Selected T24 | Note | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
External Wall | Laboratory | ExtWall_MetalFramed_NonRes | Metal frame + insulation + Gypsum board | U-value IP | Pre 1978 | N/A | ASHRAE 90.1, 2022 Table A3.3.3.1, 3.5", R-0 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352
[5 empty] | 1978-1997 | 1986 | Similar to Low-rise office: Package A/ Heat Capacity was considered ~10 (BTU/F/ft²) | 0.21277 | 0.22727 | 0.22727 | 0.21739 | 0.25641 | 0.25641 | 0.25641 | 0.25641 | 0.25641 | 0.25641 | 0.2381 | 0.2381 | 0.2381 | 0.20833 | 0.20833 | 0.21277
[5 empty] | 1998-2007 | 2001 | Table 1-H | 0.182 | 0.182 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.098 | 0.062 | 0.082 | 0.062 | 0.062 | 0.098 | 0.098 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.06 | 0.055 | 0.071 | 0.055 | 0.055 | 0.06 | 0.06 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055
Roof | Laboratory | FlatRoof_WoodFramedAndOther_NonRes | Built-up Roof roof membrane+roof insulation+metal decking | U-value IP | Pre 1978 | N/A | Considering 30 years for roof/ insulation replacement. | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 1978-1997 | 1992 |  | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 1998-2007 | 2001 | Table 1-H | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.049 | 0.039 | 0.039 | 0.039 | 0.049 | 0.075 | 0.067 | 0.067 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038
Windows | Laboratory | FixedWindow_NonRes | Single pane | U-value IP | Pre 1978 | N/A | ASHRAE Handbook of Fundamentals (Table 4-Ch15) for single pane & T24, 2013 for double pane (33%-67%)* | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108
[5 empty] | 1978-1997 | N/A |  | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108
|  |  | Double pane |  | 1998-2007 | 2001 | Table 1-H | 0.49 | 0.49 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.34 | 0.36 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.36
| Laboratory | FixedWindow_NonRes | Single pane | SHGC | Pre 1978 | N/A | ASHRAE Handbook of Fundamentals (Table 10-Ch15) for single pane & T24, 2013 for double pane (33%-67%)* | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282
[5 empty] | 1978-1997 | N/A |  | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282
|  |  | Double pane |  | 1998-2007 | 2001 | Table 1-H - WWR:31-40% / SHGC non-north | 0.43 | 0.36 | 0.41 | 0.41 | 0.41 | 0.34 | 0.34 | 0.34 | 0.34 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.43
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.22 | 0.25 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.25
Infiltration
[5 empty] | Vintage | I_75 6-sdied Infiltration rate @ 75 pa | Note | I-design (cfm/ft²) (4-sided Infiltration rate at normal pressure) (Design flow rate approach and Flow/Exterior Wall Area calculation method)
|  |  |  | Infiltration | Pre 1978 | 1.1 | 2022 CASE report (Table 38) | 0.3301
[5 empty] | 1978-1997 | 1.1 | 2022 CASE report (Table 38) | 0.3301
[5 empty] | 1998-2007 | 1.1 | 2022 CASE report (Table 38) | 0.3301
[5 empty] | 2008-2018 | 1 | 2022 CASE report (Table 38) & T24, 2008-2016 (Table 140.3-B)--Air barrier is required in CZ 10-16 | 0.3021
[5 empty] | 2019+ | 0.6 | 2022 CASE report (Table 38) & T24, 2025 (Table 140.3-B)--Air barrier is required in all CZs | 0.1801
Source: T24 air barrier requirements (all editions) and the standardized infiltration rate reported in the 2022 CASE report and Dodge 2023 data
|  |  |  | Air Leakage Memo: |  | Infiltration_rate_report_14May2025-Short-Version.docx

## HVAC System
HVAC system - Laboratory
Vintage | Zones | Heating | Cooling | Air Distribution | Source | Note
Exisiting | Conditioned zones | Gas Boiler | DX | Multi zone VAV with hydronic reheat | Engineering Judgement | 100% outdoor air for labs, but no required energy recovery
New Construction | Conditioned zones | Central air-to-water HP | Central air-cooled Chiller | VAV ( Each zone has a chilled water or hot water changeover coil with a 6-way valve for cooling or heating) | T24 2025 ACM 2025, Table 2 and 3 | System 14a – Aircooled 4pipe VAV with Exhaust heat recovery
Efficiency of HVAC system
Vintage | Upgrade/Installed year | Air-Cooled Chiller | Gas Boiler | Air-to-Water HP | Sources | Note
Pre 1978 | 2008 | Air-cooled Chiller >150 Tons--2.8 COP, 3.05 IPLV | Gas-Fired Boiler ≥ 300,000 Btu/h and ≤ 2,500,000 Btu/h-- 80% Et | n/a | T24, Part 6, 2008 , Table 112-D (for Water Chilling Packages)
1978-1997
1998-2007
2008-2018 | 2013 | Air-cooled Chiller >150 Tons--≥ 9.562 EER, ≥ 12.500 IPLV | Gas-Fired Boiler ≥ 300,000 Btu/h and ≤ 2,500,000 Btu/h-- 80% Et | n/a | T24, Part 6, 2013 , Table 110.2-D (for Water Chilling Packages) -Table 110.2-k (for Gas Fired Boiler)
New Construction | 2025 | Air-cooled Chiller >150 Tons--≥ 10.100 EER, ≥ 14.000 IPLV | n/a | Air Cooled (Heating Mode) Split system and single package≥ 135,000 Btu/h and < 240,000 Btu/h 3.3 COP | T24, Part 6, 2013 , Table 110.2-D (for Water Chilling Packages) - Table 110.2-B (for HP efficiecny)
|  | * Et = Combustion efficiency | * Et = Thermal efficiency
Fan power
Vintage | Approach | System | Total Static Pressure (TSP) in w.c. (PNNL 20405, 2010, Table 5.11) | Fan Efficiency (ACM, 2025) | Fan Motor and Drive Efficiency [ACM 2025, Table 13] | W/cfm [ACM 2025, Table 14 and 15] | Data Source | Note
Existing | PNNL TSP | System 6 VAV >5,000 cfm | 5.58 | 0.65 | 0.9 |  | PNNL 2010 TSD
Brake horse power (bhp)=(Supply cfm*TSP in w.c.)/(6356*Fan efficiency)
Fan power (w/cfm) = bhp/motor and drive efficiency *746
New Construction | ACM 2025 | Multi Zone VAV System >5,000 cfm; < 10,000 cfm | 5.0491 | 0.65 | 0.9 | 1.013 | 2025 ACM
* 0.9 is an average fan efficiency according to ACM 2025, Table 13
Fan total eff (E+ input) = 0.65 x Motor_eff
TSP (E+ input) in w.c. = Motor_eff/746 x (6356 x Fan_eff) x W/cfm
Fan_eff=0.65
Background Data [To be deleted prior to publication]

## Thermostat
Thermostat Setpoints - Laboratory
Setpoint | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16 | Source
Lab Heating Setpoint (F) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | T24 2022 - Appendix 5.4B
Lab Heating Setback (F) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
Lab Cooling Setpoint (F) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
Lab Cooling Setback (F) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
Office Heating Setpoint (F) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
Office Heating Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Office Cooling Setpoint (F) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
Office Cooling Setback (F) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
Office Cooling Setback (F) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
Source: PNNL Healthcare-Outpaitiet prototype use this setpoints: Administration zones: 72°F Cooling/70°F Heating, Critical zones: 72°F Cooling/70°F Heating, Operating rooms: 65°F Cooling/65°F Heating
PNNL Healthcare-Outpaitiet prototype use this setbacks: 77°F Cooling/65°F Heating, Critical zones: no setback, Operating rooms: 72°F Cooling/65°F Heating

## Ventilation
Outdoor Airflow Rate - Laboratory
Space Type | Space/Thermal Zone | Number of People | Floor Area (ft²) | cfm/person (T24, 2025, Equation 120.1-F and Table 120.1-A) | cfm/ft² (T24, 2025, Equation 120.1-F and Table 120.1-A) | Required exhaust rate-CFM/ft²- (T24, part 6 2025, Table 120.1-B – minimum exhaust rates) | Total cfm driven by people | Total cfm driven by area | Total cfm driven by exhaust | Total cfm | Notes
Laboratory, Scientific | Core_bottom | 264.6935 | 10587.74 | 15 | 0.15 | 1 | 3970.4025 | 1588.161 | 10587.74 | 10587.74
Laboratory, Scientific | Core_mid | 264.6935 | 10587.74 | 15 | 0.15 | 1 | 3970.4025 | 1588.161 | 10587.74 | 10587.74
Laboratory, Scientific | Core_top | 264.6935 | 10587.74 | 15 | 0.15 | 1 | 3970.4025 | 1588.161 | 10587.74 | 10587.74
Plenum | Firstfloor_plenum | 0 | 17877.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Plenum | Midfloor_plenum | 0 | 17877.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Office Area (>250 square feet) | Perimeter_bot_zn_1 | 11.1599 | 2231.98 | 15 | 0.15 | 0 | 167.3985 | 334.797 | 0 | 334.797
Office Area (>250 square feet) | Perimeter_bot_zn_2 | 7.0652 | 1413.04 | 15 | 0.15 | 0 | 105.978 | 211.956 | 0 | 211.956
Office Area (>250 square feet) | Perimeter_bot_zn_3 | 11.1599 | 2231.98 | 15 | 0.15 | 0 | 167.3985 | 334.797 | 0 | 334.797
Office Area (>250 square feet) | Perimeter_bot_zn_4 | 7.0647 | 1412.94 | 15 | 0.15 | 0 | 105.9705 | 211.941 | 0 | 211.941
Laboratory, Scientific | Perimeter_mid_zn_1 | 55.7995 | 2231.98 | 15 | 0.15 | 1 | 836.9925 | 334.797 | 2231.98 | 2231.98
Laboratory, Scientific | Perimeter_mid_zn_2 | 35.326 | 1413.04 | 15 | 0.15 | 1 | 529.89 | 211.956 | 1413.04 | 1413.04
Laboratory, Scientific | Perimeter_mid_zn_3 | 55.7995 | 2231.98 | 15 | 0.15 | 1 | 836.9925 | 334.797 | 2231.98 | 2231.98
Laboratory, Scientific | Perimeter_mid_zn_4 | 35.3235 | 1412.94 | 15 | 0.15 | 1 | 529.8525 | 211.941 | 1412.94 | 1412.94
Office Area (>250 square feet) | Perimeter_top_zn_1 | 11.1599 | 2231.98 | 15 | 0.15 | 0 | 167.3985 | 334.797 | 0 | 334.797
Office Area (>250 square feet) | Perimeter_top_zn_2 | 7.0652 | 1413.04 | 15 | 0.15 | 0 | 105.978 | 211.956 | 0 | 211.956
Office Area (>250 square feet) | Perimeter_top_zn_3 | 11.1599 | 2231.98 | 15 | 0.15 | 0 | 167.3985 | 334.797 | 0 | 334.797
Office Area (>250 square feet) | Perimeter_top_zn_4 | 7.0647 | 1412.94 | 15 | 0.15 | 0 | 105.9705 | 211.941 | 0 | 211.941
Plenum | Topfloor_plenum | 0 | 17877.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total (2 Space types) | Total ( 18 spaces) | 1049.2284 | 53633.04 | [5 empty] | 39053.16 | 41240.142
Exhaust Hood
Type of hood | Space | Max Exhaust Flow Rate (cfm/ft) [T24, 2025, Table 140.9-C] | Hood length (ft) | Hood Exhaust Rate (cfm) | Note | Source
Fume Hood | Core_bottom | 250 | 10.5877 | 2646.935 | ~1 fume hood per 500–1,500 ft² for research or academic lab buildings | 2019 High Efficiency Fume Hoods in Laboratory Spaces CASE Report
Fume Hood | Core_mid | 250 | 10.5877 | 2646.935
Fume Hood | Core_top | 250 | 10.5877 | 2646.935
Fume Hood | Perimeter_mid_zn_1 | 250 | 2.232 | 557.995
Fume Hood | Perimeter_mid_zn_2 | 250 | 1.413 | 353.26
Fume Hood | Perimeter_mid_zn_3 | 250 | 2.232 | 557.995
Fume Hood | Perimeter_mid_zn_4 | 250 | 1.4129 | 353.235
*ANSI Z9.5 is the American National Standard for Laboratory Ventilation, and Section 6.4 focuses on how and where lab exhaust air must be discharged to ensure safety, health, and code compliance.
*2025 California Title 24, Part 6, the prescriptive exhaust requirements for laboratory spaces are detailed in Section 140.9(c).
Background Data [To be deleted prior to publication]
Requirement | Description | Criterion | Value / Standard
Airflow Modulation | Reduce to minimum 10 ACH or pressurization limit | Pressure relationship | Negative relative to adjacent spaces
Variable Exhaust/Makeup Air | Coordinated VAV systems for pressurization | Pressure differential target | 0.01–0.05 in. w.c.
Fan Power Limit | ≤ 0.65 W/CFM (standard); ≤ 0.85 W/CFM (with filtration) | Infiltration modeling | Not the primary OA source; modeled as tightly controlled
Sash Closure Controls | Auto-close after 5 min inactivity with safety features | Envelope air barrier | Required per T24 standards
Makeup Air Compliance | Must meet Section 140.4(o) standards | Standard reference | ANSI Z9.5-2022, ASHRAE 62.1, ASHRAE 90.1
Outdoor Airflow Rate - Laboratory
Space Type | Total ft² | Min. occupancy load (persons/1000 ft²) | Total Number of Occupants | cfm/ft² (Table 120.1-A – Minimum Ventilation Rates) | Required Exhaust Rate-CFM/ft² (Table 120.1-B – Minimum Exhaust Rates) | cfm | Source
Laboratory, Scientific | 0 | 25 | 0 | 0.15 | 1 | 0 | T24, 2025, Equation 120.1-F and Table 120.1-A
Office Area (>250 square feet) | 14579.88 | 5 | 72.8994 | 0.15 |  | 2186.982
Total | 14579.88 |  | 72.8994 |  |  | 2186.982

## Water Heater
Water Heater - Laboratory
Vintage | WH Type | Efficiency | Tank Volume (gal) | Tank Loss | Unit | Note
Existing | Gas | 0.8 | 75.5444 | 1073.4712 | (Btu/hr)
New Construction | Gas | 0.8 | 75.5444 | 1073.4712 | (Btu/hr)
Peak Hot Water Consumption
Space Name | Baseline WH Type [CEUS 2022] | Total Area (ft²) | Number of People | Hot Water Usage Specification (gal/hr per person) [T24, 2022, Appendix 5.4A , sheet: "2022 SpaceFuncData-Input"] | Peak Hot Water Usage (gal/hr) | Peak Hot Water Usage (gal/min)
Core_bottom | Gas | 10587.74 | 264.6935 | 0.18 | 47.6448 | 0.79408
Core_mid | Gas | 10587.74 | 264.6935 | 0.18 | 47.6448 | 0.79408
Core_top | Gas | 10587.74 | 264.6935 | 0.18 | 47.6448 | 0.79408
Firstfloor_plenum | Gas | 17877.68 | 0 | 0 | 0 | 0
Midfloor_plenum | Gas | 17877.68 | 0 | 0 | 0 | 0
Perimeter_bot_zn_1 | Gas | 2231.98 | 11.1599 | 0.18 | 2.0088 | 0.03348
Perimeter_bot_zn_2 | Gas | 1413.04 | 7.0652 | 0.18 | 1.2717 | 0.021196
Perimeter_bot_zn_3 | Gas | 2231.98 | 11.1599 | 0.18 | 2.0088 | 0.03348
Perimeter_bot_zn_4 | Gas | 1412.94 | 7.0647 | 0.18 | 1.2716 | 0.021194
Perimeter_mid_zn_1 | Gas | 2231.98 | 55.7995 | 0.18 | 10.0439 | 0.1674
Perimeter_mid_zn_2 | Gas | 1413.04 | 35.326 | 0.18 | 6.3587 | 0.10598
Perimeter_mid_zn_3 | Gas | 2231.98 | 55.7995 | 0.18 | 10.0439 | 0.1674
Perimeter_mid_zn_4 | Gas | 1412.94 | 35.3235 | 0.18 | 6.3582 | 0.10597
Perimeter_top_zn_1 | Gas | 2231.98 | 11.1599 | 0.18 | 2.0088 | 0.03348
Perimeter_top_zn_2 | Gas | 1413.04 | 7.0652 | 0.18 | 1.2717 | 0.021196
Perimeter_top_zn_3 | Gas | 2231.98 | 11.1599 | 0.18 | 2.0088 | 0.03348
Perimeter_top_zn_4 | Gas | 1412.94 | 7.0647 | 0.18 | 1.2716 | 0.021194
Topfloor_plenum | Gas | 17877.68 | 0 | 0 | 0 | 0
Total |  | 107266.08 | 1049.2284 |  | 188.8611 | 3.1477
Water Heater Capacity, Tank Capacity, and Tank Loss
WH Type | Peak Hot Water Usage (gal/hr) | Heat Output (Btu/hr) [ACM, 2025, 5.9.2: Rated capacity section] | WH Capacity (Btu/hr) [ACM, 2025, 5.9.2: Rated capacity section] | Required Energy Input (Btu/hr) | Storage Volume (gal) | Standby Loss | Unit | Off/On Cycle Loss Coefficient to Ambient Temp (Btu/h-F) | Source
Gas Storage WH | 188.8611 | 125217.939 | 75130.7634 | 93913.4543 | 75.5444 | 1073.4712 | Btu/hr | 16.022 | Standby loss equation: Title 20, §1605.1 Table F-4 WH capacity equation: ACM, 2025, 5.9.2: Rated capacity section)
Electric resistance WH | 0 | 0 | 0 | 0 | 0 |  | %/hr | 0
Total | 188.8611 | 125217.939 | 75130.7634 | 93913.4543 | 75.5444
Design supply temperature (F) | 135 | Ref: T24 2022 - Appendix 5.4B |  |  | Standby Loss for Existing | 1073.4712 | Btu/hr | 16.022
Cold Water supply temperature (F) | 55 | Ref: ACM, 2025, 5.9.2: Rated capacity section
WH system factor | 0.6 | Ref: ACM, 2025, 5.9.2: Rated capacity section
Reheat multiplier | 0.4
* The 0.40 multiplier is a storage sizing factor used to account for the fact that the water heater doesn't need to store the full peak hour demand—it can reheat water during that time. This factor assumes that the heater will recover part of the hot water used during the peak hour, so only 40% of the peak hour demand needs to be stored at any given moment.
**For Gas Water Heater: UA(Btu/h-°F)​=Q˙​SL​ (Btu/h)/ΔT (∘F)​
Ambient temp | 68
Delta T | 67
** For Electric Water Heater: UA(Btu/h-°F)​= 0.0834 *SL​ (%/hr)*V gal
Background Data [To be deleted prior to publication]

## Ext Lighting
Exterior Lighting - Laboratory
Motion Controlled Luminaires (W) | Non-motion Controlled Luminaires (W) | Total (W) | Source
1719.836 | 856.541 | 2576.377 | T24, 2022 & 2025 2019 Outdoor Lighting CASE report PNNL 90.1-2010 TSD
Exterior Lighting
Items (Assume LZ2) | Assumptions (2019 Outdoor Lighting CASE Report & PNNL 90.1-2010 TSD) |  | Unit | Lighting Power Allowance (T24, part 6, 2025, Table 140.7-A & 140.7-B) | Unit | Exterior Lighting Power (W)
IWA (Initial Wattage Allowance) |  |  |  | 200 | (W) | 200
Parking area | 400 ft² for every parking space 1 parking space per 830 ft² of gross building area | 85812.8 | (ft²) | 0.019 | (W/ft²) | 1244.88
Building Entrance | 14 building entrance per PNNL Model | 2 | (count) | 15 | (W/ea) | 30
Hardscape Ornamental Light | 0.1 ft² per 1 ft² of gross building area for hardscape ornamental light | 5363 | (ft²) | 0.007 | (W/ft²) | 37.541
Building façade | 0.1 W per 1 ft² of facade area Façade Area = Perimeter × 0.5 × 28 ft (30 ft is the max height that is lit) * The 0.5 factor assumes that only half of the perimeter walls are lit. -Formula ia developed based on the 2019 Outdoor Lighting CASE report | 8190 | (ft²) | 0.1 | (W/ft²) | 819
Non-sales canopy |  | 1788 | (ft²) | 0.137 | (W/ft²) | 244.956
Motion Controlled Luminaires (W) | [5 empty] | 1719.836
Non-motion-controlled Luminaires | [5 empty] | 856.541
Total | [5 empty] | 2576.377
Total floor area | 53633
Perimeter | 546
Floors | 3
Background Data [To be deleted prior to publication]

## Equipment
Equipment - Laboratory
Spaces | Plug load Intensity (W/ft²) | Gas Power Density (Btu/hr-ft²) | Refrigeration Power Density (W/ft²) | Source | Note
Laboratory, Scientific | 2 | 13 | 0.28 | T24 2022 - Appendix 5.4A | Appendix 5.4A: Gas equipment=13 Btu/h-ft²--CEC model (Lab) has the Gas equipment for 51 Btu/h-ft² and Refrig load for 0.28 w/ft²---CPUC supports this data
Office Area (>250 square feet) | 0.7 |  |  |  | Plug load and schedules project with CEC, 2025
Plenum | 0
Elevator
Vintage | No. of Elevators | Cab Lighting Power Density (W/ft²) | Lighting Shutoff | Cab Fan Control | Fan Power Limit (W/cfm) | Regenerative Drive Threshold | Design load (w) | Note
Existing | 3 | 1.65 | n/a | n/a | n/a | n/a | 16488.22 | Design Load based on PNNL ASHRAE 90.1 2013 Laboratory prototype
New Construction | 3 | 0.6 | Automatic shut‑off after ≤ 5 min no‑occupancy | When the elevator cab is stopped and unoccupied with doors closed for over 15 minutes, the cab interior lighting and ventilation fans shall be switched off until elevator cab operation resumes. | 0.33 | n/a | 8623.13 | Design Load based on PNNL ASHRAE 90.1 2022 Laboratory prototype --- per T24 2025 §120.6 (f)---Cab Lighting power density is Exempt (covered process)
Assumptions for elevators:
One elevator for approximately 50,000 square feet in use.
For every two floors or two and a half floors, one more elevator was added.
An in-use rate of 70% for the floor area was assumed, based on engineering judgment.
Calculated number of Elevators: |  | 3 | Same as PNNL assumptions
Calculate Elevator load (kw)based on ACM 2022: |  | 30
ACM 2022 suggestion for elevator load (kw): |  | 10
Elevator load will be defined as exterior load not equipment load
Elevator Load= Elevator Lift+ Elevator Light+Fan | 2022 | 2019 | 2013
Elevator Lift (W) | 8517.82 | 16363.22 | 16363.22
Elevator Fan | 105.31 | 125 | 125
Elevator Light | 0.7 W/ft² | 1.5 w/ft² | 1.65 w/ft²
based on PNNL ASHRAE 90.1 Office Medium prototype | 8623.13 | 16488.22 | 16488.22
Background Data [To be deleted prior to publication]

## Interior Lights
Interior Lighting - Laboratory
Space Type | New Construction |  |  | Existing
| Lighting density (W/ft²) | Additional lighting power for porTable lighting (W/ft²) | Source | LPD (W/ft²) | Additional LPD for PorTable Lighting (W/ft²) | Source
Laboratory, Scientific | 0.9 |  | T24, part 6, 2025, Table 140.6 C (Area category method) | 1.4 |  | T24, part 6, 2016, Table 140.6 C (Area category method)
Office Area (>250 square feet) | 0.6 |  |  | 0.75
Plenum | 0 |  |  | 0

## Schedules
Schedules - Laboratory
Zone | Schedule | Source | Zone | Type | Hour
[5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Level 2 and 3 Lab Zones | Lab | Occupancy | T24 2022 - Appendix 5.4B, [Lab] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.9 | 0.9 | 0.45 | 0.45 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Level 2 and 3 Lab Zones | Lab | Lights | T24 2022 - Appendix 5.4B, [Lab] | Weekday | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2
|  |  |  | Saturday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
|  |  |  | Sunday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Level 2 and 3 Lab Zones | Lab | ElecEquipment | T24 2022 - Appendix 5.4B, [Lab] | Weekday | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.5 | 0.7 | 0.8 | 0.5 | 0.6 | 0.7 | 0.9 | 0.8 | 0.5 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Level 2 and 3 Lab Zones | Lab | ServiceHotWater | T24 2022 - Appendix 5.4B, [Lab] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Level 2 and 3 Lab Zones | Lab | GasEquipment | T24 2022 - Appendix 5.4B, [Lab] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.9 | 0.9 | 0.45 | 0.45 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1 | 0.1 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0
Level 2 and 3 Lab Zones | Lab | Refrigeration | T24 2022 - Appendix 5.4B, [Lab] | Weekday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Saturday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Sunday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
Level 2 and 3 Lab Zones | Lab | Infiltration | T24 2022 - Appendix 5.4B, [Lab] | Weekday | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  |  | Saturday | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  |  | Sunday | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Level 2 and 3 Lab Zones | Lab | HVACAvail | T24 2022 - Appendix 5.4B, [Lab] | Weekday | bar: Hour 1 to Hour 24
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
Level 2 and 3 Lab Zones | Lab | ExhaustCAV | T24 2022 - Appendix 5.4B, [Lab] | Weekday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Saturday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Sunday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
Level 2 and 3 Lab Zones | Lab | ExhaustVAVManualSashCtrl | T24 2022 - Appendix 5.4B, [Lab] | Weekday | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.51 | 0.56 | 0.56 | 0.53 | 0.53 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.52 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  |  | Saturday | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.52 | 0.52 | 0.52 | 0.52 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  |  | Sunday | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.52 | 0.52 | 0.52 | 0.52 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Level 2 and 3 Lab Zones | Lab | ExhaustVAVAutoSashCtrl | T24 2022 - Appendix 5.4B, [Lab] | Weekday | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.21 | 0.22 | 0.33 | 0.33 | 0.26 | 0.26 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.24 | 0.21 | 0.21 | 0.21 | 0.2 | 0.2
|  |  |  | Saturday | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.21 | 0.21 | 0.24 | 0.24 | 0.24 | 0.24 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
|  |  |  | Sunday | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.21 | 0.21 | 0.24 | 0.24 | 0.24 | 0.24 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Office Zones | Lab | HtgSetpt | T24 2022 - Appendix 5.4B, [Office] | Weekday | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
|  |  |  | Saturday | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
|  |  |  | Sunday | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
Office Zones | Lab | ClgSetpt | T24 2022 - Appendix 5.4B, [Office] | Weekday | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
|  |  |  | Saturday | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
|  |  |  | Sunday | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
Office
Office Zones | Office | Occupancy | T24 2022 - Appendix 5.4B, [Office] Updated base on Plug load and schedules project with CEC, 2025 | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
Office Zones | Office | Lights | T24 2022 - Appendix 5.4B, [Office] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.35 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Office Zones | Office | ElecEquipment | Plug load and schedules project with CEC, 2025 | Weekday | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.74 | 0.87 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.5 | 0.45 | 0.45 | 0.45
|  |  |  | Saturday | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43
|  |  |  | Sunday | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43
Office Zones | Office | HVACAvail | T24 2022 - Appendix 5.4B, [Office] Updated base on Plug load and schedules project with CEC, 202 | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Office Zones | Office | ServiceHotWater | T24 2022 - Appendix 5.4B, [Office] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.12 | 0.14 | 0.07 | 0.07 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05
|  |  |  | Sunday | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04
Office Zones | Office | Infiltration | T24 2022 - Appendix 5.4B, [Office] Updated base on Plug load and schedules project with CEC, 202 | Weekday | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
Office Zones | Office | HtgSetpt | T24 2022 - Appendix 5.4B, [Office] | Weekday | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
|  |  |  | Saturday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  |  | Sunday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Office Zones | Office | ClgSetpt | T24 2022 - Appendix 5.4B, [Office] | Weekday | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
|  |  |  | Saturday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
|  |  |  | Sunday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
Other
| Building | Elevator | T24 2022 - Appendix 5.4B, [Lab] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Building | ExtLightingNonMotionCtrl |  | Weekday | bar: Hour 1 to Hour 24
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
| Building | ExtLightingMotionCtrl |  | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0
Background Data [To be deleted prior to publication] | bar: Hour 1 to Hour 2

## Energy Usage
CalBEM Energy Consumption - Laboratory | [11 empty] | Energy Consumption - Laboratory
Prototype | CZ | CalBEM Electricity EUI (KBTU/ft²) | CalBEM Gas EUI (KBTU/ft²) | CalBEM Total EUI (KBTU/ft²) | New Construction Electricity EUI (KBTU/ft²) | New Construction Gas EUI (KBTU/ft²) | New Construction Total EUI (KBTU/ft²) | National Average | Acceptable Range (25% Higher) | Acceptable Range (25% Lower) | National Average Acceptable EUI Range | Prototype | CZ | Total Floorspace (Thousand of ft²) | CEUS 2023 Electricity EUI (kBtu/ft²) | CEUS 2023 Gas EUI (kBtu/ft²) | CEUS 2023 Total EUI (kBtu/ft²) | Acceptable Range (20% Higher) | Acceptable Range (20% Lower) | CEUS 2022 Acceptable EUI Range
Laboratory | 1 | 53.8575 | 70.1975 | 124.055 | 53.56 | 23.04 | 76.6 | 135.3 | 169.125 | 101.475 | 67.65 | Laboratory | 1 |  |  |  |  | 0 | 0 | 0
| 2 | 60.3 | 62.895 | 123.195 | 58.43 | 22.57 | 81 | 135.3 | 169.125 | 101.475 | 67.65 |  | 2 |  |  |  |  | 0 | 0 | 0
| 3 | 58.4125 | 52.9175 | 111.33 | 53.43 | 22.21 | 75.64 | 135.3 | 169.125 | 101.475 | 67.65 |  | 3 |  |  |  |  | 0 | 0 | 0
| 4 | 64.845 | 59.3725 | 124.2175 | 62.68 | 22.39 | 85.07 | 135.3 | 169.125 | 101.475 | 67.65 |  | 4 |  |  |  |  | 0 | 0 | 0
| 5 | 58.9725 | 55.7775 | 114.75 | 54.53 | 21.88 | 76.41 | 135.3 | 169.125 | 101.475 | 67.65 |  | 5 |  |  |  |  | 0 | 0 | 0
| 6 | 64.785 | 39.7125 | 104.4975 | 55.44 | 21.23 | 76.67 | 135.3 | 169.125 | 101.475 | 67.65 |  | 6 |  |  |  |  | 0 | 0 | 0
| 7 | 65.2925 | 38.7675 | 104.06 | 55.62 | 21.15 | 76.77 | 135.3 | 169.125 | 101.475 | 67.65 |  | 7 |  |  |  |  | 0 | 0 | 0
| 8 | 68.7675 | 41.7525 | 110.52 | 60.21 | 21.33 | 81.54 | 135.3 | 169.125 | 101.475 | 67.65 |  | 8 |  |  |  |  | 0 | 0 | 0
| 9 | 68.185 | 43.0275 | 111.2125 | 60.35 | 21.45 | 81.8 | 135.3 | 169.125 | 101.475 | 67.65 |  | 9 |  |  |  |  | 0 | 0 | 0
| 10 | 69.5925 | 43.5075 | 113.1 | 62.98 | 21.49 | 84.47 | 135.3 | 169.125 | 101.475 | 67.65 |  | 10 |  |  |  |  | 0 | 0 | 0
| 11 | 69.5675 | 56.075 | 125.6425 | 65.31 | 22.97 | 88.28 | 135.3 | 169.125 | 101.475 | 67.65 |  | 11 |  |  |  |  | 0 | 0 | 0
| 12 | 64.3525 | 56.4075 | 120.76 | 60.78 | 22.46 | 83.24 | 135.3 | 169.125 | 101.475 | 67.65 |  | 12 |  |  |  |  | 0 | 0 | 0
| 13 | 70.1525 | 50.3725 | 120.525 | 65.49 | 22.32 | 87.81 | 135.3 | 169.125 | 101.475 | 67.65 |  | 13 |  |  |  |  | 0 | 0 | 0
| 14 | 70.1475 | 55.1375 | 125.285 | 67.95 | 22.5 | 90.45 | 135.3 | 169.125 | 101.475 | 67.65 |  | 14 |  |  |  |  | 0 | 0 | 0
| 15 | 84.175 | 36.5875 | 120.7625 | 75.24 | 21.33 | 96.57 | 135.3 | 169.125 | 101.475 | 67.65 |  | 15 |  |  |  |  | 0 | 0 | 0
| 16 | 59.1625 | 66.8025 | 125.965 | 67.03 | 23.99 | 91.02 | 135.3 | 169.125 | 101.475 | 67.65 |  | 16 |  |  |  |  | 0 | 0 | 0
Ref: CEUS 2022 Report
And converted FZ level data to CZ level
CEUS has only one category for healthcare.

## Weights (hidden)
% of Floor Area per CZ and Vintage Bin - Laboratory | [7 empty] | % of Floor Area per CZ and Vintage Bin - Laboratory
Prototype | CZ | Vintage Bin | [5 empty] | Prototype | Vintage Bin | CZ
|  | Pre-1978 | 1978-1997 | 1998-2007 | 2008-2018 | Not available |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
Laboratory | 1 | [5 empty] | 0% | Laboratory | Pre-1978 | [16 empty] | 0%
| 2 | [5 empty] | 0% |  | 1978-1997 | [16 empty] | 0%
| 3 | [5 empty] | 0% |  | 1998-2007 | [16 empty] | 0%
| 4 | [5 empty] | 0% |  | 2008-2018 | [16 empty] | 0%
| 5 | [5 empty] | 0% |  | Not available | [16 empty] | 0%
| 6 | [5 empty] | 0% |  | Total
| 7 | [5 empty] | 0%
| 8 | [5 empty] | 0%
| 9 | [5 empty] | 0%
| 10 | [5 empty] | 0%
| 11 | [5 empty] | 0%
| 12 | [5 empty] | 0%
| 13 | [5 empty] | 0%
| 14 | [5 empty] | 0%
| 15 | [5 empty] | 0%
| 16 | [5 empty] | 0%
Statewide
Ref: CEUS 2022 dataset
Background Data [To be deleted prior to publication]

## PV (hidden)
PV - Laboratory
TBD

## EV Charger (hidden)
EV Charger - Laboratory
TBD
Background Data [To be deleted prior to publication]

## Data (hidden)
Space Function | Exhaust Required? | Electric Equipment Load Intensity | Electric Equipment Load Intensity | LPD
Aging Eye/Low-vision (Corridor Area) |  |  |  | 2013 | 2016 | 2019 | 2025
Aging Eye/Low-vision (Dining)
Aging Eye/Low-vision (Lobby, Main Entry)
Aging Eye/Low-vision (Lounge/Waiting Area)
Aging Eye/Low-vision (Multipurpose Room)
Aging Eye/Low-vision (Religious Worship Area)
Aging Eye/Low-vision (Restroom)
Aging Eye/Low-vision (Stairwell)
Audience Seating Area
Auditorium Area
Auto Repair / Maintenance Area
Barber, Beauty Salon, Spa Area
Civic Meeting Place Area
Classroom, Lecture, Training, Vocational Areas
Concourse and Atria Area
Convention, Conference, Multipurpose and Meeting Area
Copy Room | Yes
Corridor Area
Dining Area (Bar/Lounge and Fine Dining)
Dining Area (Cafeteria/Fast Food)
Dining Area (Family and Leisure)
Electrical, Mechanical, Telephone Rooms
Exercise/Fitness Center and Gymnasium Areas
Financial Transaction Area
Healthcare Facility and Hospitals (Exam/Treatment Room)
Healthcare Facility and Hospitals (Imaging Room)
Healthcare Facility and Hospitals (Medical Supply Room)
Healthcare Facility and Hospitals (Nursery)
Healthcare Facility and Hospitals (Nurse's Station)
Healthcare Facility and Hospitals (Operating Room)
Healthcare Facility and Hospitals (Patient Room)
Healthcare Facility and Hospitals (Physical Therapy Room)
Healthcare Facility and Hospitals (Recovery Room)
Hotel Function Area
Kitchen/Food Preparation Area | Yes
Kitchenette or Residential Kitchen | Yes
Laboratory, Scientific | Yes
Laundry Area | Yes
Library (Reading Area)
Library (Stacks Area)
Lobby, Main Entry
Locker Room | Yes
Lounge, Breakroom, or Waiting Area
Manufacturing, Commercial & Industrial Work Area (Low Bay)
Manufacturing, Commercial & Industrial Work Area (High Bay)
Manufacturing, Commercial & Industrial Work Area (Precision)
Museum Area (Exhibition/Display)
Museum Area (Restoration Room)
Office Area (>250 square feet)
Office Area (<250 square feet)
Parking Garage Area (Parking Zone and Ramps)
Parking Garage Area (Daylight Adaptation Zones)
Pharmacy Area
Retail Sales Area (Grocery Sales)
Retail Sales Area (Retail Merchandise Sales)
Retail Sales Area (Fitting Room)
Religious Worship Area
Restrooms
Stairwell
Storage, Commercial/Industrial (Warehouse)
Storage, Commercial/Industrial (Refrigerated)
Storage, Commercial/Industrial (Shipping & Handling)
Storage (General)
Sports Arena - Playing Area (> 5,000 Spectators)
Sports Arena - Playing Area (2,000 - 5,000 Spectators)
Sports Arena - Playing Area (< 2,000 Spectators)
Sports Arena - Playing Area (Recreational)
Theater Area (Motion Picture)
Theater Area (Performance)
Transportation Function (Baggage Area)
Transportation Function (Ticketing Area)
Videoconferencing Studio
High-Rise Residential Living Spaces
Hotel/Motel Guest Room
All other
Attic
Reception Area
Elevator
Plenum
IT Room (EPD 12)
Computer Room (EPD 20)
Server Room (EPD 45)