## Notes
Data Sources
Dataset | Dodge 2023
CEUS 2022
CBECS 2018
ComStock 2023
Prototype | CEC prototype (CBECC 2022.3.1) | https://bees.noresco.com/software2022.html
| PNNL prototype (90.1-2022) | https://www.energycodes.gov/prototype-building-models#Commercial
| DEER prototype (June 2023) | https://github.com/sound-data/DEER-Prototypes-EnergyPlus
| ORNL 2019 Large Office prototype zoning | https://www.sciencedirect.com/science/article/abs/pii/S0306261920312186
https://publications.ibpsa.org/proceedings/simbuild/2020/papers/simbuild2020_C064.pdf
| Massachusetts Large Office prototype | https://www.mass.gov/doc/large-office-prototype-basis-of-design-report/download
Codes | Title 24, part 6, referred to as T24 (1984, 2001, 2008, 2010, 2013, 2022, 2025)
ASHRAE 90.1 (2022)
CFR Title 10 (2010, 2024)
Others | ACM (2022)
| Title 24, 2022 - Appendix 5.4A and Appendix 5.4B | https://www.energy.ca.gov/publications/2022/2022-nonresidential-and-multifamily-alternative-calculation-method-reference
| 2022 Reduced infiltration CASE report | https://title24stakeholders.com/wp-content/uploads/2020/10/2022-T24-Final-CASE-Report_Reduce-Infiltration.pdf
| 2019 Outdoor Lighting CASE Report | https://title24stakeholders.com/wp-content/uploads/2016/10/T24-2019-CASE-Study-Results-Report-Outdoor-Sources_Final_with-Attachments.pdf
| PNNL 20405, 2010 | https://www.pnnl.gov/main/publications/external/technical_reports/PNNL-20405.pdf
| Air leakage Memo, NORESCO, 2025 | Infiltration_rate_report_14May2025-Short-Version.docx
| Proposed Updates to Equipment Power Densities and Building Schedules for the 2028 Energy Code, referred to as "Plug load and schedules project with CEC, 2025" (Docket Number =25-BSTD-03 & TN=265693) | https://efiling.energy.ca.gov/GetDocument.aspx?tn=265693&DocumentContentId=102545
Construction Rate
Total Floor area (thousands of sf)
[5 empty] | Pre-1978 | 1978-1997 | 1998-2007 | 2008-2018 | 2019-2022
[5 empty] | New Construction (2019+) | 248465.9 | 93016.2 | 62305.7 | 27851.1
Source: Dodge 2023 data ( NEW large office built after 1967)
Notes
Large office building is defined as any office building with a total area >150,000 sf, by analyzing Dodge 2023 data.
Large office buildings cover approximately 52% of the floor area and 7% of the total number of the CA office buildings (according to the Dodge 2023 datasets).
Only 2% of offices in CA have stories >6 and area <150,000. (according to the Dodge 2023 datasets)
Analysis of the Dodge 2023 dataset (see table and chart below) shows that the median and average number of stories and total floor area (not footprint of each story) are considerably smaller than those represented in the existing prototypes developed by PNNL and CBECC. This suggests that a smaller prototype might better reflect the California building stock. However, we have chosen to continue using the existing prototype floor area and number of stories for the following reasons:
- Developing a smaller prototype would make the CEC prototype different from national Large Office prototype.
- Change would likely have little impact on energy consumption on a per sf basis (kBTU/sf), nor would it result in different HVAC system design .
| Statical Analysis of the CA Large Office Building Stock (STC:7,305,405 & floor area>150 ksf) | No. of Stories | Footprint (sf) | Total Area (sf)
| Median | 6 | 40000 | 250000
| Average | 9 | 35555 | 320000
Source: Dodge 2023 data ( NEW large office buildings built after 1967)
| Existing Large Office Prototype | No. of Stories | Footprint* (sf) | Total Area (sf)
| CBECC (CEC) 2022 | 13 | 38400 | 498000
| PNNL ASHRAE 90.1 2022 | 13 | 38400 | 498000
| DEER (CPUC) 2024 | 10 | 17500 | 175000
Source: Dodge 2023 data ( NEW large office buildings built after 1967)

## Prototype
NORESCO, Updated November 2025
OfficeLarge
Characteristic | Value | Data Sources
Building Type | Large Office
Building Category | Nonresidential
Vintages | 4 Vintages: Pre-1978 , 1978-1997 ,1998-2007 , 2008-2018 New Construction (2019+) | Based on the vintage bin analysis | NonRes-Vintage bins-Draft Report-30Nov2023-Final.docx
Shape |  | Number of floors: Based on the existing Large Office prototypes (PNNL, CEC) Footprint (floor area of each story): Supported by Dodge 2023 data and consistent with the existing Large Office prototypes Zone configuration and floor plan layout: Based on the ORNL 2019 project, with modifications informed by engineering and architectural judgment (see the "Zones" tab for more details) | https://publications.ibpsa.org/proceedings/simbuild/2020/papers/simbuild2020_C064.pdf
Total Floor Area (ft2) | 498,589 (240 ft *160 ft) | Same as CEC and PNNL
Aspect Ratio | 1.5 | Same as CEC and PNNL
Number of Floors | 12 Floor + basement | Number of floor: based on the existing Large Office prototypes (PNNL,CEC)
Roof type | Flat | Supported by CBECS 2018 data (Same as CEC and PNNL)
WWR | 40% of the above grade wall
Window dimensions | Even distribution
Shading Geometry | None
Floor to floor height (feet) | 13 | Same as CEC and PNNL
Floor to ceiling height (feet) | 9 | Same as CEC and PNNL
Glazing sill height (feet) | 3 | Same as CEC and PNNL

## Envelope
Envelope - OfficeLarge
Element | Prototype | Assembly Type | Construction | Thermal Properties | Vintage | Selected T24 | Note | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
External Wall | OfficeLarge | ExtWall_MetalFramed_NonRes | Metal frame + insulation + Gypsum board | U-factor IP | Pre 1978 | N/A | ASHRAE 90.1 Table A3.3.3.1, 16" on center, R-0 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352
[5 empty] | 1978-1997 | 1986 | High-rise office: Package A with heat capacity 10.0-14.99 (BTU/F/ft2) | 0.21277 | 0.22727 | 0.22727 | 0.21739 | 0.21739 | 0.25641 | 0.25641 | 0.25641 | 0.25641 | 0.25641 | 0.2381 | 0.2381 | 0.2381 | 0.20833 | 0.20833 | 0.21277
[5 empty] | 1998-2007 | 2001 |  | 0.182 | 0.182 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182
[5 empty] | 2008-2018 | 2013 |  | 0.098 | 0.062 | 0.082 | 0.062 | 0.062 | 0.098 | 0.098 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062
[5 empty] | 2019+ | 2025 |  | 0.06 | 0.055 | 0.071 | 0.055 | 0.055 | 0.06 | 0.06 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055
Roof | OfficeLarge | FlatRoof_WoodFramedAndOther_NonRes | Metal deck + insulation + Roof membrane | U-factor IP | Pre 1978 | N/A | Considering 30 years for roof/ insulation replacement. | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 1978-1997 | 1992 |  | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 1998-2007 | 2001 |  | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 2008-2018 | 2013 |  | 0.049 | 0.039 | 0.039 | 0.039 | 0.049 | 0.075 | 0.067 | 0.067 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039
[5 empty] | 2019+ | 2025 |  | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.047 | 0.047 | 0.047 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028
Windows | OfficeLarge | FixedWindow_NonRes | CBECS 2018 shows that ~50% of large offices that were built before 2000 are single pane | U-factor IP | Pre 1978 | N/A | ASHRAE Handbook of Fundamentals for single pane (Table 4-Ch15) & T24, 2013 for double pane(50%-50%)* | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74
[5 empty] | 1978-1997 | N/A |  | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74
|  |  | Double pane |  | 1998-2007 | 2001 |  | 0.49 | 0.49 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49
[5 empty] | 2008-2018 | 2013 |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36
[5 empty] | 2019+ | 2025 |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.34 | 0.36 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.36
|  | FixedWindow_NonRes | CBECS 2018 shows that ~50% of large offices that were built before 2000 are single pane | SHGC | Pre 1978 | N/A | ASHRAE Handbook of Fundamentals for single pane (Table 10-Ch15) & T24, 2013 for double pane(50%-50%)* | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52
[5 empty] | 1978-1997 | N/A |  | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52
[5 empty] | 1998-2007 | 2001 | WWR:20-30 / SHGC non-north (Non-north SHGC is more stringent than north and is therefore considered for all sides) | 0.43 | 0.36 | 0.41 | 0.41 | 0.41 | 0.39 | 0.39 | 0.39 | 0.39 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.43
[5 empty] | 2008-2018 | 2013 |  | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
[5 empty] | 2019+ | 2025 |  | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.22 | 0.25 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.25
Infiltration rate at normal pressure (cfm/ft2) (Design flow rate approach and Flow/Exterior Wall Area calculation method)
[5 empty] | Vintage | I_75 (cfm/sf) 6-sdied Infiltration rate @ 75 pa | Note | CZ1: I-design (cfm/ft2) (4-sided Infiltration rate at normal pressure) (Design flow rate approach and Flow/Exterior Wall Area calculation method)
|  |  |  | Infiltration | Pre 1978 | 1.1 | 2022 CASE report (Table 38) | CZ1: 0.2053
[5 empty] | 1978-1997 | 1.1 | 2022 CASE report (Table 38) | CZ1: 0.2053
[5 empty] | 1998-2007 | 1.1 | 2022 CASE report (Table 38) | CZ1: 0.2053
[5 empty] | 2008-2018 | 1 | 2022 CASE report (Table 38) & Title 24, part 6, 2008-2016 (Table 140.3-B) | CZ1: 0.1878
[5 empty] | 2019+ | 0.6 | 2022 CASE report (Table 38) & Title 24, part 6, 2025 (Table 140.3-B) | CZ1: 0.112
Source: Title 24 air barrier requirements (all editions) and the standardized infiltration rate reported in the 2022 CASE report and Dodge 2023 data
|  |  |  | Air Leakage Memo: |  | Infiltration_rate_report_14May2025-Short-Version.docx
*Note for windows properties in vintage 1 &2 :
We’ve considered a 50% single-pane and 50% double-pane mix (based on the 2013 requirements) for the window properties in Vintage 1 & 2 (pre-1998 buildings).
We don't have California-specific data, and the decision was based on the CBECS 2018 data, which indicates:
- 30% of large offices built before 1978 have mixed windows, while only 16% of large offices from the second vintage (1978-1997) have mixed glass.
- Pre-1980: Among those with either single or double-pane windows, 70% have single-pane windows, and 30% have double-pane windows.
- 1980-1999: Among those with either single or double-pane windows, 43% have single-pane windows, and 57% have double-pane windows.
- Pre-2000: Among those with either single or double-pane windows, 49% has single pane windows.
Considering the Pre-2000 percentage, we've decided to apply the 50%-50% mix to the window properties of the first two vintages.
|  | Fixed windows | Double pane | SHGC | 1998-2007 | 2001 | WWR:20-30 / SHGC north | 0.47 | 0.47 | 0.61 | 0.61 | 0.61 | 0.61 | 0.61 | 0.61 | 0.61 | 0.47 | 0.47 | 0.47 | 0.47 | 0.47 | 0.47 | 0.47
[7 empty] | WWR:20-30 / SHGC non-north | 0.43 | 0.36 | 0.41 | 0.41 | 0.41 | 0.39 | 0.39 | 0.39 | 0.39 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.43

## Zones
Proposed Layout - OfficeLarge
Space/ Thermal Zone | Space Type | HVAC System Name/AHU Name | Schedule Category | Conditioned (Y/N) | Area Fraction | Area (ft²) | Volume (ft³) | Multipliers | Number of People | People (Persons/1,000 ft²) [T24, 2025,Table 120.1-A]
Perimeter_Open_ Office_N_Basement | Office Area (>250 square feet) | VAV With Reheat_Basement | Office | Y | 1.688% | 8416.86 | 75751.74 | 1 | 42.0843 | 5
Perimeter_Open_ Office_S_Basement | Office Area (>250 square feet) | VAV With Reheat_Basement | Office | Y | 0.7346% | 3662.18 | 32959.62 | 1 | 18.3109 | 5
Core_Enclosed_Office_Basement | Office Area (>250 square feet) | VAV With Reheat_Basement | Office | Y | 0.7429% | 3703.68 | 33333.12 | 1 | 18.5184 | 5
Server_Room_Basement | Server Room (EPD 45) | CRAH_ServerRoom_Basement | Data | Y | 1.651% | 8228 | 74052 | 1 | 0 | 0
Mech/Elec_Basement | Electrical, Mechanical, Telephone Rooms | VAV With Reheat_Basement | Office | Y | 1.596% | 7958 | 71622 | 1 | 0 | 0
Conference_Basement | Convention, Conference, Multipurpose and Meeting Area | VAV With Reheat_Basement | Office | Y | 0.1163% | 579.7 | 5217.3 | 1 | 19.1301 | 33
Break_Basement | Lounge, Breakroom, or Waiting Area | VAV With Reheat_Basement | Office | Y | 0.1952% | 973 | 8757 | 1 | 32.109 | 33
Storage_Basement | Storage (General) | VAV With Reheat_Basement | Office | Y | 0.2469% | 1231 | 11079 | 1 | 0 | 0
Restroom_Basement | Restrooms | VAV With Reheat_Basement | Office | Y | 0.1978% | 986 | 8874 | 1 | 0 | 0
Lobby_Basement | Lobby, Main Entry | VAV With Reheat_Basement | Office | Y | 0.1418% | 707 | 6363 | 1 | 7.07 | 10 | Number of People: 10 according to ASHRAE 62.1 Table 6-1 for main entry lobbies T24: 33 for main Entry lobbies & 5 for reception area
Stair/Elevator_Basement | Stairwell | VAV With Reheat_Basement | Office | Y | 0.1888% | 941 | 8469 | 1 | 0 | 0
Corridor_W_Basement | Corridor Area | VAV With Reheat_Basement | Office | Y | 0.05274% | 262.9 | 2366.1 | 1 | 1.3145 | 5
Corridor_E_Basement | Corridor Area | VAV With Reheat_Basement | Office | Y | 0.141% | 703 | 6327 | 1 | 3.515 | 5
Perimeter_Open_ Office_N_FloorG | Office Area (>250 square feet) | VAV With Reheat_FloorG | Office | Y | 1.41% | 7031 | 63279 | 1 | 35.155 | 5
Perimeter_Open_ Office_W_FloorG | Office Area (>250 square feet) | VAV With Reheat_FloorG | Office | Y | 1.163% | 5795.76 | 52161.84 | 1 | 28.9788 | 5
Perimeter_Open_ Office_E_FloorG | Office Area (>250 square feet) | VAV With Reheat_FloorG | Office | Y | 1.179% | 5875.48 | 52879.32 | 1 | 29.3774 | 5
Perimeter_Enclosed_ Office_NE_FloorG | Office Area (>250 square feet) | VAV With Reheat_FloorG | Office | Y | 0.184% | 917.38 | 8256.42 | 1 | 4.5869 | 5
Perimeter_Enclosed_ Office_NW_FloorG | Office Area (>250 square feet) | VAV With Reheat_FloorG | Office | Y | 0.2268% | 1130.61 | 10175.49 | 1 | 5.653 | 5 |  | Basement |  |  |  | First Floor |  |  | Middle/Top Floors
Core_Enclosed_Office_FloorG | Office Area (>250 square feet) | VAV With Reheat_FloorG | Office | Y | 0.6644% | 3312 | 29808 | 1 | 16.56 | 5
Server_Room_FloorG | Computer Room (EPD 20) | CRAC DX Clg_FloorG | Data | Y | 0.08384% | 417.94 | 3761.46 | 1 | 0 | 0 |  |  | Spaces of Basement​ | Area (ft2)​ | % of footprint | Spaces of First Floor​ | Area (ft2)​ | % of footprint | Spaces of Middle/Top Floor​s | Area (ft2)​ | % of footprint
Mech/Elec_FloorG | Electrical, Mechanical, Telephone Rooms | VAV With Reheat_FloorG | Office | Y | 0.1703% | 849 | 7641 | 1 | 0 | 0 |  |  | Open office​ | 12079.04 | 31.49% | Open office​ | 18702.24 | 48.76% | Open office​ | 21287.86 | 55.51%
Conference_FloorG | Convention, Conference, Multipurpose and Meeting Area | VAV With Reheat_FloorG | Office | Y | 0.1585% | 790 | 7110 | 1 | 26.07 | 33 |  |  | Core Enclosed Office​ | 3703.68 | 9.657% | Core Enclosed Office​ | 3312 | 8.636% | Core Enclosed Office​ | 3233 | 8.43%
Break_FloorG | Lounge, Breakroom, or Waiting Area | VAV With Reheat_FloorG | Office | Y | 0.124% | 618.05 | 5562.45 | 1 | 20.3956 | 33 |  |  | Perimeter Enclosed Office​ | _ | _ | Perimeter Enclosed Office​ | 2047.99 | 5.34% | Perimeter Enclosed Office​ | 4092.56 | 10.67%
FoodPrep_FloorG | Kitchen/Food Preparation Area | VAV With Reheat_FloorG | Office | Y | 0.1879% | 936.94 | 8432.46 | 1 | 2.8108 | 3 |  |  | Conference​ | 579.7 | 1.511% | Conference​ | 790 | 2.06% | Conference​ | 2323.24 | 6.058%
Storage_FloorG | Storage (General) | VAV With Reheat_FloorG | Office | Y | 0.1924% | 959.02 | 8631.18 | 1 | 0 | 0 |  |  | Break + Food prep​ | 973 | 2.537% | Break + Food prep​ | 1554.99 | 4.054% | Break + Food prep​ | 910 | 2.373%
Locker_FloorG | Locker Room | VAV With Reheat_FloorG | Office | Y | 0.3641% | 1814.97 | 16334.73 | 1 | 18.1497 | 10 | Based on 2022 CEC AP5 |  | Storage​ | 1231 | 3.21% | Storage​+locker | 2773.99 | 7.233% | Storage​ | 738 | 1.924%
Lobby_S_FloorG | Lobby, Main Entry | VAV With Reheat_FloorG | Office | Y | 0.6741% | 3360.63 | 30245.67 | 1 | 33.6063 | 10 |  |  | Mech/Elec​ | 7958 | 20.75% | Mech/Elec​ | 849 | 2.214% | Mech/Elec​ | 1070 | 2.79%
Lobby_FloorG | Lobby, Main Entry | VAV With Reheat_FloorG | Office | Y | 0.1371% | 683.36 | 6150.24 | 1 | 6.8336 | 10 |  |  | Server Room​ | 8228 | 21.45% | Server Room​ | 417.94 | 1.09% | Server Room​ | 418 | 1.09%
Restroom_FloorG | Restrooms | VAV With Reheat_FloorG | Office | Y | 0.2319% | 1156 | 10404 | 1 | 0 | 0 |  |  | Corridor​ | 965.9 | 2.518% | Corridor​ | 1803.99 | 4.704% | Corridor​ | 1591.24 | 4.149%
Stair/Elevator_FloorG | Stairwell | VAV With Reheat_FloorG | Office | Y | 0.1701% | 848 | 7632 | 1 | 0 | 0 |  |  | Restroom​ | 986 | 2.571% | Restroom​ | 1156 | 3.014% | Restroom​ | 1155 | 3.011%
Corridor_W_FloorG | Corridor Area | VAV With Reheat_FloorG | Office | Y | 0.2018% | 1005.88 | 9052.92 | 1 | 5.0294 | 5 |  |  | Lobby​ | 707 | 1.843% | Lobby​ | 4043.99 | 10.54% | Lobby​ | 684 | 1.783%
Corridor_E_FloorG | Corridor Area | VAV With Reheat_FloorG | Office | Y | 0.1601% | 798.11 | 7182.99 | 1 | 3.9906 | 5 |  |  | Stair/Elevator​ | 941 | 2.454% | Stair/Elevator​ | 848 | 2.211% | Stair/Elevator​ | 848 | 2.211%
Plenum_FloorG | Plenum | _ |  | N |  | 38352.015 | 153408.06 | 1 | 0 | 0 | [5 empty] | Plenum​ | 38352.015 | 100% | Plenum​ | 38,353 ​ | 100%
Perimeter_Open_ Office_N_FloorM | Office Area (>250 square feet) | VAV With Reheat_FloorM | Office | Y | 1.431% | 7131.29 | 64181.61 | 10 | 35.6564 | 5 |  |  |  | 38353 | [5 empty] | 38350.9
Perimeter_Open_ Office_S_FloorM | Office Area (>250 square feet) | VAV With Reheat_FloorM | Office | Y | 1.051% | 5237.37 | 47136.33 | 10 | 26.1868 | 5
Perimeter_Open_ Office_E_FloorM | Office Area (>250 square feet) | VAV With Reheat_FloorM | Office | Y | 0.8968% | 4470.44 | 40233.96 | 10 | 22.3522 | 5
Perimeter_Open_ Office_W_FloorM | Office Area (>250 square feet) | VAV With Reheat_FloorM | Office | Y | 0.8924% | 4448.76 | 40038.84 | 10 | 22.2438 | 5
Perimeter_Enclosed_ Office_NE_FloorM | Office Area (>250 square feet) | VAV With Reheat_FloorM | Office | Y | 0.184% | 917.38 | 8256.42 | 10 | 4.5869 | 5
Perimeter_Enclosed_ Office_NW_FloorM | Office Area (>250 square feet) | VAV With Reheat_FloorM | Office | Y | 0.2269% | 1131.21 | 10180.89 | 10 | 5.6561 | 5
Perimeter_Enclosed_ Office_SW_FloorM | Office Area (>250 square feet) | VAV With Reheat_FloorM | Office | Y | 0.2027% | 1010.49 | 9094.41 | 10 | 5.0524 | 5
Perimeter_Enclosed_ Office_SE_FloorM | Office Area (>250 square feet) | VAV With Reheat_FloorM | Office | Y | 0.2073% | 1033.48 | 9301.32 | 10 | 5.1674 | 5
Core_Enclosed_ Office_FloorM | Office Area (>250 square feet) | VAV With Reheat_FloorM | Office | Y | 0.6485% | 3233 | 29097 | 10 | 16.165 | 5
Server_Room_FloorM | Computer Room (EPD 20) | CRAC DX Clg_FloorM | Data | Y | 0.08385% | 418 | 3762 | 10 | 0 | 0
Mech/Elec_FloorM | Electrical, Mechanical, Telephone Rooms | VAV With Reheat_FloorM | Office | Y | 0.2146% | 1070 | 9630 | 10 | 0 | 0
Conference_N_FloorM | Convention, Conference, Multipurpose and Meeting Area | VAV With Reheat_FloorM | Office | Y | 0.1584% | 789.8 | 7108.2 | 10 | 26.0634 | 33
Conference_W_FloorM | Convention, Conference, Multipurpose and Meeting Area | VAV With Reheat_FloorM | Office | Y | 0.06749% | 336.44 | 3027.96 | 10 | 11.1025 | 33
Conference_S_FloorM | Convention, Conference, Multipurpose and Meeting Area | VAV With Reheat_FloorM | Office | Y | 0.1532% | 763.8 | 6874.2 | 10 | 25.2054 | 33
Conference_E_FloorM | Convention, Conference, Multipurpose and Meeting Area | VAV With Reheat_FloorM | Office | Y | 0.0869% | 433.2 | 3898.8 | 10 | 14.2956 | 33
Break_FloorM | Lounge, Breakroom, or Waiting Area | VAV With Reheat_FloorM | Office | Y | 0.1825% | 910 | 8190 | 10 | 30.03 | 33
Storage_FloorM | Storage (General) | VAV With Reheat_FloorM | Office | Y | 0.148% | 738 | 6642 | 10 | 0 | 0
Lobby_FloorM | Lobby, Main Entry | VAV With Reheat_FloorM | Office | Y | 0.1372% | 684 | 6156 | 10 | 6.84 | 10
Restroom_FloorM | Restrooms | VAV With Reheat_FloorM | Office | Y | 0.2317% | 1155 | 10395 | 10 | 0 | 0
Stair/Elevator_FloorM | Stairwell | VAV With Reheat_FloorM | Office | Y | 0.1701% | 848 | 7632 | 10 | 0 | 0
Corridor_W_FloorM | Corridor Area | VAV With Reheat_FloorM | Office | Y | 0.2018% | 1005.88 | 9052.92 | 10 | 5.0294 | 5
Corridor_E_FloorM | Corridor Area | VAV With Reheat_FloorM | Office | Y | 0.1174% | 585.36 | 5268.24 | 10 | 2.9268 | 5
Plenum_FloorM | Plenum | _ |  | N |  | 38352.015 | 153408.06 | 10 | 0 | 0
Perimeter_Open_ Office_N_FloorT | Office Area (>250 square feet) | VAV With Reheat_FloorT | Office | Y | 1.431% | 7131.29 | 64181.61 | 1 | 35.6564 | 5
Perimeter_Open_ Office_S_FloorT | Office Area (>250 square feet) | VAV With Reheat_FloorT | Office | Y | 1.051% | 5237.37 | 47136.33 | 1 | 26.1868 | 5
Perimeter_Open_ Office_E_FloorT | Office Area (>250 square feet) | VAV With Reheat_FloorT | Office | Y | 0.8968% | 4470.44 | 40233.96 | 1 | 22.3522 | 5
Perimeter_Open_ Office_W_FloorT | Office Area (>250 square feet) | VAV With Reheat_FloorT | Office | Y | 0.8924% | 4448.76 | 40038.84 | 1 | 22.2438 | 5
Perimeter_Enclosed_ Office_NE_FloorT | Office Area (>250 square feet) | VAV With Reheat_FloorT | Office | Y | 0.184% | 917.38 | 8256.42 | 1 | 4.5869 | 5
Perimeter_Enclosed_ Office_NW_FloorT | Office Area (>250 square feet) | VAV With Reheat_FloorT | Office | Y | 0.2269% | 1131.21 | 10180.89 | 1 | 5.6561 | 5
Perimeter_Enclosed_ Office_SW_FloorT | Office Area (>250 square feet) | VAV With Reheat_FloorT | Office | Y | 0.2027% | 1010.49 | 9094.41 | 1 | 5.0524 | 5
Perimeter_Enclosed_ Office_SE_FloorT | Office Area (>250 square feet) | VAV With Reheat_FloorT | Office | Y | 0.2073% | 1033.48 | 9301.32 | 1 | 5.1674 | 5
Core_Enclosed_ Office_FloorT | Office Area (>250 square feet) | VAV With Reheat_FloorT | Office | Y | 0.6485% | 3233 | 29097 | 1 | 16.165 | 5
Server_Room_FloorT | Computer Room (EPD 20) | CRAC DX Clg_FloorT | Data | Y | 0.08385% | 418 | 3762 | 1 | 0 | 0
Mech/Elec_FloorT | Electrical, Mechanical, Telephone Rooms | VAV With Reheat_FloorT | Office | Y | 0.2146% | 1070 | 9630 | 1 | 0 | 0
Conference_N_FloorT | Convention, Conference, Multipurpose and Meeting Area | VAV With Reheat_FloorT | Office | Y | 0.1584% | 789.8 | 7108.2 | 1 | 26.0634 | 33
Conference_W_FloorT | Convention, Conference, Multipurpose and Meeting Area | VAV With Reheat_FloorT | Office | Y | 0.06749% | 336.44 | 3027.96 | 1 | 11.1025 | 33
Conference_S_FloorT | Convention, Conference, Multipurpose and Meeting Area | VAV With Reheat_FloorT | Office | Y | 0.1532% | 763.8 | 6874.2 | 1 | 25.2054 | 33
Conference_E_FloorT | Convention, Conference, Multipurpose and Meeting Area | VAV With Reheat_FloorT | Office | Y | 0.0869% | 433.2 | 3898.8 | 1 | 14.2956 | 33
Break_FloorT | Lounge, Breakroom, or Waiting Area | VAV With Reheat_FloorT | Office | Y | 0.1825% | 910 | 8190 | 1 | 30.03 | 33
Storage_FloorT | Storage (General) | VAV With Reheat_FloorT | Office | Y | 0.148% | 738 | 6642 | 1 | 0 | 0
Lobby_FloorT | Lobby, Main Entry | VAV With Reheat_FloorT | Office | Y | 0.1372% | 684 | 6156 | 1 | 6.84 | 10
Restroom_FloorT | Restrooms | VAV With Reheat_FloorT | Office | Y | 0.2317% | 1155 | 10395 | 1 | 0 | 0
Stair/Elevator_FloorT | Stairwell | VAV With Reheat_FloorT | Office | Y | 0.1701% | 848 | 7632 | 1 | 0 | 0
Corridor_W_FloorT | Corridor Area | VAV With Reheat_FloorT | Office | Y | 0.2018% | 1005.88 | 9052.92 | 1 | 5.0294 | 5
Corridor_E_FloorT | Corridor Area | VAV With Reheat_FloorT | Office | Y | 0.1174% | 585.36 | 5268.24 | 1 | 2.9268 | 5
Plenum_FloorT | Plenum | _ |  | N |  | 38352.015 | 153408.06 | 1 | 0 | 0
Total Zones in E+: 79 Total with multiplier: 286 | Total (13 Space Types) | Total systems in E+: 8 Total with multiplier: 26 | Total (1 category) | Total zones in E+: 76 conditioned and 3 unconditioned. Total with multiplier: 274 Conditioned , 12 Unconditioned ) | 100% | 498512.35
N
Open Office
Lobby
Enclosed Office
Lobby
Stair/Elevator
Corridor
Restroom
Food Prep
Enclosed Office
Enclosed Office
Break
Open Office
Open Office
Mech/Elec
Storage
Locker
Server Room
Conference
Open Office
Open Office
Enclosed Office Middle/Top Floors ed Office
Enclosed Office
Conference
Conference
Enclosed Office
Conference
Lobby
Stair/Elevator
Corridor
Break
Mech/Elec
Storage
Server Room
Enclosed Office
Restroom
Open Office
Enclosed Office
Open Office
Conference
Open Office
Open Office
Mech/Elec
Server Room
Enclosed Office
Lobby
Stair/Elevator
Corridor
Conference
Break & Food Prep
Restroom
Storage & Locker
Corridor
Corridor
Corridor

## HVAC System
HVAC system - OfficeLarge
Vintage | Zones | Heating | Cooling | Air Distribution | Source | Note
Existing | Server Room_B | - | built up CRAH with chilled water coils (Computer Room Air Handling unit) | CAV | Engineering Judgement
| Server_Room_G Server_Room_M Server_Room_T | - | DX Computer Room Air Conditioner | CAV | Engineering Judgement | DX Computer Room Air Conditioner units have been a standard solution in server rooms for many years.
| All other conditioned zones | Gas Boiler | Chiller (it also serves the Server_Room_B zone) | built-up VAV with hydronic reheat | CEUS 2022
New Construction | Server Room_B | - | built up CRAH with chilled water coils (Computer Room Air Handling unit) | CAV | T24 2025
| Server_Room_G Server_Room_M Server_Room_T | - | DX Computer Room Air Conditioner (CRAC) | CAV | T24 2025
| All other conditioned zones | Gas Boiler | Chiller (it also serves the Server_Room_B zone) | VAV | T24 2025
Efficiency of HVAC system
| Upgrade/Installed year | DX Computer Room Air Conditioner Server_Room_G/M/T (CRAC) | Chiller | Gas Boiler | Sources | Note
Pre 1978 | 2008 | EER=9.0 | 6.10 COP 6.40 IPLV | Efficiency of 80% | CFR Energy 2008 (for DX CRAC) | Two centrifugal chillers (Total cooling plant load > 600 tons) Two atmospheric boilers (no combustion air fans) | FR-2009-03-23.pdf
1978-1997
1998-2007
2008-2018 | 2013 | EER=9.0 | ≤ 0.590 kW/ton ≤ 0.400 IPLV | Thermal efficiency (Et) of 80% | CFR Energy 2010:Title 10- Table 9 (for DX CRAC) Title 24, Part 6, 2013 ,Table 110.2-J (for Boiler thermal efficiency) | water-cooled centrifugal chillers Two Boilers each with capacity between 300-2,500 KBTU/hr
New Construction | 2025 | SEER=13.4 SCOP=2.09 | ≤ 0.625 kW/ton ≤ 0.410 IPLV | Thermal efficiency (Et) of 84% | CFR Energy 2025, Table 12 (for DX CRAC) Title 24, Part 6, 2022 ,Table 110.2-J (for Boiler thermal efficiency) | Two water-cooled screw chillers (Each between 300-600 ton), Path B, Positive displacement chiller with design leaving fluid temperature ≤ 32°F Two Boilers each with capacity between 300-2,500 KBTU/hr | CFR-2024-title10-vol3-part431-subpartF.pdf
Economizer is required for all the systems. CRAC units should have "integrated airside economizer"
Only adiabatic humidification |  | Title 24, Part 6_ 2025, Section 140.9 (a)1
Demand Control ventilation
Background Data [To be deleted prior to publication]
Existing prototypes:
| Space | System No. | System Type | Fan Control | Cooling Type | Heating Type
CBECC 2025 | All Space |  |  | VAV | Chilled water | Hot-water fossil fuel boiler
CPUC 2024 | All Space |  |  | VAV | Chiller water | Gas Boiler
PNNL ASHRAE 90.1- 2022 San Diego | data center room | 14. WSHP (CRAC) | Water source heat pump (Computer room air conditioning unit) | Constant volume | Fluid cooler | Hot-water fossil fuel boiler
| Basement (Except data center) | 12. SZ-CV-HW | Single-zone system | Constant volume | Chilled water | Hot-water fossil fuel boiler
| Other spaces | 7. VAV with reheat | VAV with reheat | VAV | Chilled water | Hot-water fossil fuel boiler
Basement system in PNNL model is :SZ-CV-HW (Single zone system: CV fan control & Chilled water cooling & Hot-water fossil fuel boiler heating)
Other floors system in PNNL model is: VAV Reheat ( VAV with Reheat: VA fan control & Chilled water cooling & Hot-water fossil fuel boiler heating )
Dat center zone has its won system in PNNL model: WSHP (CRAC): Water source heat pump (Computer room air conditioning unit) system: CV fan control & Fluid cooler & Hot-water fossil fuel boiler heating
CEUS 2022 data:
Heating System
Calculation method | Building Type | Fan Coil / Unit Ventilator | Dual Duct Constant Air Volume | Dual Duct Variable Air Volume |  | Single Duct Constant Air Volume | Single Duct Variable Air Volume
Floorspace-Based | Office, Large |  | 3% | 15% |  | 43% | 21%
Sites-Based | Office, Large | 13% | 2% | 7% |  | 66% | 12%
Chiller System
Calculation method | Building Type | Boiler/ Hydronic | Package System / Heat Pump | Split-System / Heat Pump |  | Ductless Mini-Split Heat Pump | Room Heating
Floorspace-Based | Office, Large | 59% | 35% | 5% |  | 0% | 0%
Sites-Based | Office, Large | 34% | 58% | 7% |  | 0% | 0%
Heating Fuel Type
Calculation method | Building Type | Gas Share | Electric Share
Floorspace-Based | Office, Large | 86% | 13%
Sites-Based | Office, Large | 79% | 20%
Fuel Share Large office (area >3,000 sf)
CZ | Heating system |  |  | Water heater
| Saturation (Electric) | Saturation (Gas) | Saturation (Other Fuels) | Saturation (Electric) | Saturation (Gas) | Saturation (Other Fuels)
1 | 3% | 97% | 0% | 17% | 83% | 0%
2 | 7% | 93% | 0% | 30% | 70% | 0%
3 | 2% | 94% | 4% | 36% | 64% | 4%
4 | 1% | 94% | 4% | 35% | 65% | 4%
5 | 4% | 95% | 2% | 74% | 26% | 2%
6 | 21% | 79% | 0% | 38% | 62% | 0%
7 | 11% | 87% | 2% | 30% | 70% | 1%
8 | 23% | 77% | 0% | 37% | 63% | 0%
9 | 16% | 83% | 0% | 33% | 67% | 0%
10 | 16% | 83% | 1% | 49% | 51% | 0%
11 | 10% | 89% | 1% | 42% | 58% | 1%
12 | 10% | 88% | 2% | 38% | 62% | 3%
13 | 4% | 96% | 0% | 16% | 84% | 0%
14 | 31% | 69% | 0% | 43% | 57% | 0%
15 | 9% | 89% | 2% | 82% | 18% | 0%
16 | 20% | 80% | 0% | 35% | 65% | 0%
Fan power
Vintage | Approach | System | Total Static Pressure (TSP) (in w.c.) | Fan Efficiency [ACM 2025] | Fan Motor and Drive Efficiency [ACM 2025, Table 13] | W/cfm [ACM 2025, Table 14 and 15] | Data Source | Note
Existing | PNNL TSP | CAV System <7,437 cfm | 2.5 | 0.65 | ~0.9 (The full-load efficiency of the motor serving the fan- will be determined based on ACM 2025, Table 13) |  | Fan Motor and Efficiency: ACM 2025, 0.5 Engineering judgement TSP:[PNNL 20405, 2010, Table 5.11
|  | CAV System >7,437 cfm | 4.09 | 0.65
|  | VAV System > 4,648 cfm | 5.58 | 0.65
Brake horse power (bhp)=(Supply cfm*TSP in w.c.)/(6356*Fan efficiency)
Fan power (w/cfm) = bhp/motor and drive efficiency *746
New Construction | ACM 2025 | VAV System > 10,000 cfm | 4.7201 | 0.65 | 0.9 | 0.947 | Fan Motor and Efficiency and W/cfm: ACM 2025 | 0.35 w/cfm for indoor unit fan (T24, 2025, Section 140.4(a)3 D)
* 0.9 is an average fan efficiency according to ACM 2025, Table 13
Fan total eff (E+ input) = 0.65 x Motor_eff
TSP (E+ input) in w.c. = Motor_eff/746 x (6356 x Fan_eff) x W/cfm
Fan_eff=0.65
Microsoft Word - PNNL 90 1-2010_TSD_Final 5-23-2011_Final.docx

## Thermostat
Thermostat Setpoints - OfficeLarge
Spaces/Zones | Setpoint | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16 | Source
All conditioned zones except server rooms | Heating Setpoint (F) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | T24 2022 - Appendix 5.4B
| Heating Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
| Cooling Setpoint (F) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
| Cooling Setback (F) | 85 | 85* | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
Server rooms | Cooling Setpoint (F) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | Title 24, Part 6, 2025, section 140.9 (a) and PNNL ASHRAE 90.1 2022 Large Office prototype
| Heating Setback (F) | CZ1: The Server room with 20 W/ft2 load would likely don't require heating system as the equipment constantly generate enough heat. **
*PNNL has considered 80 F for cooling setback of Large Office prototype (same as Medium Office). However cooling setback is 85 F in Small Office prototype !
**PNNL has set the heating system temperature to 65°F for all of their data center zones.
Background Data [To be deleted prior to publication] | bar: CZ3 to CZ5
Heating/ CoolingSetpointsSchedules (existing prototypes extracted from the idf files (presented below)
| Heating | CZ9: Cooling
| CEC-2022 | CZ4: PNNL-2022; CZ9: CEC-2022; CZ13: PNNL-2022
| CEC-Weekday | CEC-Saturday | CEC-Sunday |  | PNNL-Weekday | PNNL-Saturday | PNNL-Sunday |  |  | CEC-Weekday | CEC-Saturday | CEC-Sunday |  | PNNL-Weekday | PNNL-Saturday | PNNL-Sunday
1 | 60 | 60 | 60 |  | 60.08 | 60.08 | 60.08 |  |  | 85 | 85 | 85 |  | 80.06 | 80.06 | 80.06
2 | 60 | 60 | 60 |  | 60.08 | 60.08 | 60.08 |  |  | 85 | 85 | 85 |  | 80.06 | 80.06 | 80.06
3 | 60 | 60 | 60 |  | 60.08 | 60.08 | 60.08 |  |  | 85 | 85 | 85 |  | 80.06 | 80.06 | 80.06
4 | 60 | 60 | 60 |  | 60.08 | 60.08 | 60.08 |  |  | 85 | 85 | 85 |  | 80.06 | 80.06 | 80.06
5 | 60 | 60 | 60 |  | 60.08 | 60.08 | 60.08 |  |  | 85 | 85 | 85 |  | 80.06 | 80.06 | 80.06
6 | 70 | 70 | 60 |  | 64.04 | 64.04 | 60.08 |  |  | 75 | 75 | 85 |  | 78.08 | 78.26 | 80.06
7 | 70 | 70 | 60 |  | 68 | 68 | 60.08 |  |  | 75 | 75 | 85 |  | 77 | 77 | 80.06
8 | 70 | 70 | 60 |  | 69.8 | 69.8 | 60.08 |  |  | 75 | 75 | 85 |  | 75.2 | 75.2 | 80.06
9 | 70 | 70 | 60 |  | 69.8 | 69.8 | 60.08 |  |  | 75 | 75 | 85 |  | 75.2 | 75.2 | 80.06
10 | 70 | 70 | 60 |  | 69.8 | 69.8 | 60.08 |  |  | 75 | 75 | 85 |  | 75.2 | 75.2 | 80.06
11 | 70 | 70 | 60 |  | 69.8 | 69.8 | 60.08 |  |  | 75 | 75 | 85 |  | 75.2 | 75.2 | 80.06
12 | 70 | 70 | 60 |  | 69.8 | 69.8 | 60.08 |  |  | 75 | 75 | 85 |  | 75.2 | 75.2 | 80.06
13 | 70 | 70 | 60 |  | 69.8 | 69.8 | 60.08 |  |  | 75 | 75 | 85 |  | 75.2 | 75.2 | 80.06
14 | 70 | 70 | 60 |  | 69.8 | 69.8 | 60.08 |  |  | 75 | 75 | 85 |  | 75.2 | 75.2 | 80.06
15 | 70 | 70 | 60 |  | 69.8 | 69.8 | 60.08 |  |  | 75 | 75 | 85 |  | 75.2 | 75.2 | 80.06
16 | 70 | 70 | 60 |  | 69.8 | 69.8 | 60.08 |  |  | 75 | 75 | 85 |  | 75.2 | 75.2 | 80.06
17 | 70 | 70 | 60 |  | 69.8 | 69.8 | 60.08 |  |  | 75 | 75 | 85 |  | 75.2 | 75.2 | 80.06
18 | 70 | 70 | 60 |  | 69.8 | 60.08 | 60.08 |  |  | 75 | 75 | 85 |  | 75.2 | 80.06 | 80.06
19 | 70 | 70 | 60 |  | 69.8 | 60.08 | 60.08 |  |  | 75 | 75 | 85 |  | 75.2 | 80.06 | 80.06
20 | 70 | 60 | 60 |  | 69.8 | 60.08 | 60.08 |  |  | 75 | 85 | 85 |  | 75.2 | 80.06 | 80.06
21 | 70 | 60 | 60 |  | 69.8 | 60.08 | 60.08 |  |  | 75 | 85 | 85 |  | 75.2 | 80.06 | 80.06
22 | 70 | 60 | 60 |  | 69.8 | 60.08 | 60.08 |  |  | 75 | 85 | 85 |  | 75.2 | 80.06 | 80.06
23 | 70 | 60 | 60 |  | 60.08 | 60.08 | 60.08 |  |  | 75 | 85 | 85 |  | 80.06 | 80.06 | 80.06
24 | 70 | 60 | 60 |  | 60.08 | 60.08 | 60.08 |  |  | 75 | 85 | 85 |  | 80.06 | 80.06 | 80.06

## Ventilation
Outdoor Airflow Rate - OfficeLarge
Space Name | Number of People | Floor Area (ft²) | cfm/person (T24, 2025, Equation 120.1-F and Table 120.1-A) | cfm/ft² (T24, 2025, Equation 120.1-F and Table 120.1-A) | Required Exhaust Rate (T24, 2025, Table 120.1-B – Minimum Exhaust Rates) | Total cfm Driven by People | Total cfm Driven by Area | Total cfm Driven by Exhaust | Total cfm | Note
Perimeter_Open_ Office_N_Basement | 42.0843 | 8416.86 | 15 | 0.15 |  | 631.2645 | 1262.529 |  | 1262.529
Perimeter_Open_ Office_S_Basement | 18.3109 | 3662.18 | 15 | 0.15 |  | 274.6635 | 549.327 |  | 549.327
Core_Enclosed_Office_Basement | 18.5184 | 3703.68 | 15 | 0.15 |  | 277.776 | 555.552 |  | 555.552
Server_Room_Basement | 0 | 8228 | 15 | 0.15 |  | 0 | 1234.2 |  | 1234.2
Mech/Elec_Basement | 0 | 7958 | 15 | 0.15 |  | 0 | 1193.7 |  | 1193.7
Conference_Basement | 19.1301 | 579.7 | 15 | 0.15 |  | 286.9515 | 86.955 |  | 286.9515
Break_Basement | 32.109 | 973 | 15 | 0.15 |  | 481.635 | 145.95 |  | 481.635
Storage_Basement | 0 | 1231 | 15 | 0.15 |  | 0 | 184.65 |  | 184.65
Restroom_Basement | 0 | 986 | 15 | 0.15 | 5* 25/50 (cfm/unit) | 0 | 147.9 | 125 | 147.9 | Almost 1 unit per 30 occupant for exhaust fan
Lobby_Basement | 7.07 | 707 | 15 | 0.15 |  | 106.05 | 106.05 |  | 106.05
Stair/Elevator_Basement | 0 | 941 | 15 | 0.15 |  | 0 | 141.15 |  | 141.15
Corridor_W_Basement | 1.3145 | 262.9 | 15 | 0.15 |  | 19.7175 | 39.435 |  | 39.435
Corridor_E_Basement | 3.515 | 703 | 15 | 0.15 |  | 52.725 | 105.45 |  | 105.45
Perimeter_Open_ Office_N_FloorG | 35.155 | 7031 | 15 | 0.15 |  | 527.325 | 1054.65 |  | 1054.65
Perimeter_Open_ Office_W_FloorG | 28.9788 | 5795.76 | 15 | 0.15 |  | 434.682 | 869.364 |  | 869.364
Perimeter_Open_ Office_E_FloorG | 29.3774 | 5875.48 | 15 | 0.15 |  | 440.661 | 881.322 |  | 881.322
Perimeter_Enclosed_ Office_NE_FloorG | 4.5869 | 917.38 | 15 | 0.15 |  | 68.8035 | 137.607 |  | 137.607
Perimeter_Enclosed_ Office_NW_FloorG | 5.653 | 1130.61 | 15 | 0.15 |  | 84.7957 | 169.5915 |  | 169.5915
Core_Enclosed_Office_FloorG | 16.56 | 3312 | 15 | 0.15 |  | 248.4 | 496.8 |  | 496.8
Server_Room_FloorG | 0 | 417.94 | 15 | 0.15 |  | 0 | 62.691 |  | 62.691
Mech/Elec_FloorG | 0 | 849 | 15 | 0.15 |  | 0 | 127.35 |  | 127.35
Conference_FloorG | 26.07 | 790 | 15 | 0.15 |  | 391.05 | 118.5 |  | 391.05
Break_FloorG | 20.3956 | 618.05 | 15 | 0.15 |  | 305.9347 | 92.7075 |  | 305.9347
FoodPrep_FloorG | 2.8108 | 936.94 | 15 | 0.15 |  | 42.1623 | 140.541 |  | 140.541
Storage_FloorG | 0 | 959.02 | 15 | 0.15 |  | 0 | 143.853 |  | 143.853
Locker_FloorG | 18.1497 | 1814.97 | 15 | 0.15 | 0.25 (cfm/sf) | 272.2455 | 272.2455 | 453.7425 | 453.7425
Lobby_S_FloorG | 33.6063 | 3360.63 | 15 | 0.15 |  | 504.0945 | 504.0945 |  | 504.0945
Lobby_FloorG | 6.8336 | 683.36 | 15 | 0.15 |  | 102.504 | 102.504 |  | 102.504
Restroom_FloorG | 0 | 1156 | 15 | 0.15 | 8* 25/50 (cfm/unit) | 0 | 173.4 | 200 | 200
Stair/Elevator_FloorG | 0 | 848 | 15 | 0.15 |  | 0 | 127.2 |  | 127.2
Corridor_W_FloorG | 5.0294 | 1005.88 | 15 | 0.15 |  | 75.441 | 150.882 |  | 150.882
Corridor_E_FloorG | 3.9906 | 798.11 | 15 | 0.15 |  | 59.8583 | 119.7165 |  | 119.7165
Plenum_FloorG | 0 | 38352.015 |  |  |  | 0 | 0 |  | 0
Perimeter_Open_ Office_N_FloorM | 35.6564 | 7131.29 | 15 | 0.15 |  | 534.8468 | 1069.6935 |  | 1069.6935
Perimeter_Open_ Office_S_FloorM | 26.1868 | 5237.37 | 15 | 0.15 |  | 392.8028 | 785.6055 |  | 785.6055
Perimeter_Open_ Office_E_FloorM | 22.3522 | 4470.44 | 15 | 0.15 |  | 335.283 | 670.566 |  | 670.566
Perimeter_Open_ Office_W_FloorM | 22.2438 | 4448.76 | 15 | 0.15 |  | 333.657 | 667.314 |  | 667.314
Perimeter_Enclosed_ Office_NE_FloorM | 4.5869 | 917.38 | 15 | 0.15 |  | 68.8035 | 137.607 |  | 137.607
Perimeter_Enclosed_ Office_NW_FloorM | 5.6561 | 1131.21 | 15 | 0.15 |  | 84.8408 | 169.6815 |  | 169.6815
Perimeter_Enclosed_ Office_SW_FloorM | 5.0524 | 1010.49 | 15 | 0.15 |  | 75.7867 | 151.5735 |  | 151.5735
Perimeter_Enclosed_ Office_SE_FloorM | 5.1674 | 1033.48 | 15 | 0.15 |  | 77.511 | 155.022 |  | 155.022
Core_Enclosed_ Office_FloorM | 16.165 | 3233 | 15 | 0.15 |  | 242.475 | 484.95 |  | 484.95
Server_Room_FloorM | 0 | 418 | 15 | 0.15 |  | 0 | 62.7 |  | 62.7
Mech/Elec_FloorM | 0 | 1070 | 15 | 0.15 |  | 0 | 160.5 |  | 160.5
Conference_N_FloorM | 26.0634 | 789.8 | 15 | 0.15 |  | 390.951 | 118.47 |  | 390.951
Conference_W_FloorM | 11.1025 | 336.44 | 15 | 0.15 |  | 166.5378 | 50.466 |  | 166.5378
Conference_S_FloorM | 25.2054 | 763.8 | 15 | 0.15 |  | 378.081 | 114.57 |  | 378.081
Conference_E_FloorM | 14.2956 | 433.2 | 15 | 0.15 |  | 214.434 | 64.98 |  | 214.434
Break_FloorM | 30.03 | 910 | 15 | 0.15 |  | 450.45 | 136.5 |  | 450.45
Storage_FloorM | 0 | 738 | 15 | 0.15 |  | 0 | 110.7 |  | 110.7
Lobby_FloorM | 6.84 | 684 | 15 | 0.15 |  | 102.6 | 102.6 |  | 102.6
Restroom_FloorM | 0 | 1155 | 15 | 0.15 | 9* 25/50 (cfm/unit) | 0 | 173.25 | 225 | 225
Stair/Elevator_FloorM | 0 | 848 | 15 | 0.15 |  | 0 | 127.2 |  | 127.2
Corridor_W_FloorM | 5.0294 | 1005.88 | 15 | 0.15 |  | 75.441 | 150.882 |  | 150.882
Corridor_E_FloorM | 2.9268 | 585.36 | 15 | 0.15 |  | 43.902 | 87.804 |  | 87.804
Plenum_FloorM | 0 | 38352.015 |  |  |  | 0 | 0 |  | 0
Perimeter_Open_ Office_N_FloorT | 35.6564 | 7131.29 | 15 | 0.15 |  | 534.8468 | 1069.6935 |  | 1069.6935
Perimeter_Open_ Office_S_FloorT | 26.1868 | 5237.37 | 15 | 0.15 |  | 392.8028 | 785.6055 |  | 785.6055
Perimeter_Open_ Office_E_FloorT | 22.3522 | 4470.44 | 15 | 0.15 |  | 335.283 | 670.566 |  | 670.566
Perimeter_Open_ Office_W_FloorT | 22.2438 | 4448.76 | 15 | 0.15 |  | 333.657 | 667.314 |  | 667.314
Perimeter_Enclosed_ Office_NE_FloorT | 4.5869 | 917.38 | 15 | 0.15 |  | 68.8035 | 137.607 |  | 137.607
Perimeter_Enclosed_ Office_NW_FloorT | 5.6561 | 1131.21 | 15 | 0.15 |  | 84.8408 | 169.6815 |  | 169.6815
Perimeter_Enclosed_ Office_SW_FloorT | 5.0524 | 1010.49 | 15 | 0.15 |  | 75.7867 | 151.5735 |  | 151.5735
Perimeter_Enclosed_ Office_SE_FloorT | 5.1674 | 1033.48 | 15 | 0.15 |  | 77.511 | 155.022 |  | 155.022
Core_Enclosed_ Office_FloorT | 16.165 | 3233 | 15 | 0.15 |  | 242.475 | 484.95 |  | 484.95
Server_Room_FloorT | 0 | 418 | 15 | 0.15 |  | 0 | 62.7 |  | 62.7
Mech/Elec_FloorT | 0 | 1070 | 15 | 0.15 |  | 0 | 160.5 |  | 160.5
Conference_N_FloorT | 26.0634 | 789.8 | 15 | 0.15 |  | 390.951 | 118.47 |  | 390.951
Conference_W_FloorT | 11.1025 | 336.44 | 15 | 0.15 |  | 166.5378 | 50.466 |  | 166.5378
Conference_S_FloorT | 25.2054 | 763.8 | 15 | 0.15 |  | 378.081 | 114.57 |  | 378.081
Conference_E_FloorT | 14.2956 | 433.2 | 15 | 0.15 |  | 214.434 | 64.98 |  | 214.434
Break_FloorT | 30.03 | 910 | 15 | 0.15 |  | 450.45 | 136.5 |  | 450.45
Storage_FloorT | 0 | 738 | 15 | 0.15 |  | 0 | 110.7 |  | 110.7
Lobby_FloorT | 6.84 | 684 | 15 | 0.15 |  | 102.6 | 102.6 |  | 102.6
Restroom_FloorT | 0 | 1155 | 15 | 0.15 | 9* 25/50 (cfm/unit) | 0 | 173.25 | 225 | 225
Stair/Elevator_FloorT | 0 | 848 | 15 | 0.15 |  | 0 | 127.2 |  | 127.2
Corridor_W_FloorT | 5.0294 | 1005.88 | 15 | 0.15 |  | 75.441 | 150.882 |  | 150.882
Corridor_E_FloorT | 2.9268 | 585.36 | 15 | 0.15 |  | 43.902 | 87.804 |  | 87.804
Plenum_FloorT | 0 | 38352.015 | 15 |  |  | 0 | 0 |  | 0
Background Data [To be deleted prior to publication]

## Water Heater
Water Heater - OfficeLarge
Vintage | WH Type | Efficiency | Tank Volume (gal) | Tank Loss | Unit | Source
Existing | Gas | 80% | 183 | 1771.9389 | Btu/hr | Fuel Type based on CEUS
New Construction | Gas | 80% | 183 | 1771.9389 | Btu/hr
Peak Hot Water Consumption
Space Name | Baseline WH Type [T24, 2022, Appendix 5.4A , sheet: "2022 SpaceFuncData-Input"] | Total Area (ft²) | Number of People | Hot Water Usage Specification (gal/hr per person) [T24, 2022, Appendix 5.4A , sheet: "2022 SpaceFuncData-Input"] | Peak Hot Water Usage (gal/hr) | Peak Hot Water Usage (gal/min)
Perimeter_Open_ Office_N_Basement | Gas | 8416.86 | 42.0843 | 0.18 | 7.5752 | 0.12625
Perimeter_Open_ Office_S_Basement | Gas | 3662.18 | 18.3109 | 0.18 | 3.296 | 0.054933
Core_Enclosed_Office_Basement | Gas | 3703.68 | 18.5184 | 0.18 | 3.3333 | 0.055555
Server_Room_Basement | Gas | 8228 | 0 | 0.18 | 0 | 0
Mech/Elec_Basement | Gas | 7958 | 0 | 0.18 | 0 | 0
Conference_Basement | Gas | 579.7 | 19.1301 | 0.09 | 1.7217 | 0.028695
Break_Basement | Gas | 973 | 32.109 | 0.09 | 2.8898 | 0.048164
Storage_Basement |  | 1231 | 0 | 0 | 0 | 0
Restroom_Basement |  | 986 | 0 | 0 | 0 | 0
Lobby_Basement | Gas | 707 | 7.07 | 0.09 | 0.6363 | 0.010605
Stair/Elevator_Basement |  | 941 | 0 | 0 | 0 | 0
Corridor_W_Basement |  | 262.9 | 1.3145 | 0 | 0 | 0
Corridor_E_Basement |  | 703 | 3.515 | 0 | 0 | 0
Perimeter_Open_ Office_N_FloorG | Gas | 7031 | 35.155 | 0.18 | 6.3279 | 0.10546
Perimeter_Open_ Office_W_FloorG | Gas | 5795.76 | 28.9788 | 0.18 | 5.2162 | 0.086936
Perimeter_Open_ Office_E_FloorG | Gas | 5875.48 | 29.3774 | 0.18 | 5.2879 | 0.088132
Perimeter_Enclosed_ Office_NE_FloorG | Gas | 917.38 | 4.5869 | 0.18 | 0.82564 | 0.013761
Perimeter_Enclosed_ Office_NW_FloorG | Gas | 1130.61 | 5.653 | 0.18 | 1.0175 | 0.016959
Core_Enclosed_Office_FloorG | Gas | 3312 | 16.56 | 0.18 | 2.9808 | 0.04968
Server_Room_FloorG | Gas | 417.94 | 0 | 0.18 | 0 | 0
Mech/Elec_FloorG | Gas | 849 | 0 | 0.18 | 0 | 0
Conference_FloorG | Gas | 790 | 26.07 | 0.09 | 2.3463 | 0.039105
Break_FloorG | Gas | 618.05 | 20.3956 | 0.09 | 1.8356 | 0.030593
FoodPrep_FloorG | Gas | 936.94 | 2.8108 | 0.578 | 1.6247 | 0.027078
Storage_FloorG | Gas | 959.02 | 0 | 0 | 0 | 0
Locker_FloorG | Gas | 1814.97 | 18.1497 | 0.578 | 10.4905 | 0.17484
Lobby_S_FloorG | Gas | 3360.63 | 33.6063 | 0.09 | 3.0246 | 0.050409
Lobby_FloorG | Gas | 683.36 | 6.8336 | 0.09 | 0.61502 | 0.01025
Restroom_FloorG |  | 1156 | 0 | 0 | 0 | 0
Stair/Elevator_FloorG |  | 848 | 0 | 0 | 0 | 0
Corridor_W_FloorG |  | 1005.88 | 5.0294 | 0 | 0 | 0
Corridor_E_FloorG |  | 798.11 | 3.9906 | 0 | 0 | 0
Plenum_FloorG |  | 38352.015 | 0 | 0 | 0 | 0
Perimeter_Open_ Office_N_FloorM | Gas | 71312.9 | 356.5645 | 0.18 | 64.1816 | 1.0697
Perimeter_Open_ Office_S_FloorM | Gas | 52373.7 | 261.8685 | 0.18 | 47.1363 | 0.78561
Perimeter_Open_ Office_E_FloorM | Gas | 44704.4 | 223.522 | 0.18 | 40.234 | 0.67057
Perimeter_Open_ Office_W_FloorM | Gas | 44487.6 | 222.438 | 0.18 | 40.0388 | 0.66731
Perimeter_Enclosed_ Office_NE_FloorM | Gas | 9173.8 | 45.869 | 0.18 | 8.2564 | 0.13761
Perimeter_Enclosed_ Office_NW_FloorM | Gas | 11312.1 | 56.5605 | 0.18 | 10.1809 | 0.16968
Perimeter_Enclosed_ Office_SW_FloorM | Gas | 10104.9 | 50.5245 | 0.18 | 9.0944 | 0.15157
Perimeter_Enclosed_ Office_SE_FloorM | Gas | 10334.8 | 51.674 | 0.18 | 9.3013 | 0.15502
Core_Enclosed_ Office_FloorM | Gas | 32330 | 161.65 | 0.18 | 29.097 | 0.48495
Server_Room_FloorM | Gas | 4180 | 0 | 0.18 | 0 | 0
Mech/Elec_FloorM | Gas | 10700 | 0 | 0.18 | 0 | 0
Conference_N_FloorM | Gas | 7898 | 260.634 | 0.09 | 23.4571 | 0.39095
Conference_W_FloorM | Gas | 3364.4 | 111.0252 | 0.09 | 9.9923 | 0.16654
Conference_S_FloorM | Gas | 7638 | 252.054 | 0.09 | 22.6849 | 0.37808
Conference_E_FloorM | Gas | 4332 | 142.956 | 0.09 | 12.866 | 0.21443
Break_FloorM | Gas | 9100 | 300.3 | 0.09 | 27.027 | 0.45045
Storage_FloorM |  | 7380 | 0 | 0 | 0 | 0
Lobby_FloorM | Gas | 6840 | 68.4 | 0.09 | 6.156 | 0.1026
Restroom_FloorM |  | 11550 | 0 | 0 | 0 | 0
Stair/Elevator_FloorM |  | 8480 | 0 | 0 | 0 | 0
Corridor_W_FloorM |  | 10058.8 | 50.294 | 0 | 0 | 0
Corridor_E_FloorM |  | 5853.6 | 29.268 | 0 | 0 | 0
Plenum_FloorM |  | 383520.15 | 0 | 0 | 0 | 0
Perimeter_Open_ Office_N_FloorT | Gas | 7131.29 | 35.6564 | 0.18 | 6.4182 | 0.10697
Perimeter_Open_ Office_S_FloorT | Gas | 5237.37 | 26.1868 | 0.18 | 4.7136 | 0.078561
Perimeter_Open_ Office_E_FloorT | Gas | 4470.44 | 22.3522 | 0.18 | 4.0234 | 0.067057
Perimeter_Open_ Office_W_FloorT | Gas | 4448.76 | 22.2438 | 0.18 | 4.0039 | 0.066731
Perimeter_Enclosed_ Office_NE_FloorT | Gas | 917.38 | 4.5869 | 0.18 | 0.82564 | 0.013761
Perimeter_Enclosed_ Office_NW_FloorT | Gas | 1131.21 | 5.6561 | 0.18 | 1.0181 | 0.016968
Perimeter_Enclosed_ Office_SW_FloorT | Gas | 1010.49 | 5.0524 | 0.18 | 0.90944 | 0.015157
Perimeter_Enclosed_ Office_SE_FloorT | Gas | 1033.48 | 5.1674 | 0.18 | 0.93013 | 0.015502
Core_Enclosed_ Office_FloorT | Gas | 3233 | 16.165 | 0.18 | 2.9097 | 0.048495
Server_Room_FloorT | Gas | 418 | 0 | 0.18 | 0 | 0
Mech/Elec_FloorT | Gas | 1070 | 0 | 0.18 | 0 | 0
Conference_N_FloorT | Gas | 789.8 | 26.0634 | 0.09 | 2.3457 | 0.039095
Conference_W_FloorT | Gas | 336.44 | 11.1025 | 0.09 | 0.99923 | 0.016654
Conference_S_FloorT | Gas | 763.8 | 25.2054 | 0.09 | 2.2685 | 0.037808
Conference_E_FloorT | Gas | 433.2 | 14.2956 | 0.09 | 1.2866 | 0.021443
Break_FloorT | Gas | 910 | 30.03 | 0.09 | 2.7027 | 0.045045
Storage_FloorT |  | 738 | 0 | 0 | 0 | 0
Lobby_FloorT | Gas | 684 | 6.84 | 0.09 | 0.6156 | 0.01026
Restroom_FloorT |  | 1155 | 0 | 0 | 0 | 0
Stair/Elevator_FloorT |  | 848 | 0 | 0 | 0 | 0
Corridor_W_FloorT |  | 1005.88 | 5.0294 | 0 | 0 | 0
Corridor_E_FloorT |  | 585.36 | 2.9268 | 0 | 0 | 0
Plenum_FloorT |  | 38352.015 | 0 | 0 | 0 | 0
Water Heater Capacity, Tank Capacity, and Tank Loss
WH Type | Peak Hot Water Usage (gal/hr) | Heat Output (Btu/hr) [ACM, 2025, 5.9.2: Rated capacity section] | WH Capacity (Btu/hr) [ACM, 2025, 5.9.2: Rated capacity section] | Required Energy Input (Btu/hr) | Storage Volume (gal) | Standby Loss |  | Off/On Cycle Loss Coefficient to Ambient Temp (Btu/h-F) | Source
Gas Storage WH | 456.7194 | 302812.2451 | 181687.3471 | 227109.1838 | 183 | 1771.9389 | Btu/hr | 26.0579 | Standby loss equation: Title 20, §1605.1 Table F-4 WH capacity equation: ACM, 2025, 5.9.2: Rated capacity section)
Electric resistance WH | 0 | 0 | 0 | 0 | 0 | 0 | %/hr | 0
Total | 456.7194 |  |  |  | 182.6877
Design supply temperature (F) | 135 | Ref: T24 2022 - Appendix 5.4B
Cold Water supply temperature (F) | 55 | Ref: ACM, 2025, 5.9.2: Rated capacity section
WH system factor | 0.6 | Ref: ACM, 2025, 5.9.2: Rated capacity section
Reheat multiplier | 0.4 | Ref: ACM, 2025, 5.9.2: Storage Volume
* The 0.40 multiplier is a storage sizing factor used to account for the fact that the water heater doesn't need to store the full peak hour demand—it can reheat water during that time. This factor assumes that the heater will recover part of the hot water used during the peak hour, so only 40% of the peak hour demand needs to be stored at any given moment.
Ambient temp | 68
Delta T | 67
Background Data [To be deleted prior to publication]

## Interior Lights
Interior Lighting - OfficeLarge
Space Type | New Construction |  |  | Existing |  |  | Note
| LPD (W/ft²) | Additional LPD for Portable Lighting (W/ft²) | Source | LPD (W/ft²) | Additional LPD for Portable Lighting (W/ft²) | Source
Office Area (>250 square feet) | 0.6 |  | T24, part 6, 2025, Table 140.6 C For Computer and Server room: Engineering Judgement | 0.75 |  | T24, part 6, 2013, Table 140.6 C For Computer and Server room: Engineering Judgement
Convention, Conference, Multipurpose and Meeting Area | 0.75 |  |  | 1.4
Lobby, Main Entry | 0.7 |  |  | 1.1
Locker Room | 0.45 |  |  | 0.8
Storage (General) | 0.4 |  |  | 0.6
Electrical, Mechanical, Telephone Rooms | 0.4 |  |  | 0.7
Server Room (EPD 45) | 1.1 |  |  | 1.1
Computer Room (EPD 20) | 1.1 |  |  | 1.1
Restrooms | 0.6 |  |  | 0.6
Lounge, Breakroom, or Waiting Area | 0.55 |  |  | 1,1
Kitchen/Food Preparation Area | 0.95 |  |  | 1.6
Stairwell | 0.6 |  |  | 0.6
Corridor Area | 0.4 |  |  | 0.6
Plenum
Whole Building method
| 2025 | 2013
LPD for Office Building ((W/ft²) | 0.6 | 0.8 | Ref: T24, Table 140.6 B
Background Data [To be deleted prior to publication]

## Ext Lighting
Exterior Lighting - OfficeLarge
Motion Controlled Luminaires (W) | Non-motion Controlled Luminaires (W) | Total (W) | Source
15940.1308 | 1548.9586 | 17489.0894 | Title 24, 2022
Exterior Lighting
Items (Assume LZ2) | Assumptions [2019 Outdoor Lighting CASE Report & PNNL 90.1-2010 TSD] |  | Unit | Lighting Power Allowance [T24, 2025, Table 140.7-A & 140.7-B] | Unit | Exterior Lighting Power (W)
IWA (Initial Wage Allowance) |  |  |  | 200 | (W) | 200
Parking area | 400 ft² for every parking space 1 parking space per 250 ft² of gross building area | 797619.76 | (ft²) | 0.019 | (W/ft²) | 15154.7754
Building Entrance | 2 building entrance (1 per 10,000 ft² footprint) | 4 | (count) | 15 | (W/ea) | 60
Hardscape Ornamental Light | 0.1 ft² per 1 ft² of gross building area for hardscape ornamental light | 49851.235 | (ft²) | 0.007 | (W/ft²) | 348.9586
Building façade | 0.1 W per ft² of facade area Façade Area* = Perimeter × 0.5 × 30 ft (30 ft is the max height that is lit) The 0.5 factor assumes that only half of the perimeter walls are lit. -Formula ia developed based on the 2019 Outdoor Lighting CASE report | 12000 | (ft²) | 0.1 | (W/ft²) | 1200
Non-sales canopy |  | 3834.7104 | (ft²) | 0.137 | (W/ft²) | 525.3553
Motion controlled Luminaires | [5 empty] | 15940.1308
Non-motion-controlled Luminaires | [5 empty] | 1548.9586
Total | [5 empty] | 17489.0894
*Developed based on 2019 Outdoor Lighting CASE Report
Perimeter (ft) | 800
Total floor area (ft²) | 498512.35
Floors (above ground) | 12
Floors (all) | 13
Background Data [To be deleted prior to publication]

## Equipment
Equipment - OfficeLarge
Space Type | Plug load Power Density (W/ft²) | Gas Power Density (Btu/hr-ft²) | Refrigeration Power Density (W/ft²) | Source
Office Area (>250 square feet) | 0.7 |  |  | Plug load and schedule project with CEC, 2025
Server Room (EPD 45) | 45 |  |  | PNNL ASHRAE 90.1 2022
Computer Room (EPD 20) | 20 |  |  | Based on PNNL ASHRAE 90.1 2022 assumptions and minimum load for computer room
Electrical, Mechanical, Telephone Rooms | 0.5 |  |  | T24 2022 - Appendix 5.4A
Lounge, Breakroom, or Waiting Area | 0.5
Convention, Conference, Multipurpose and Meeting Area | 0.8
Storage (General) | 0.2
Locker Room | 0.5
Kitchen/Food Preparation Area | 1.5
Lobby, Main Entry | 0.5
Restrooms | 0
Stairwell | 0
Corridor Area | 0
Plenum | 0
OfficeLarge prototype is assumed to have a transformer, and its losses will be explicitly modeled.
Elevator
Vintages | No of Elevator | Design Load (W) | Source
New Construction and Existing | 10 | 140657.19 | PNNL Large Office prorotype
Assumptions for elevators:
One elevator for approximately 50,000 ft² in use. |  |  |  |  | https://buildingandinteriors.com/find-the-magic-number-elevators-per-building/
For every two floors or two and a half floors, one more elevator was added.
An in-use rate of 70% for the floor area was assumed, based on engineering judgment.
Calculated number of Elevators: |  | 10
Calculate Elevator load (kw)based on ACM 2022: |  | 100 | 140.7 kW is PNNL ASHRE 90.1 2019 elevator load (Design level + Light/Fan) |  | 140.6572
ACM 2022 suggestion for elevator load (kw): |  | 10
Elevator load will be defined as exterior load not equipment load (Same as PNNL ASHRAE 90.1 Large Hotel prototype).
If we consider 10 elevators, the total load (10 × 10 kW) would be 100 kW, which is 40% lower than the PNNL assumption. However, CBECC considered both elevator and Escalator for medium office prototype (10,000 for elevator and 3930 per Escalator) for a 3 stoy, 50 k office buildings. Since elevator load is not typically climate-dependent, we will adopt the PNNL value for the Large Office prototype.
Background Data [To be deleted prior to publication]

## Schedules
Schedules - OfficeLarge
Zone | Schedule Category | Schedule | Source | Type | Hour
[5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
All zones | Office | Occupancy | T24 2022 - Appendix 5.4B, [Office] Updated base on Plug load and schedules project with CEC, 2025 | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
All zones | Office | Lights | T24 2022 - Appendix 5.4B, [Office] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.35 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
All zones | Office | ElecEquipment | Plug load and schedules project with CEC, 2025 | Weekday | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.74 | 0.87 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.5 | 0.45 | 0.45 | 0.45
|  |  |  | Saturday | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43
|  |  |  | Sunday | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43
All zones | Office | HVACAvail | T24 2022 - Appendix 5.4B, [Office] Updated base on Plug load and schedules project with CEC, 202 | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
All zones | Office | ServiceHotWater | T24 2022 - Appendix 5.4B, [Office] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.12 | 0.14 | 0.07 | 0.07 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05
|  |  |  | Sunday | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04
All zones | Office | Infiltration | T24 2022 - Appendix 5.4B, [Office] Updated base on Plug load and schedules project with CEC, 202 | Weekday | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
All zones | Office | HtgSetpt |  | Weekday | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
|  |  |  | Saturday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  |  | Sunday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
All zones | Office | ClgSetpt |  | Weekday | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
|  |  |  | Saturday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
|  |  |  | Sunday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
Data
Server rooms | Data | Occupancy | T24 2022 - Appendix 5.4B, [Data] Updated base on office schedule | Weekday | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.25 | 0.65 | 0.65 | 0.65 | 0.65 | 0.6 | 0.6 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.25 | 0.1 | 0.05 | 0.05 | 0.05 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0
Server rooms | Data | Lights | T24 2022 - Appendix 5.4B, [Data] Updated base on office schedule | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.7 | 0.8 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.8 | 0.35 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05
Server rooms | Data | HVACAvail | T24 2022 - Appendix 5.4B, [Data] | Weekday | bar: Hour 1 to Hour 24
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
Server rooms | Data | ServiceHotWater | T24 2022 - Appendix 5.4B, [Data] | Weekday | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.9 | 0.9 | 0.5 | 0.5 | 0.7 | 0.5 | 0.5 | 0.5 | 0.1 | 0.1 | 0.1 | 0.1 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Server rooms | Data | Infiltration | T24 2022 - Appendix 5.4B, [Data] | Weekday | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  |  | Saturday | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  |  | Sunday | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Server rooms | Data | ClgSetpt | Based on Activity level and thermostat setpoint | Weekday | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
|  |  |  | Saturday | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
|  |  |  | Sunday | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
Other
| Building | Elevator | T24 2022 - Appendix 5.4B, [Office] Updated base on Plug load and schedules project with CEC, 202 | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Building | ExtLightingNonMotionCtrl |  | Weekday | bar: Hour 1 to Hour 24
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
| Building | ExtLightingMotionCtrl |  | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Office | Building | FunctionalAreaPeopleActivityLevel | Based on Activity level schedules in CEC Prototypes | Weekday | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
|  |  |  | Saturday | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
|  |  |  | Sunday | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
Server room | Building | ComputerRoomPeopleActivityLevel | Based on Activilty level schedules in CEC Prototypes | Weekday | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
|  |  |  | Saturday | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
|  |  |  | Sunday | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
Conference room | Building | MeetingAreaPeopleActivityLevel | Based on Activilty level schedules in CEC Prototypes | Weekday | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2
|  |  |  | Saturday | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2
|  |  |  | Sunday | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2
Corridor, Stair, Lobby, Restroom, Mech, Storage, Break | Building | CommonAreaPeopleActivityLevel | Based on Activilty level schedules in CEC Prototypes | Weekday | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5
|  |  |  | Saturday | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5
|  |  |  | Sunday | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5
Kitchen/Food prep | Building | KitchenPeopleActivityLevel | Based on Activilty level schedules in CEC Prototypes | Weekday | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8
|  |  |  | Saturday | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8
|  |  |  | Sunday | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8
Locker | Building | LockerRoomPeopleActivityLevel | Based on Activilty level schedules in CEC Prototypes | Weekday | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9
|  |  |  | Saturday | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9
|  |  |  | Sunday | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9
Background Data [To be deleted prior to publication]
Operating Schedule
| System Capacity fraction | Developed based on CEC and CEUS |  | Weekday
Saturday
Alternative HVAC System Operating
| Alternative HVAC System Operating | Developed based on CEC schedules and CEUS operating hours |  | Weekday
Saturday
Otherday
Weekday
Saturday
Otherday

## Energy Usage
CalBEM Energy Consumption - OfficeLarge | [7 empty] | National Average (EnergyStar Portfolio Manager) |  |  |  |  | CEUS Energy Consumption - OfficeLarge
Prototype | CZ | CalBEM Electricity EUI (KBTU/ft²) | CalBEM Gas EUI (KBTU/ft²) | CalBEM Total EUI (KBTU/ft²) | New Construction Electricity EUI (KBTU/ft²) | New Construction Gas EUI (KBTU/ft²) | New Construction Total EUI (KBTU/ft²) | National Average | Acceptable RangeRange (25% Higher) | Acceptable RangeRange (25% Lower) | National Average Acceptable Range | Zip code | Prototype | CZ | Total Floorspace (Thousand of ft2) | CEUS 2022 Electric Energy Intensity (kWh/ft²) | CEUS 2022 Annual Gas Intensity (kWh/ft²) | CEUS 2022 Total EUI (kBtu/ft²) | Acceptable Range (25% Higher) | Acceptable Range (25% Lower) | CEUS 2022 Acceptable Range
HotelSmall | 1 | 47.7 | 9.7 | 57.4 | 44.8 | 8.2 | 53.1 | 71.5 | 89.375 | 53.625 | 35.75 | 95521 | Large Office | 1 | 5279 | 16.7 | 5.01 | 74.0745 | 92.5932 | 55.5559 | 37.0373
| 2 | 56 | 8.5 | 64.5 | 47.9 | 7.3 | 55.3 | 77.3 | 96.625 | 57.975 | 38.65 | 95476 |  | 2 | 12449 | 15.2 | 6.24 | 73.1533 | 91.4416 | 54.865 | 36.5766
| 3 | 52 | 7.6 | 59.6 | 46.7 | 6.9 | 53.5 | 74 | 92.5 | 55.5 | 37 | 94612 |  | 3 | 242565 | 14.3 | 4.83 | 65.2716 | 81.5895 | 48.9537 | 32.6358
| 4 | 56.6 | 7.5 | 64.1 | 50.4 | 6.5 | 56.9 | 79.5 | 99.375 | 59.625 | 39.75 | 93446 |  | 4 | 137610 | 14.4 | 4.76 | 65.3739 | 81.7174 | 49.0304 | 32.687
| 5 | 53.2 | 7.8 | 61 | 48.1 | 7.1 | 55.2 | 71.4 | 89.25 | 53.55 | 35.7 | 93455 |  | 5 | 3834 | 8.6 | 9.32 | 61.143 | 76.4288 | 45.8573 | 30.5715
| 6 | 53.4 | 5.4 | 58.8 | 49.8 | 4.9 | 54.7 | 80.8 | 101 | 60.6 | 40.4 | 93550 |  | 6 | 109980 | 10.9 | 4.88 | 53.8414 | 67.3017 | 40.381 | 26.9207
| 7 | 55.4 | 5.3 | 60.7 | 49.8 | 4.6 | 54.4 | 76.7 | 95.875 | 57.525 | 38.35 | 92101 |  | 7 | 76710 | 14.8 | 9.36 | 82.4339 | 103.0424 | 61.8254 | 41.217
| 8 | 55.3 | 5.4 | 60.7 | 51.4 | 5 | 56.4 | 77.6 | 97 | 58.2 | 38.8 | 92831 |  | 8 | 177013 | 10.4 | 4.24 | 49.9517 | 62.4396 | 37.4638 | 24.9758
| 9 | 56.2 | 5.6 | 61.9 | 51 | 5.1 | 56.1 | 77.7 | 97.125 | 58.275 | 38.85 | 91505 |  | 9 | 240000 | 10.9 | 4.38 | 52.1354 | 65.1692 | 39.1015 | 26.0677
| 10 | 55.8 | 5.5 | 61.2 | 51.7 | 5.2 | 56.9 | 78.1 | 97.625 | 58.575 | 39.05 | 92501 |  | 10 | 65927 | 11.9 | 7.21 | 65.2033 | 81.5041 | 48.9025 | 32.6017
| 11 | 51.5 | 6.7 | 58.2 | 51.2 | 6.3 | 57.5 | 80.3 | 100.375 | 60.225 | 40.15 | 96080 |  | 11 | 18413 | 11.4 | 4.29 | 53.5343 | 66.9179 | 40.1507 | 26.7671
| 12 | 54.2 | 7.1 | 61.3 | 50 | 6.4 | 56.3 | 79.6 | 99.5 | 59.7 | 39.8 | 95814 |  | 12 | 171620 | 14.4 | 6.12 | 70.0142 | 87.5178 | 52.5107 | 35.0071
| 13 | 55 | 6.2 | 61.2 | 51.3 | 5.7 | 57 | 80 | 100 | 60 | 40 | 93721 |  | 13 | 19959 | 15.9 | 3.71 | 66.9093 | 83.6366 | 50.182 | 33.4547
| 14 | 54.6 | 6.1 | 60.7 | 51.7 | 5.6 | 57.4 | 80.8 | 101 | 60.6 | 40.4 | 93550 |  | 14 | 18934 | 9.8 | 4.4 | 48.4504 | 60.563 | 36.3378 | 24.2252
| 15 | 58.2 | 4.1 | 62.3 | 54.9 | 4.2 | 59.1 | 79.5 | 99.375 | 59.625 | 39.75 | 92262 |  | 15 | 23127 | 9.7 | 5.14 | 50.6341 | 63.2926 | 37.9756 | 25.317
| 16 | 50.1 | 7.7 | 57.8 | 49.3 | 6.2 | 55.5 | 82.3 | 102.875 | 61.725 | 41.15 | 95715 |  | 16 | 39406 | 11.6 | 4.42 | 54.6602 | 68.3253 | 40.9952 | 27.3301
Ref: CEUS 2022 Report
And by applying FZ-CZ multipliers for converting FZ data to CZ data
Background Data [To be deleted prior to publication]

## Weights
% of floor area per CZ and vintage bin - OfficeLarge
Prototype | CZ | Vintage Bin | [5 empty] | Floor area distribution of CA office buildings (CEUS 2022)
|  | Pre-1978 | 1978-1997 | 1998-2007 | 2008-2018 | Not available |  | Office, Small | Office, Medium | Office, Large
OfficeSmall | 1 | 58.42% | 23.37% | 8.059% | 3.566% | 6.59% | 100% | 35.39% | 29.43% | 35.18%
| 2 | 49.15% | 36.42% | 14.39% | 0.01642% | 0.03034% | 100%
| 3 | 39.04% | 34.62% | 15.64% | 7.994% | 2.703% | 100%
| 4 | 39.42% | 34.19% | 15.72% | 8.051% | 2.62% | 100%
| 5 | 18.23% | 72.98% | 3.482% | 3.023% | 2.286% | 100%
| 6 | 33.04% | 40.09% | 15.45% | 6.416% | 5.004% | 100%
| 7 | 16.64% | 53.22% | 21.55% | 6.978% | 1.606% | 100%
| 8 | 35.09% | 41.33% | 11.31% | 5.179% | 7.09% | 100%
| 9 | 38.4% | 40.67% | 9.23% | 6.323% | 5.384% | 100%
| 10 | 16.2% | 41.33% | 26.42% | 9.855% | 6.194% | 100%
| 11 | 46.79% | 16.13% | 14.62% | 8.828% | 13.62% | 100%
| 12 | 37.43% | 31.21% | 16.49% | 8.794% | 6.067% | 100%
| 13 | 68.74% | 13.07% | 3.979% | 4.987% | 9.218% | 100%
| 14 | 21.03% | 41.59% | 21.25% | 6.024% | 10.11% | 100%
| 15 | 30.2% | 16.76% | 25.29% | 17.74% | 10.02% | 100%
| 16 | 27.08% | 30.95% | 23.93% | 6.613% | 11.43% | 100%
| Statewide | 34.88% | 38.18% | 15.17% | 7.116% | 4.65%
Ref: CEUS 2022 dataset
Ref: Dodge 2023
Background Data [To be deleted prior to publication]

## PV (hidden)
PV - OfficeLarge

## EV Charger (hidden)
EV Charger - OfficeLarge
Background Data [To be deleted prior to publication]

## Data (hidden)
Space Function | Electric Equipment Load Intensity | Electric Equipment Load Intensity | LPD
Aging Eye/Low-vision (Corridor Area) |  |  | 2013 | 2016 | 2019 | 2025
Aging Eye/Low-vision (Dining)
Aging Eye/Low-vision (Lobby, Main Entry)
Aging Eye/Low-vision (Lounge/Waiting Area)
Aging Eye/Low-vision (Multipurpose Room)
Aging Eye/Low-vision (Religious Worship Area)
Aging Eye/Low-vision (Restroom)
Aging Eye/Low-vision (Stairwell)
Audience Seating Area
Auditorium Area
Auto Repair / Maintenance Area
Barber, Beauty Salon, Spa Area
Civic Meeting Place Area
Classroom, Lecture, Training, Vocational Areas
Concourse and Atria Area
Convention, Conference, Multipurpose and Meeting Area
Copy Room
Corridor Area
Dining Area (Bar/Lounge and Fine Dining)
Dining Area (Cafeteria/Fast Food)
Dining Area (Family and Leisure)
Electrical, Mechanical, Telephone Rooms
Exercise/Fitness Center and Gymnasium Areas
Financial Transaction Area
Healthcare Facility and Hospitals (Exam/Treatment Room)
Healthcare Facility and Hospitals (Imaging Room)
Healthcare Facility and Hospitals (Medical Supply Room)
Healthcare Facility and Hospitals (Nursery)
Healthcare Facility and Hospitals (Nurse's Station)
Healthcare Facility and Hospitals (Operating Room)
Healthcare Facility and Hospitals (Patient Room)
Healthcare Facility and Hospitals (Physical Therapy Room)
Healthcare Facility and Hospitals (Recovery Room)
Hotel Function Area
Kitchen/Food Preparation Area
Kitchenette or Residential Kitchen
Laboratory, Scientific
Laundry Area
Library (Reading Area)
Library (Stacks Area)
Lobby, Main Entry
Locker Room
Lounge, Breakroom, or Waiting Area
Manufacturing, Commercial & Industrial Work Area (Low Bay)
Manufacturing, Commercial & Industrial Work Area (High Bay)
Manufacturing, Commercial & Industrial Work Area (Precision)
Museum Area (Exhibition/Display)
Museum Area (Restoration Room)
Office Area (>250 square feet)
Office Area (<250 square feet)
Parking Garage Area (Parking Zone and Ramps)
Parking Garage Area (Daylight Adaptation Zones)
Pharmacy Area
Retail Sales Area (Grocery Sales)
Retail Sales Area (Retail Merchandise Sales)
Retail Sales Area (Fitting Room)
Religious Worship Area
Restrooms
Stairwell
Storage, Commercial/Industrial (Warehouse)
Storage, Commercial/Industrial (Refrigerated)
Storage, Commercial/Industrial (Shipping & Handling)
Storage (General)
Sports Arena - Playing Area (> 5,000 Spectators)
Sports Arena - Playing Area (2,000 - 5,000 Spectators)
Sports Arena - Playing Area (< 2,000 Spectators)
Sports Arena - Playing Area (Recreational)
Theater Area (Motion Picture)
Theater Area (Performance)
Transportation Function (Baggage Area)
Transportation Function (Ticketing Area)
Videoconferencing Studio
High-Rise Residential Living Spaces
Hotel/Motel Guest Room
All other
Attic
Reception Area
Elevator
Plenum
IT Room (EPD 12)
Computer Room (EPD 20)
Server Room (EPD 45)