## Comments (hidden)
Comments | By | Date | Action
How about considering punched windows not one large window? | Liam Buckley | TAG meeting 2/24/2025 | There is other improvement we can apply to our models that could have a greater impact than replacing ribbon window with punched windows. For example, more accurate schedules. Additionally, many medium/large office buildings have already been constructed with ribbon windows, making them a common feature in these types of buildings. We reviewed some of the Comstock models and found that they are also developed with ribbon windows.
It's more realistic to seperate corner zones and assined them with their own CAV system ( for vintage 1&2) or with VAV | Liam Buckley | TAG meeting 2/24/2025 | We will investigate the impact of separating corner spaces after completing the development of the first set of medium office prototypes in CZ12. We are considering two options : - Separating corner parts of the perimeter closed office zones at the west-south and east-south corners and defining them as new corner zones. - Dividing conference spaces into two and relocating them to the corners, then defining them as separate zones."
conference spaces are expected to have different schedules than office spaces | ? | TAG meeting 2/24/2025
Considering two enterance for the Medium Office prototype
generating a set of dynamic occupancy schedules to bring random variations to the occupancy schedules. The Occupancy Simulator developed by Lawrence Berkeley National Laboratory (Chen et al. 2018) can be used to generate the dynamic and stochastic occupancy schedules |  |  | https://publications.ibpsa.org/proceedings/simbuild/2020/papers/simbuild2020_C064.pdf
Add Schedule for IT room

## Notes
Data Sources
Dataset | Dodge 2023
| CEUS 2022 | https://www.energy.ca.gov/publications/2023/2022-california-commercial-end-use-survey-ceus-final-report
| CBECS 2018 | https://www.eia.gov/consumption/commercial/data/2018/index.php?view=microdata
| Comstock 2023 | https://data.openei.org/s3_viewer?bucket=oedi-data-lake&prefix=nrel-pds-building-stock%2Fend-use-load-profiles-for-us-building-stock%2F2023%2Fcomstock_amy2018_release_2%2Fmetadata_and_annual_results%2Fby_state%2Fstate%3DCA%2F
Prototype | CEC Medium Office prototype (CBECC 2022.3.1) | https://bees.noresco.com/software2022.html
| PNNL Medium Office prototype (90.1-2022) | https://www.energycodes.gov/prototype-building-models#Commercial
| DEER Large Office prototype (June 2023) | https://github.com/sound-data/DEER-Prototypes-EnergyPlus
| ORNL 2019 Medium Office prototype zoning | https://web.eecs.utk.edu/~jnew1/publications/2019_IBPSA_OpenStudioOffice.pdf
Codes | Title 24, part 6, referred to as T24 (1984, 2001, 2008, 2010, 2013, 2022, 2025)
ASHRAE 90.1 (2022)
| CFR Title 10 ( 2024) | https://www.govinfo.gov/content/pkg/CFR-2024-title10-vol3/pdf/CFR-2024-title10-vol3-part431-subpartF.pdf
Others | ACM (2022)
| Title 24, 2022 - Appendix 5.4A and Appendix 5.4B | https://www.energy.ca.gov/publications/2022/2022-nonresidential-and-multifamily-alternative-calculation-method-reference
| 2022 Reduced infiltration CASE report | https://title24stakeholders.com/wp-content/uploads/2020/10/2022-T24-Final-CASE-Report_Reduce-Infiltration.pdf
| 2019 Outdoor Lighting CASE Report | https://title24stakeholders.com/wp-content/uploads/2016/10/T24-2019-CASE-Study-Results-Report-Outdoor-Sources_Final_with-Attachments.pdf
| PNNL 20405, 2010 | https://www.pnnl.gov/main/publications/external/technical_reports/PNNL-20405.pdf
| Air leakage Memo, NORESCO, 2025 | Infiltration_rate_report_14May2025-Short-Version.docx
| Proposed Updates to Equipment Power Densities and Building Schedules for the 2028 Energy Code, referred to as "Plug load and schedules project with CEC, 2025" (Docket Number =25-BSTD-03 & TN=265693) | https://efiling.energy.ca.gov/GetDocument.aspx?tn=265693&DocumentContentId=102545
Construction Rate
Notes
| Saturation is defined as the % of total floorspace for each combination of end-use and fuel-type. |  |  | 1978-84 | 1985-97 | 1992-1997
1986 is the representative year for the 1984-1997 vintage bin | Most medium offices in this vintage bin were built after 1984 (more than 54% ) and the CA energy code did not noticeably changed between 1984 to 1992) . Edition 1986 included 6 prescriptive packages per CZ for office buildings compared to 1984 with 3 packages per CZ. Also "Heat Capacity" for external wall is considered between 10.0 to 14.99 (BTU/F/ft2) Package A was selected for the thermal properties Medium office was considered as low rise office |  | Construction rate (Dodge 2023 data for new medium offices) | 46.19% | 53.81% | 12.39%
2001 is the representative year for the 1998-2007 vintage bin | Wall and roof prescriptive criteria from 1998 to 2005 remain unchanged except for CZ2 and 6 in 2001 version (the percentage of change is less than 10%). Since the construction rate between 1998-2005 is greater than the 2006-2007 period, the envelope properties of 1998 -2005 were chosen for envelope properties. The windows requirement considerably changed in the 2001 code and makes this year (2001) as the nominated year for this vintage. It should be noticed that, only one Title 24 should be chosen within each vintage bin for building envelope properties since the entire envelope is built at once. We can't choose 1998 for walls and 2001 for windows. Wall and roof prescriptive criteria from 1998 to 2005 remain unchanged except for CZ2 and 6 in 2001 version (the percentage of change is less than 10%).
2013 is the representative year for the 2008-2018 vintage bin | Wall properties remain unchanged from the 2008 code to the 2016 code but the roof did changed. Although the 2016 code introduced improvement for roof in nearly all CZ and for wall in a few CZ, and construction activity surged between 2017 and 2018, the extende period from 2008 to 2016 resulted in a higher construction rate during that time . As a result, it was decided to select the code that was effective during 2008-2016. The 2013 code modified the solar reflectance requirement for low-sloped roof products ( by approximately 15%), and enhanced window properties. Therefore, the 2013 code was chosen as the representative code. Additionally, construction activity from 2014-2018 was higher compared to 2008-2013 period.

## Prototype
NORESCO, Updated November 2025
OfficeMedium
Characteristic | Value | Data Sources
Building Type | Medium Office
Building Category | Nonresidential
Vintages | 4 Vintages: Pre-1978 , 1978-1997 ,1998-2007 , 2008-2018 New Construction (2019+) | Based on vintage bin analysis | NonRes-Vintage bins-Draft Report-30Nov2023-Final.docx
Shape |  | Rectangular shape is supported by CBECS, CEC, and PNNL
Total Floor Area (ft2) | 53,628 (163.7 ft x 109.2 ft) | Supported by Dodge 2023 data (Same as CEC and PNNL)
Aspect Ratio | 1.5 | Same as CEC and PNNL
Number of Floors | 3 | Supported by Dodge 2023 data (Same as CEC and PNNL) DEER doesn't offer medium office prototype
Roof type | Flat | Supported by CBECS 2018 data (Same as CEC and PNNL)
Window dimensions | 33% (Window Dimensions: 163.8 ft x 4.29 ft on the long side of facade 109.2 ft x 4.29 ft on the short side of the façade) | Same as CEC and PNNL CBECS: 26-50% Comstock:11-25% CEC prototype: 33% same as PNNL DEER: 33% for Large Office prototype
Shading Geometry | No Shades | Same as CEC and PNNL
Floor to floor height (feet) | 13 | Same as CEC and PNNL
Floor to ceiling height (feet) | 9 (4 ft above-ceiling plenum) | Same as CEC and PNNL
Glazing sill height (feet) | 3.35 ft (top of the window is 7.64 ft high with 4.29 ft high glass) | Same as CEC and PNNL

## Zones
Proposed OfficeMedium | [11 empty] | Layout
Space/Thermal Zone | Space Type | HVAC System Name/AHU Name | Schedule Category | Conditioned (Y/N) | Area Fraction | Area (ft²) | Volume (ft³) | Multipliers | Number of People | People (Persons/1,000 ft²) [T24, 2025,Table 120.1-A] | Note
Open_Office_Core_FloorG | Office Area (>250 square feet) |  | Office | Yes | 7.986% | 4283 | 38547 | 1 | 21.415 | 5
Open_Office_N_FloorG | Office Area (>250 square feet) |  | Office | Yes | 4.285% | 2297.9873 | 20681.8859 | 1 | 11.4899 | 5
Closed_Office_W_FloorG | Office Area (>250 square feet) |  | Office | Yes | 3.054% | 1637.8612 | 14740.7504 | 1 | 8.1893 | 5
Closed_Office_E_FloorG | Office Area (>250 square feet) |  | Office | Yes | 3.054% | 1637.8612 | 14740.7504 | 1 | 8.1893 | 5
Open_Office_S_FloorG | Office Area (>250 square feet) |  | Office | Yes | 2.212% | 1186.2075 | 10675.8676 | 1 | 5.931 | 5
Conference_FloorG | Convention, Conference, Multipurpose and Meeting Area |  | Office | Yes | 2.073% | 1111.7798 | 10006.0183 | 1 | 36.6887 | 33 | Number of People: ORNL: 54, T24:33
Lobby/Lounge_FloorG | Lobby, Main Entry |  | Office | Yes | 1.975% | 1059.1755 | 9532.5792 | 1 | 10.5918 | 10 | People: 10 according to ASHRAE 62.1 Table 6-1 for main entry lobbies T24: 33 for main Entry lobbies & 5 for reception area
Storage_FloorG | Storage (General) |  | Office | Yes | 1.833% | 983.1561 | 8848.405 | 1 |  | -
Mechanical/Electrical_FloorG | Electrical, Mechanical, Telephone Rooms |  | Office | Yes | 0.6663% | 357.3503 | 3216.1531 | 1 |  | -
IT-Room_FloorG | IT Room (EPD 12) |  | Data | Yes | 0.3337% | 178.9373 | 1610.4357 | 1 | ? | -
Restroom_FloorG | Restrooms |  | Office | Yes | 1.2% | 643.5778 | 5792.2004 | 1 |  | -
Break_FloorG | Lounge, Breakroom, or Waiting Area |  | Office | Yes | 0.4332% | 232.343 | 2091.0866 | 1 | 7.6673 | 33 | Number of People: T24: 33 for Breakroom
Stairway_FloorG | Stairwell |  | Office | Yes | 1.233% | 661.3923 | 5952.5303 | 1 |  | -
Corridor_W_FloorG | Corridor Area |  | Office | Yes | 0.5594% | 300 | 2700 | 1 | 1.5 | 5
Corridor_N_FloorG | Corridor Area |  | Office | Yes | 0.9379% | 502.9724 | 4526.7516 | 1 | 2.5149 | 5 |  | Layout of Spaces | Spaces
Corridor_E_FloorG | Corridor Area |  | Office | Yes | 0.5579% | 299.2076 | 2692.8684 | 1 | 1.496 | 5
Corridor_S_FloorG | Corridor Area |  | Office | Yes | 0.9379% | 502.9724 | 4526.7516 | 1 | 2.5149 | 5
Plenum_FloorG | Plenum |  | Office | No |  | 17875.9325 | 71503.73 | 1 |  | -
Open_Office_Core_FloorM | Office Area (>250 square feet) |  | Office | Yes | 7.986% | 4283 | 38547 | 1 | 21.415 | 5
Open_Office_N_FloorM | Office Area (>250 square feet) |  | Office | Yes | 4.285% | 2297.9873 | 20681.8859 | 1 | 11.4899 | 5
Closed_Office_W_FloorM | Office Area (>250 square feet) |  | Office | Yes | 3.054% | 1637.8612 | 14740.7504 | 1 | 8.1893 | 5
Closed_Office_E_FloorM | Office Area (>250 square feet) |  | Office | Yes | 3.054% | 1637.8612 | 14740.7504 | 1 | 8.1893 | 5
Open_Office_S_FloorM | Office Area (>250 square feet) |  | Office | Yes | 2.212% | 1186.2075 | 10675.8676 | 1 | 5.931 | 5
Conference_FloorM | Convention, Conference, Multipurpose and Meeting Area |  | Office | Yes | 2.073% | 1111.7798 | 10006.0183 | 1 | 36.6887 | 33
Lobby/Lounge_FloorM | Lobby, Main Entry |  | Office | Yes | 1.975% | 1059.1755 | 9532.5792 | 1 | 10.5918 | 10 | People: 10 according to ASHRAE 62.1 Table 6-1
Storage_FloorM | Storage (General) |  | Office | Yes | 1.833% | 983.1561 | 8848.405 | 1 |  | -
Mechanical/Electrical_FloorM | Electrical, Mechanical, Telephone Rooms |  | Office | Yes | 0.6663% | 357.3503 | 3216.1531 | 1 |  | -
IT-Room_FloorM | IT Room (EPD 12) |  | Data | Yes | 0.3337% | 178.9373 | 1610.4357 | 1 |  | -
Restroom_FloorM | Restrooms |  | Office | Yes | 1.2% | 643.5778 | 5792.2004 | 1 |  | -
Break_FloorM | Lounge, Breakroom, or Waiting Area |  | Office | Yes | 0.4332% | 232.343 | 2091.0866 | 1 | 7.6673 | 33
Stairway_FloorM | Stairwell |  | Office | Yes | 1.233% | 661.3923 | 5952.5303 | 1 |  | -
Corridor_W_FloorM | Corridor Area |  | Office | Yes | 0.5594% | 300 | 2700 | 1 | 1.5 | 5
Corridor_N_FloorM | Corridor Area |  | Office | Yes | 0.9379% | 502.9724 | 4526.7516 | 1 | 2.5149 | 5
Corridor_E_FloorM | Corridor Area |  | Office | Yes | 0.5579% | 299.2076 | 2692.8684 | 1 | 1.496 | 5 |  | Layout of Zones
Corridor_S_FloorM | Corridor Area |  | Office | Yes | 0.9379% | 502.9724 | 4526.7516 | 1 | 2.5149 | 5
Plenum_FloorM | Plenum |  | Office | No |  | 17875.9325 | 71503.73 | 1 |  | -
Open_Office_Core_FloorT | Office Area (>250 square feet) |  | Office | Yes | 7.986% | 4283 | 38547 | 1 | 21.415 | 5
Open_Office_N_FloorT | Office Area (>250 square feet) |  | Office | Yes | 4.285% | 2297.9873 | 20681.8859 | 1 | 11.4899 | 5
Closed_Office_W_FloorT | Office Area (>250 square feet) |  | Office | Yes | 3.054% | 1637.8612 | 14740.7504 | 1 | 8.1893 | 5
Closed_Office_E_FloorT | Office Area (>250 square feet) |  | Office | Yes | 3.054% | 1637.8612 | 14740.7504 | 1 | 8.1893 | 5
Open_Office_S_FloorT | Office Area (>250 square feet) |  | Office | Yes | 2.212% | 1186.2075 | 10675.8676 | 1 | 5.931 | 5
Conference_FloorT | Convention, Conference, Multipurpose and Meeting Area |  | Office | Yes | 2.073% | 1111.7798 | 10006.0183 | 1 | 36.6887 | 33
Lobby/Lounge_FloorT | Lobby, Main Entry |  | Office | Yes | 1.975% | 1059.1755 | 9532.5792 | 1 | 10.5918 | 10 | People: 10 according to ASHRAE 62.1 Table 6-1
Storage_FloorT | Storage (General) |  | Office | Yes | 1.833% | 983.1561 | 8848.405 | 1 |  | -
Mechanical/Electrical_FloorT | Electrical, Mechanical, Telephone Rooms |  | Office | Yes | 0.6663% | 357.3503 | 3216.1531 | 1 |  | -
IT-Room_FloorT | IT Room (EPD 12) |  | Data | Yes | 0.3337% | 178.9373 | 1610.4357 | 1 |  | -
Restroom_FloorT | Restrooms |  | Office | Yes | 1.2% | 643.5778 | 5792.2004 | 1 |  | -
Break_FloorT | Lounge, Breakroom, or Waiting Area |  | Office | Yes | 0.4332% | 232.343 | 2091.0866 | 1 | 7.6673 | 33
Stairway_FloorT | Stairwell |  | Office | Yes | 1.233% | 661.3923 | 5952.5303 | 1 |  | -
Corridor_W_FloorT | Corridor Area |  | Office | Yes | 0.5594% | 300 | 2700 | 1 | 1.5 | 5
Corridor_N_FloorT | Corridor Area |  | Office | Yes | 0.9379% | 502.9724 | 4526.7516 | 1 | 2.5149 | 5
Corridor_E_FloorT | Corridor Area |  | Office | Yes | 0.5594% | 300 | 2692.8684 | 1 | 1.5 | 5
Corridor_S_FloorT | Corridor Area |  | Office | Yes | 0.9379% | 502.9724 | 4526.7516 | 1 | 2.5149 | 5
Plenum_FloorT | Plenum |  | Office | No |  | 17875.9325 | 71503.73 | 1 |  | -
Total (54 Space) | Total (11 Space Type) | Total () | Total (1 category) | Total (51 Conditioned zones, 3 unconditioned zones) | 100% | 53628.1373 | 658610.294
Ref: Geometry and zones: ORNL 2019 medium office prototype with modification
https://web.eecs.utk.edu/~jnew1/publications/2019_IBPSA_OpenStudioOffice.pdf
https://web.eecs.utk.edu/~jnew1/presentations/2019_IBPSA_OpenStudioOffice.pdf
N

## Envelope
Envelope - OfficeMedium
Element | Prototype | Assembly Type | Construction | Thermal Properties | Vintage | Selected T24 | Note | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
External Wall | OfficeMedium | ExtWall_MetalFramed_NonRes | Metal-frame walls + insulation + Gypsum board | U-factor IP | Pre 1978 | N/A | ASHRAE 90.1, 2022, Table A3.3.3.1, 3.5", R-0 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352
[5 empty] | 1978-1997 | 1986 | Low-rise office: Package A/ Heat Capacity was considered ~10 (BTU/F/ft2) | 0.15083 | 0.15748 | 0.15748 | 0.14368 | 0.14368 | 0.21645 | 0.21645 | 0.21645 | 0.21645 | 0.21645 | 0.18622 | 0.18622 | 0.18622 | 0.15873 | 0.15873 | 0.15083
[5 empty] | 1998-2007 | 2001 |  | 0.182 | 0.182 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182
[5 empty] | 2008-2018 | 2013 |  | 0.098 | 0.062 | 0.082 | 0.062 | 0.062 | 0.098 | 0.098 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062
[5 empty] | 2019+ | 2025 |  | 0.06 | 0.055 | 0.071 | 0.055 | 0.055 | 0.06 | 0.06 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055
Roof | OfficeMedium | FlatRoof_WoodFramedAndOther_NonRes | Metal-Deck roof + insulation + Roof membrane | U-factor IP | Pre 1978 | N/A | Considering 30 years for roof/ insultation replacement. | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 1978-1997 | 1992 | Considering 30 years for roof/ insultation replacement. | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 1998-2007 | 2001 |  | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 2008-2018 | 2013 |  | 0.049 | 0.039 | 0.039 | 0.039 | 0.049 | 0.075 | 0.067 | 0.067 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039
[5 empty] | 2019+ | 2025 |  | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.047 | 0.047 | 0.047 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028
Windows | OfficeMedium | FixedWindow_NonRes | CBECS 2018 shows that over 50 % of medium offices that were built before 2000 are single pane | U-factor IP | Pre 1978 | N/A | ASHRAE Handbook of Fundamentals for single pane & T24, 2013 for double pane(50%-50%)* | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74
[5 empty] | 1978-1997 | N/A |  | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74
|  |  | Double pane |  | 1998-2007 | 2001 |  | 0.49 | 0.49 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49
[5 empty] | 2008-2018 | 2013 |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36
[5 empty] | 2019+ | 2025 |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.34 | 0.36 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.36
| OfficeMedium | FixedWindow_NonRes | CBECS 2018 shows that over 50% of medium offices that were built before 2000 are single pane | SHGC | Pre 1978 | N/A | ASHRAE Handbook of Fundamentals for single pane & T24, 2013 for double pane(50%-50%)* | 0.615 | 0.58 | 0.605 | 0.605 | 0.605 | 0.595 | 0.595 | 0.595 | 0.595 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.615
[5 empty] | 1978-1997 | N/A |  | 0.615 | 0.58 | 0.605 | 0.605 | 0.605 | 0.595 | 0.595 | 0.595 | 0.595 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.615
|  |  | Double pane |  | 1998-2007 | 2001 | WWR:20-30 / SHGC north | 0.47 | 0.47 | 0.61 | 0.61 | 0.61 | 0.61 | 0.61 | 0.61 | 0.61 | 0.47 | 0.47 | 0.47 | 0.47 | 0.47 | 0.47 | 0.47
[7 empty] | WWR:20-30 / SHGC non-north | 0.43 | 0.36 | 0.41 | 0.41 | 0.41 | 0.39 | 0.39 | 0.39 | 0.39 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.43
[5 empty] | 2008-2018 | 2013 |  | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
[5 empty] | 2019+ | 2025 |  | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.22 | 0.25 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.25
Infiltration
[5 empty] | Vintage | I_75 (cfm/ft²) 6-sdied Infiltration rate @ 75 pa | Source | I-design (cfm/ft²) (4-sided Infiltration rate at normal pressure) (Design flow rate approach and Flow/Exterior Wall Area calculation method)
|  |  |  | Infiltration | Pre 1978 | 1.1 | 2022 CASE report (Table 38) | 0.3302
[5 empty] | 1978-1997 | 1.1 | 2022 CASE report (Table 38) | 0.3302
[5 empty] | 1998-2007 | 1.1 | 2022 CASE report (Table 38) | 0.3302
[5 empty] | 2008-2018 | 1* | 2022 CASE report (Table 38) & T24, 2008-2016 (Table 140.3-C) | 0.3021
[5 empty] | 2019+ | 0.6** | 2022 CASE report (Table 38) & T24,140.3(a)9Cii & T24, 2025 (Table 140.3-C) | 0.1801
Infiltration_rate_report_14May2025-Short-Version.docx
* An air barrier was not required for guest rooms under T24, until the 2019 edition. However, to reflect typical construction practices, we assumed that all exterior walls are equipped with an air barrier where it was required for nonresidential walls.
*** T24 require 0.4 cfm/ft² for tested condition but it also in section 140.3(a)9Cii says that if the air leakage requirements are not met, a visual inspection and diagnostic evaluation shall be completed , all observed leaks shall be sealed where such sealing can be made without destruction of existing building components, and buildings where the tested leakage rate exceeded 0.6 cfm/ft² of building shell area at 75 Pa have been retested to confirm leakage is below 0.6 cfm/ft² of building shell at 75 Pa.
*Note for windows properties in vintage 1 &2 :
We’ve considered a 50% single-pane and 50% double-pane mix (based on the 2013 requirements) for the window properties in Vintage 1 & 2 (pre-1998 buildings).
Since we don't have California-specific data, the decision is based on the CBECS 2018 data, which indicates:
- 40% of medium offices built before 1978 have mixed windows, while only 6% of offices from the second vintage (1978-1997) have mixed glass.
- Pre-1978: Among those with either single or double-pane windows, 80% have single-pane windows, and 20% have double-pane windows.
- 1978-1997: Among those with either single or double-pane windows, 55% have single-pane windows, and 45% have double-pane windows.
- Pre 1999: Among those with either single or double-pane windows, 61% has single pane windows.
Since we don't have California-specific data and CBECS data is for 2018, it's likely that a percentage of pre-1978 buildings have undergone retrofitting in the past 7 years and upgraded their windows. Based on this, we've decided to apply the 50%-50% mix for the window properties.

## HVAC System
HVAC system - OfficeMedium
Vintage | Space/Thermal Zone | Heating | Cooling | Air Distribution | Source
Existing | All | Furnace (Gas) | Packaged (DX) | CAV with Reheat for the first two vintages VAV with Reheat for vintage 3 and 4 | CEUS 2022 + Engineering Judgement | PTAC
New Construction | All | VRF | VRF | VRF | T24, 2025 | VRF
It Room hasa dedicated HVAC system
Efficiency of HVAC system | [5 empty] | Detailed efficiency of cooling system
Vintage | Upgrade/Installed year | Heating | Cooling | Source |  | Vintage | Cooling System (& air distribution ) | HVAC Zones | Serving floor | Serving area (ft2) | Estimated cooling capapcity (Btu/hr) | Size category (Btu/hr) | Cooling | Upgrade/Installed year | Source
Pre 1978 | 2008 | Efficiency 80% | EER=10.3, 9.7, 9.5 | T24, 2008 (Table 112-A) |  | Pre-1978 & 1978-1997 | West_AC_CAV | West_ZN | No.1,2,3 | 5813.5835 | 116271.6696 | 65,000-13,5000 | EER=10.3 | 2008 | T24, Part 6, 2008 (Table 112-A): Ellectrically operated Unitary Air Conditioners and Condensing units- Minimun Efficicenc Requirements
1978-1997 | [6 empty] | East_AC_CAV | East ZN | No.1,2,3 | 5813.5835 | 116271.6696 | 65,000-13,5000 | EER=10.3 | 2008
1998-2007 | 2008 | Efficiency 80% | EER=9.5 | T24, 2008 (Table 112-A) |  |  | North_AC_CAV | North_ZN | No.1,2,3 | 8402.8792 | 168057.5832 | 135,000-240,000 | EER=9.7 | 2008
2008-2018 | 2010 | COP=3 / Efficiency 80% | EER=10 | T24,2010 (Table 112-A) |  |  | South_AC_CAV | South_ZoneN | No.1,2,3 | 8402.8792 | 168057.5832 | 135,000-240,000 | EER=9.7 | 2008
New Construction | 2025 | COP=3.3 / Efficiency 80% | EER=10 | T24, 2025 (Table 112-A) & CFR Energy 2024:Title 10- Table 19 - § 431.97 |  |  | Core_Office_AC_CAV | Core_Office_ZN | No.1,2,3 | 12849 | 256980 | 240,000-760,000 | EER=9.5 | 2008
[7 empty] | Core_Service_AC_CAV | Core_Service_ZN | No.1,2,3 | 12347.7968 | 246955.9361 | 240,000-760,000 | EER=9.5 | 2008
[6 empty] | 1998-2007 | Floor_1_AC_VAV | All Zones in Floor 1 | No. 1 | 17875.9325 | 357518.65 | 240,000-760,000 | EER=9.5 | 2008
[7 empty] | Floor_2_AC_VAV | All Zones in Floor 2 | No. 2 | 17875.9325 | 357518.65 | 240,000-760,000 | EER=9.5 | 2008
[7 empty] | Floor_3_AC_VAV | All Zones in Floor 3 | No. 3 | 17875.9325 | 357518.65 | 240,000-760,000 | EER=9.5 | 2008
[6 empty] | 2008-2018 | Floor_1_AC_VAV | All Zones in Floor 1 | No. 1 | 17875.9325 | 357518.65 | 240,000-760,000 | EER=10 | 2010 | T24, Part 6, 2010 (Table 112-A): Electrically operated Unitary Air Conditioners and Condensing units- Minimum Efficiency Requirements | 2010 California Energy Code, Part 6 - SUBCHAPTER 2
[7 empty] | Floor_2_AC_VAV | All Zones in Floor 2 | No. 2 | 17875.9325 | 357518.65 | 240,000-760,000 | EER=10 | 2010
[7 empty] | Floor_3_AC_VAV | All Zones in Floor 3 | No. 3 | 17875.9325 | 357518.65 | 240,000-760,000 | EER=10 | 2010
[6 empty] | New Construction | Floor_1_AC_VRF | All Zones in Floor 1 | No. 1 | 17875.9325 | 357518.65 | >=240,000 | EER=10 | 2025 | T24, Part 6, 2025 (Table 110.2-A) & CFR Energy 2024:Title 10- Table 1 - § 431.97 | eCFR :: 10 CFR 431.97 -- Energy efficiency standards and their compliance dates.
[7 empty] | Floor_2_AC_VRF | All Zones in Floor 2 | No. 2 | 17875.9325 | 357518.65 | >=240,000 | EER=10 | 2025 |  | https://www.govinfo.gov/content/pkg/CFR-2024-title10-vol3/pdf/CFR-2024-title10-vol3-part431-subpartF.pdf
[7 empty] | Floor_3_AC_VRF | All Zones in Floor 3 | No. 3 | 17875.9325 | 357518.65 | >=240,000 | EER=10 | 2025
IT_Room is served by a dedicated system
Fan power
Vintage | Approach | System | Total Static Pressure (TSP) (in w.c.) | Fan Efficiency [ACM 2025] | Fan Motor and Drive Efficiency [ACM 2025, Table 13] | W/cfm [ACM 2025, Table 14 and 15] | Data Source | Note
Existing | PNNL TSP | CAV System <7,437 cfm | 2.5 | 0.65 | ~0.9 (The full-load efficiency of the motor serving the fan- will be determined based on ACM 2025, Table 13) |  | Fan Motor and Efficiency: ACM 2025, 0.5 Engineering judgement TSP:[PNNL 20405, 2010, Table 5.11
|  | CAV System >7,437 cfm | 4.09 | 0.65
|  | VAV System > 4,648 cfm | 5.58 | 0.65
Brake horse power (bhp)=(Supply cfm*TSP in w.c.)/(6356*Fan efficiency)
Fan power (w/cfm) = bhp/motor and drive efficiency *746
New Construction | ACM 2025 | Small indoor fan at zone (for VRF) | 1.7445 | 0.65 | 0.9 | 0.35 | Fan Motor and Efficiency and W/cfm: ACM 2025 | 0.35 w/cfm for indoor unit fan (T24, 2025, Section 140.4(a)3 D)
* 0.9 is an average fan efficiency according to ACM 2025, Table 13
Fan total eff (E+ input) = 0.65 x Motor_eff
TSP (E+ input) in w.c. = Motor_eff/746 x (6356 x Fan_eff) x W/cfm
Fan_eff=0.65
Microsoft Word - PNNL 90 1-2010_TSD_Final 5-23-2011_Final.docx
Title 24, part6/2008 |  |  |  | Title 24, Part 6/2010 |  |  |  | Title 24, Part 6/2025 |  |  |  |  | CFR/2024

## Thermostat
Thermostat Setpoints: OfficeMedium
Setpoint | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16 | Source
Heating Setpoint (F) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | T24 2022 - Appendix 5.4B
Heating Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Cooling Setpoint (F) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
Cooling Setback (F) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
*PNNL has considered 80 F for cooling setback of Medium Office prototype. However cooling setback is 85 F for Small Office prototype !!
Note: The Medium Office prototype by PNNL also uses the same setpoints, except for one of the perimeter zones, which has a heating setpoint of 69 °F and a cooling setpoint of 76 °F during hours of 10:00-11:00, 12:00-13:00, and 14:00-15:00 .
Background Data [To be deleted prior to publication]
Heating/ CoolingSetpointsSchedules (existing prototypes extracted from the idf files (presented below)
| Heating | [8 empty] | Cooling
| CEC-2022 |  |  |  | PNNL-2022 |  |  |  |  | CEC-2022 |  |  |  | PNNL-2022
| CEC-Weekday | CEC-Saturday | CEC-Sunday |  | PNNL-Weekday | PNNL-Saturday | PNNL-Sunday |  |  | CEC-Weekday | CEC-Saturday | CEC-Sunday |  | PNNL-Weekday | PNNL-Saturday | PNNL-Sunday
1 | 60 | 60 | 60 |  | 60.08 | 60.08 | 60.08 |  |  | 85 | 85 | 85 |  | 80.06 | 80.06 | 80.06
2 | 60 | 60 | 60 |  | 60.08 | 60.08 | 60.08 |  |  | 85 | 85 | 85 |  | 80.06 | 80.06 | 80.06
3 | 60 | 60 | 60 |  | 60.08 | 60.08 | 60.08 |  |  | 85 | 85 | 85 |  | 80.06 | 80.06 | 80.06
4 | 60 | 60 | 60 |  | 60.08 | 60.08 | 60.08 |  |  | 85 | 85 | 85 |  | 80.06 | 80.06 | 80.06
5 | 60 | 60 | 60 |  | 60.08 | 60.08 | 60.08 |  |  | 85 | 85 | 85 |  | 80.06 | 80.06 | 80.06
6 | 70 | 70 | 60 |  | 64.04 | 64.04 | 60.08 |  |  | 75 | 75 | 85 |  | 78.08 | 78.26 | 80.06
7 | 70 | 70 | 60 |  | 68 | 68 | 60.08 |  |  | 75 | 75 | 85 |  | 77 | 77 | 80.06
8 | 70 | 70 | 60 |  | 69.8 | 69.8 | 60.08 |  |  | 75 | 75 | 85 |  | 75.2 | 75.2 | 80.06
9 | 70 | 70 | 60 |  | 69.8 | 69.8 | 60.08 |  |  | 75 | 75 | 85 |  | 75.2 | 75.2 | 80.06
10 | 70 | 70 | 60 |  | 69.8 | 69.8 | 60.08 |  |  | 75 | 75 | 85 |  | 75.2 | 75.2 | 80.06
11 | 70 | 70 | 60 |  | 69.8 | 69.8 | 60.08 |  |  | 75 | 75 | 85 |  | 75.2 | 75.2 | 80.06
12 | 70 | 70 | 60 |  | 69.8 | 69.8 | 60.08 |  |  | 75 | 75 | 85 |  | 75.2 | 75.2 | 80.06
13 | 70 | 70 | 60 |  | 69.8 | 69.8 | 60.08 |  |  | 75 | 75 | 85 |  | 75.2 | 75.2 | 80.06
14 | 70 | 70 | 60 |  | 69.8 | 69.8 | 60.08 |  |  | 75 | 75 | 85 |  | 75.2 | 75.2 | 80.06
15 | 70 | 70 | 60 |  | 69.8 | 69.8 | 60.08 |  |  | 75 | 75 | 85 |  | 75.2 | 75.2 | 80.06
16 | 70 | 70 | 60 |  | 69.8 | 69.8 | 60.08 |  |  | 75 | 75 | 85 |  | 75.2 | 75.2 | 80.06
17 | 70 | 70 | 60 |  | 69.8 | 69.8 | 60.08 |  |  | 75 | 75 | 85 |  | 75.2 | 75.2 | 80.06
18 | 70 | 70 | 60 |  | 69.8 | 60.08 | 60.08 |  |  | 75 | 75 | 85 |  | 75.2 | 80.06 | 80.06
19 | 70 | 70 | 60 |  | 69.8 | 60.08 | 60.08 |  |  | 75 | 75 | 85 |  | 75.2 | 80.06 | 80.06
20 | 70 | 60 | 60 |  | 69.8 | 60.08 | 60.08 |  |  | 75 | 85 | 85 |  | 75.2 | 80.06 | 80.06
21 | 70 | 60 | 60 |  | 69.8 | 60.08 | 60.08 |  |  | 75 | 85 | 85 |  | 75.2 | 80.06 | 80.06
22 | 70 | 60 | 60 |  | 69.8 | 60.08 | 60.08 |  |  | 75 | 85 | 85 |  | 75.2 | 80.06 | 80.06
23 | 70 | 60 | 60 |  | 60.08 | 60.08 | 60.08 |  |  | 75 | 85 | 85 |  | 80.06 | 80.06 | 80.06
24 | 70 | 60 | 60 |  | 60.08 | 60.08 | 60.08 |  |  | 75 | 85 | 85 |  | 80.06 | 80.06 | 80.06

## Ventilation
Outdoor Airflow Rate - OfficeMedium
Space | Number of People | Floor Area (ft²) | cfm/person (T24, 2025, Equation 120.1-F and Table 120.1-A) | cfm/ft² (T24, 2025, Equation 120.1-F and Table 120.1-A) | Required Exhaust Rate (T24, 2025, Table 120.1-B – Minimum Exhaust Rates) | Total cfm Driven by People | Total cfm Driven by Area | Total cfm Driven by Exhaust | Total cfm | Note
Open_Office_Core_FloorG | 21.415 | 4283 | 15 | 0.15 |  | 321.225 | 642.45 | 0 | 642.45
Open_Office_N_FloorG | 11.4899 | 2297.9873 | 15 | 0.15 |  | 172.349 | 344.6981 | 0 | 344.6981
Closed_Office_W_FloorG | 8.1893 | 1637.8612 | 15 | 0.15 |  | 122.8396 | 245.6792 | 0 | 245.6792
Closed_Office_E_FloorG | 8.1893 | 1637.8612 | 15 | 0.15 |  | 122.8396 | 245.6792 | 0 | 245.6792
Open_Office_S_FloorG | 5.931 | 1186.2075 | 15 | 0.15 |  | 88.9656 | 177.9311 | 0 | 177.9311
Conference_FloorG | 36.6887 | 1111.7798 | 15 | 0.15 |  | 550.331 | 166.767 | 0 | 550.331
Lobby/Lounge_FloorG | 10.5918 | 1059.1755 | 15 | 0.15 |  | 158.8763 | 158.8763 | 0 | 158.8763
Storage_FloorG | 0 | 983.1561 | 15 | 0.15 |  |  | 147.4734 | 0 | 147.4734
Mechanical/Electrical_FloorG | 0 | 357.3503 | 15 | 0.15 |  |  | 53.6026 | 0 | 53.6026
IT-Room_FloorG | ? | 178.9373 | 15 | 0.15 |  |  | 26.8406 | 0 | 26.8406
Restroom_FloorG | 0 | 643.5778 | 15 | 0.15 | 4*25/50 cfm per unit |  | 96.5367 | 100 | 100 | Almost 1 unit per 30 occupant for exhaust fan
Break_FloorG | 7.6673 | 232.343 | 15 | 0.15 |  | 115.0098 | 34.8514 | 0 | 115.0098
Stairway_FloorG | 0 | 661.3923 | 15 | 0.15 |  |  | 99.2088 | 0 | 99.2088
Corridor_W_FloorG | 1.5 | 300 | 15 | 0.15 |  | 22.5 | 45 | 0 | 45
Corridor_N_FloorG | 2.5149 | 502.9724 | 15 | 0.15 |  | 37.7229 | 75.4459 | 0 | 75.4459
Corridor_E_FloorG | 1.496 | 299.2076 | 15 | 0.15 |  | 22.4406 | 44.8811 | 0 | 44.8811
Corridor_S_FloorG | 2.5149 | 502.9724 | 15 | 0.15 |  | 37.7229 | 75.4459 | 0 | 75.4459
Plenum_FloorG | 0 | 17875.9325 |  | - |  |  |  | 0 | 0
Open_Office_Core_FloorM | 21.415 | 4283 | 15 | 0.15 |  | 321.225 | 642.45 | 0 | 642.45
Open_Office_N_FloorM | 11.4899 | 2297.9873 | 15 | 0.15 |  | 172.349 | 344.6981 | 0 | 344.6981
Closed_Office_W_FloorM | 8.1893 | 1637.8612 | 15 | 0.15 |  | 122.8396 | 245.6792 | 0 | 245.6792
Closed_Office_E_FloorM | 8.1893 | 1637.8612 | 15 | 0.15 |  | 122.8396 | 245.6792 | 0 | 245.6792
Open_Office_S_FloorM | 5.931 | 1186.2075 | 15 | 0.15 |  | 88.9656 | 177.9311 | 0 | 177.9311
Conference_FloorM | 36.6887 | 1111.7798 | 15 | 0.15 |  | 550.331 | 166.767 | 0 | 550.331
Lobby/Lounge_FloorM | 10.5918 | 1059.1755 | 15 | 0.15 |  | 158.8763 | 158.8763 | 0 | 158.8763
Storage_FloorM | 0 | 983.1561 | 15 | 0.15 |  |  | 147.4734 | 0 | 147.4734
Mechanical/Electrical_FloorM | 0 | 357.3503 | 15 | 0.15 |  |  | 53.6026 | 0 | 53.6026
IT-Room_FloorM | 0 | 178.9373 | 15 | 0.15 |  |  | 26.8406 | 0 | 26.8406
Restroom_FloorM | 0 | 643.5778 | 15 | 0.15 | 4*25/50 cfm per unit |  | 96.5367 | 100 | 100
Break_FloorM | 7.6673 | 232.343 | 15 | 0.15 |  | 115.0098 | 34.8514 | 0 | 115.0098
Stairway_FloorM | 0 | 661.3923 | 15 | 0.15 |  |  | 99.2088 | 0 | 99.2088
Corridor_W_FloorM | 1.5 | 300 | 15 | 0.15 |  | 22.5 | 45 | 0 | 45
Corridor_N_FloorM | 2.5149 | 502.9724 | 15 | 0.15 |  | 37.7229 | 75.4459 | 0 | 75.4459
Corridor_E_FloorM | 1.496 | 299.2076 | 15 | 0.15 |  | 22.4406 | 44.8811 | 0 | 44.8811
Corridor_S_FloorM | 2.5149 | 502.9724 | 15 | 0.15 |  | 37.7229 | 75.4459 | 0 | 75.4459
Plenum_FloorM | 0 | 17875.9325 | 0 | - |  |  |  | 0 | 0
Open_Office_Core_FloorT | 21.415 | 4283 | 15 | 0.15 |  | 321.225 | 642.45 | 0 | 642.45
Open_Office_N_FloorT | 11.4899 | 2297.9873 | 15 | 0.15 |  | 172.349 | 344.6981 | 0 | 344.6981
Closed_Office_W_FloorT | 8.1893 | 1637.8612 | 15 | 0.15 |  | 122.8396 | 245.6792 | 0 | 245.6792
Closed_Office_E_FloorT | 8.1893 | 1637.8612 | 15 | 0.15 |  | 122.8396 | 245.6792 | 0 | 245.6792
Open_Office_S_FloorT | 5.931 | 1186.2075 | 15 | 0.15 |  | 88.9656 | 177.9311 | 0 | 177.9311
Conference_FloorT | 36.6887 | 1111.7798 | 15 | 0.15 |  | 550.331 | 166.767 | 0 | 550.331
Lobby/Lounge_FloorT | 10.5918 | 1059.1755 | 15 | 0.15 |  | 158.8763 | 158.8763 | 0 | 158.8763
Storage_FloorT | 0 | 983.1561 | 15 | 0.15 |  |  | 147.4734 | 0 | 147.4734
Mechanical/Electrical_FloorT | 0 | 357.3503 | 15 | 0.15 |  |  | 53.6026 | 0 | 53.6026
IT-Room_FloorT | 0 | 178.9373 | 15 | 0.15 |  |  | 26.8406 | 0 | 26.8406
Restroom_FloorT | 0 | 643.5778 | 15 | 0.15 | 4* 25/50 cfm per unit |  | 96.5367 | 100 | 100
Break_FloorT | 7.6673 | 232.343 | 15 | 0.15 |  | 115.0098 | 34.8514 | 0 | 115.0098
Stairway_FloorT | 0 | 661.3923 | 15 | 0.15 |  |  | 99.2088 | 0 | 99.2088
Corridor_W_FloorT | 1.5 | 300 | 15 | 0.15 |  | 22.5 | 45 | 0 | 45
Corridor_N_FloorT | 2.5149 | 502.9724 | 15 | 0.15 |  | 37.7229 | 75.4459 | 0 | 75.4459
Corridor_E_FloorT | 1.5 | 300 | 15 | 0.15 |  | 22.5 | 45 | 0 | 45
Corridor_S_FloorT | 2.5149 | 502.9724 | 15 | 0.15 |  | 37.7229 | 75.4459 | 0 | 75.4459
Plenum_FloorT | 0 | 17875.9325 | 0 | - |  |  |  | 0 | 0
CEUS 2022 Data shows that about 50% of the unconditioned floor area belongs to the first vintage bin (Pre-1978)

## Water Heater
Water Heater - OfficeMedium
Vintage | WH Type | Efficiency | Tank Volume (gal) | Tank Loss | Unit | Source
Existing | Gas | 0.8 | 50 | 855.5146 | Btu/hr
New Construction | Gas | 0.8 | 50 | 855.5146 | Btu/hr
Peak Hot Water Consumption
Space Name | Baseline WH Type [T24, 2022, Appendix 5.4A , sheet: "2022 SpaceFuncData-Input"] | Total Area (ft²) | Number of People | Hot Water Usage Specification (gal/hr per person) [T24, 2022, Appendix 5.4A , sheet: "2022 SpaceFuncData-Input"] | Peak Hot Water Usage (gal/hr) | Peak Hot Water Usage (gal/min)
Open_Office_Core_FloorG | Gas | 4283 | 21.415 | 0.18 | 3.8547 | 0.064245
Open_Office_N_FloorG | Gas | 2297.9873 | 11.4899 | 0.18 | 2.0682 | 0.03447
Closed_Office_W_FloorG | Gas | 1637.8612 | 8.1893 | 0.18 | 1.4741 | 0.024568
Closed_Office_E_FloorG | Gas | 1637.8612 | 8.1893 | 0.18 | 1.4741 | 0.024568
Open_Office_S_FloorG | Gas | 1186.2075 | 5.931 | 0.18 | 1.0676 | 0.017793
Conference_FloorG | Gas | 1111.7798 | 36.6887 | 0.09 | 3.302 | 0.055033
Lobby/Lounge_FloorG | Gas | 1059.1755 | 10.5918 | 0.09 | 0.95326 | 0.015888
Storage_FloorG |  | 983.1561 |  | 0 | 0 | 0
Mechanical/Electrical_FloorG | Gas | 357.3503 |  | 0.18 | 0 | 0
IT-Room_FloorG | Gas | 178.9373 |  | 0.18 | 0 | 0
Restroom_FloorG | Gas | 643.5778 |  |  | 0 | 0
Break_FloorG | Gas | 232.343 | 7.6673 | 0.09 | 0.69006 | 0.011501
Stairway_FloorG |  | 661.3923 |  | 0 | 0 | 0
Corridor_W_FloorG |  | 300 | 1.5 | 0 | 0 | 0
Corridor_N_FloorG |  | 502.9724 | 2.5149 | 0 | 0 | 0
Corridor_E_FloorG |  | 299.2076 | 1.496 | 0 | 0 | 0
Corridor_S_FloorG |  | 502.9724 | 2.5149 | 0 | 0 | 0
Plenum_FloorG |  | 17875.9325 |  | 0 | 0 | 0
Open_Office_Core_FloorM | Gas | 4283 | 21.415 | 0.18 | 3.8547 | 0.064245
Open_Office_N_FloorM | Gas | 2297.9873 | 11.4899 | 0.18 | 2.0682 | 0.03447
Closed_Office_W_FloorM | Gas | 1637.8612 | 8.1893 | 0.18 | 1.4741 | 0.024568
Closed_Office_E_FloorM | Gas | 1637.8612 | 8.1893 | 0.18 | 1.4741 | 0.024568
Open_Office_S_FloorM | Gas | 1186.2075 | 5.931 | 0.18 | 1.0676 | 0.017793
Conference_FloorM | Gas | 1111.7798 | 36.6887 | 0.09 | 3.302 | 0.055033
Lobby/Lounge_FloorM | Gas | 1059.1755 | 10.5918 | 0.09 | 0.95326 | 0.015888
Storage_FloorM |  | 983.1561 |  | 0 | 0 | 0
Mechanical/Electrical_FloorM | Gas | 357.3503 |  | 0.18 | 0 | 0
IT-Room_FloorM | Gas | 178.9373 |  | 0.18 | 0 | 0
Restroom_FloorM |  | 643.5778 |  | 0 | 0 | 0
Break_FloorM | Gas | 232.343 | 7.6673 | 0.09 | 0.69006 | 0.011501
Stairway_FloorM |  | 661.3923 |  | 0 | 0 | 0
Corridor_W_FloorM |  | 300 | 1.5 | 0 | 0 | 0
Corridor_N_FloorM |  | 502.9724 | 2.5149 | 0 | 0 | 0
Corridor_E_FloorM |  | 299.2076 | 1.496 | 0 | 0 | 0
Corridor_S_FloorM |  | 502.9724 | 2.5149 | 0 | 0 | 0
Plenum_FloorM |  | 17875.9325 |  | 0 | 0 | 0
Open_Office_Core_FloorT | Gas | 4283 | 21.415 | 0.18 | 3.8547 | 0.064245
Open_Office_N_FloorT | Gas | 2297.9873 | 11.4899 | 0.18 | 2.0682 | 0.03447
Closed_Office_W_FloorT | Gas | 1637.8612 | 8.1893 | 0.18 | 1.4741 | 0.024568
Closed_Office_E_FloorT | Gas | 1637.8612 | 8.1893 | 0.18 | 1.4741 | 0.024568
Open_Office_S_FloorT | Gas | 1186.2075 | 5.931 | 0.18 | 1.0676 | 0.017793
Conference_FloorT | Gas | 1111.7798 | 36.6887 | 0.09 | 3.302 | 0.055033
Lobby/Lounge_FloorT | Gas | 1059.1755 | 10.5918 | 0.09 | 0.95326 | 0.015888
Storage_FloorT |  | 983.1561 |  | 0 | 0 | 0
Mechanical/Electrical_FloorT | Gas | 357.3503 |  | 0.18 | 0 | 0
IT-Room_FloorT | Gas | 178.9373 |  | 0.18 | 0 | 0
Restroom_FloorT |  | 643.5778 |  | 0 | 0 | 0
Break_FloorT |  | 232.343 | 7.6673 |  | 0 | 0
Stairway_FloorT |  | 661.3923 |  | 0 | 0 | 0
Corridor_W_FloorT |  | 300 | 1.5 | 0 | 0 | 0
Corridor_N_FloorT |  | 502.9724 | 2.5149 | 0 | 0 | 0
Corridor_E_FloorT |  | 300 | 1.5 | 0 | 0 | 0
Corridor_S_FloorT |  | 502.9724 | 2.5149 | 0 | 0 | 0
Plenum_FloorT |  | 17875.9325 |  | 0 | 0 | 0
Water Heater Capacity, Tank Capacity, and Tank Loss
WH Type | Peak Hot Water Usage (gal/hr) | Heat Output (Btu/hr) [ACM, 2025, 5.9.2: Rated capacity section] | WH Capacity (Btu/hr) [ACM, 2025, 5.9.2: Rated capacity section] | Required Energy Input (Btu/hr) | Storage Volume (gal) | Standby Loss |  | Off/On Cycle Loss Coefficient to Ambient Temp (Btu/h-F) | Source
Gas Storage WH | 125 | 82877 | 49726.2 | 62157.75 | 50 | 855.5146 | Btu/hr | 12.5811 | Standby loss equation: Title 20, §1605.1 Table F-4 WH capacity equation: ACM, 2025, 5.9.2: Rated capacity section)
Electric resistance WH | 0 | 0 | 0 | 0 | 0 | 0 | %/hr | 0
Total | 125 |  |  |  | 50
Design supply temperature (F) | 135 | Ref: T24 2022 - Appendix 5.4B
Cold Water supply temperature (F) | 55 | Ref: ACM, 2025, 5.9.2: Rated capacity section
WH system factor | 0.6 | Ref: ACM, 2025, 5.9.2: Rated capacity section
Reheat multiplier | 0.4 | Ref: ACM, 2025, 5.9.2: Storage Volume
* The 0.40 multiplier is a storage sizing factor used to account for the fact that the water heater doesn't need to store the full peak hour demand—it can reheat water during that time. This factor assumes that the heater will recover part of the hot water used during the peak hour, so only 40% of the peak hour demand needs to be stored at any given moment.
Ambient temp | 68
Delta T | 67
Background Data [To be deleted prior to publication]

## Interior Lights
Interior Lighting - OfficeMedium
Space Type | New Construction |  |  | Existing |  |  | Note
| LPD (W/ft²) | Additional LPD for Portable Lighting (W/ft²) | Source | LPD (W/ft²) | Additional LPD for Portable Lighting (W/ft²) | Source
Office Area (>250 square feet) | 0.6 |  | T24, part 6, 2025, Table 140.6 C | 0.75 |  | T24, part 6, 2013, Table 140.6 C
Convention, Conference, Multipurpose and Meeting Area | 0.75 |  |  | 1.4
Lobby, Main Entry | 0.7 |  |  | 1.1
Storage (General) | 0.4 |  |  | 0.6
Electrical, Mechanical, Telephone Rooms | 0.4 |  |  | 0.7
IT Room (EPD 12) | 1.1 |  |  | 1.2
Restrooms | 0.6 |  |  | 0.6
Lounge, Breakroom, or Waiting Area | 0.55 |  |  | 1.1 |  |  | 2013 LPD is for "Lounge" area
Stairwell | 0.6 |  |  | 0.6
Corridor Area | 0.4 |  |  | 0.6
Plenum | -
Whole Building method
| 2025 | 2013
LPD for Office Building ((W/ft²) | 0.6 | 0.8
Ref: T24, Table 140.6 B
Background Data [To be deleted prior to publication]
Ref: Title 24, Part 6- Table 140.6-C (office area >250nSF)
Title 24, part 6 Code cycle | Lighting density for office Buildings: (complete building Method) | Lighting density for office area >250 sf Floor area Method | Table | Note |  | T24, part 6 2022 | file://carcgl.com/amer/NOR/Groups/CodesStds/Standards/California/2022%20Building%20Energy%20Efficiency%20Standards%20for%20Residential%20and%20Nonresidential%20Buildings.pdf
2025 | 0.6 | 0.6, 0.2 (additional) | Table 140.6 C |  |  | T24, part 6 2019 | file://carcgl.com/amer/NOR/Groups/CodesStds/Standards/California/2016-CEC-400-2015-037-CMF.pdf
2022 | 0.6 | 0.6, 0.2 (additional) |  |  |  | T24, part 6 2016 | file://carcgl.com/amer/NOR/Groups/CodesStds/Standards/California/2016-CEC-400-2015-037-CMF.pdf
2019 | 0.65
2016 | 0.8
2013 | 0.8 | 0.75
2010 | 0.85
2008 | 0.085 | 0.9 | Table 146-E
2005 |  | 1.2
TBD: Review the CASE report on 2016 for lighting
Review of existing Medium Office prototype
Prototype/Source | Downloaded on | Zone | Light Intensity | Unit | Total intensity multipliers | Total lighting intensity | Core/Perims area ratio | Working days | 249
PNNL | 2024-02-01 | All | 0.53921 | W/ft2 | 1988.2232 | 1072.0652 | 41.4% | Saturday | 52
CEC (CBECC 2023) | 2024-06-01 | All | 0.6 | W/ft2 | 2238.1 | 1342.86 | 41.4% | Sunday | 52
[8 empty] | Holiday | 11
Interior lighting Schedules (existing prototypes extracted from the idf files (presented below)
| CEC |  |  |  | PNNL
Hour | CEC-Weekday | CEC-Saturday | CEC-Sunday |  | PNNL-Weekday | PNNL-Saturday | PNNL-Otherday
1 | 0.05 | 0.05 | 0.05 |  | 0.035971 | 0.035971 | 0.035971
2 | 0.05 | 0.05 | 0.05 |  | 0.035971 | 0.035971 | 0.035971
3 | 0.05 | 0.05 | 0.05 |  | 0.035971 | 0.035971 | 0.035971
4 | 0.05 | 0.05 | 0.05 |  | 0.035971 | 0.035971 | 0.035971
5 | 0.05 | 0.05 | 0.05 |  | 0.035971 | 0.035971 | 0.035971
6 | 0.1 | 0.05 | 0.05 |  | 0.071953 | 0.035971 | 0.035971
7 | 0.1 | 0.1 | 0.05 |  | 0.071953 | 0.071953 | 0.035971
8 | 0.3 | 0.1 | 0.05 |  | 0.21586 | 0.071953 | 0.035971
9 | 0.65 | 0.3 | 0.05 |  | 0.64758 | 0.21586 | 0.035971
10 | 0.65 | 0.3 | 0.05 |  | 0.64758 | 0.21586 | 0.035971
11 | 0.65 | 0.3 | 0.05 |  | 0.64758 | 0.21586 | 0.035971
12 | 0.65 | 0.3 | 0.05 |  | 0.64758 | 0.21586 | 0.035971
13 | 0.65 | 0.15 | 0.05 |  | 0.64758 | 0.10792 | 0.035971
14 | 0.65 | 0.15 | 0.05 |  | 0.64758 | 0.10792 | 0.035971
15 | 0.65 | 0.15 | 0.05 |  | 0.64758 | 0.10792 | 0.035971
16 | 0.65 | 0.15 | 0.05 |  | 0.64758 | 0.10792 | 0.035971
17 | 0.65 | 0.15 | 0.05 |  | 0.64758 | 0.10792 | 0.035971
18 | 0.35 | 0.05 | 0.05 |  | 0.35976 | 0.035971 | 0.035971
19 | 0.3 | 0.05 | 0.05 |  | 0.21586 | 0.035971 | 0.035971
20 | 0.3 | 0.05 | 0.05 |  | 0.21586 | 0.035971 | 0.035971
21 | 0.2 | 0.05 | 0.05 |  | 0.14391 | 0.035971 | 0.035971
22 | 0.2 | 0.05 | 0.05 |  | 0.14391 | 0.035971 | 0.035971
23 | 0.1 | 0.05 | 0.05 |  | 0.071953 | 0.035971 | 0.035971
24 | 0.05 | 0.05 | 0.05 |  | 0.035971 | 0.035971 | 0.035971
Sum of intensity multiplier | 8.1 | 2.8 | 1.2 |  | 7.555 | 2.0146 | 0.035971
| Same as Small Office | Same as Small Office | Same as Small Office

## Ext Lighting
Exterior Lighting - OfficeMedium
Motion Controlled Luminaires (W) | Non-motion Controlled Luminaires (W) | Total (W) | Source
1860.2954 | 856.2397 | 2716.5351 | Title 24, 2022
Exterior Lighting
Items (Assume LZ2) | Assumptions [2019 Outdoor Lighting CASE Report & PNNL 90.1-2010 TSD] |  | Unit | Lighting Power Allowance [T24, 2025, Table 140.7-A & 140.7-B] | Unit | Exterior Lighting Power (W)
IWA (Initial Wage Allowance) |  |  |  | 200 | (W) | 200
Parking area | 400 ft² for every parking space 1 parking space per 250 ft² of gross building area | 85805.0197 | (ft²) | 0.019 | (W/ft²) | 1630.2954
Building Entrance | 2 building entrance (1 per 10,000 ft² footprint) | 2 | (count) | 15 | (W/ea) | 30
Hardscape Ornamental Light | 0.1 ft² per 1 ft² of gross building area for hardscape ornamental light | 5362.8137 | (ft²) | 0.007 | (W/ft²) | 37.5397
Building façade | 0.1 W per ft² of facade area Façade Area* = Perimeter × 0.5 × 30 ft (30 ft is the max height that is lit) The 0.5 factor assumes that only half of the perimeter walls are lit. -Formula ia developed based on the 2019 Outdoor Lighting CASE report | 8187 | (ft²) | 0.1 | (W/ft²) | 818.7
Motion controlled Luminaires | [5 empty] | 1860.2954
Non-motion-controlled Luminaires | [5 empty] | 856.2397
Total | [5 empty] | 2716.5351
*Developed based on 2019 Outdoor Lighting CASE Report
Perimeter (ft) | 545.8
Total floor area (ft²) | 53628.1373
Floors (above ground) | 3
Background Data [To be deleted prior to publication]
Exterior Lighting
Ref: Title 24, Part 6- Table 140.6-C (office area >250 SF)
Title 24, part 6 Code cycle | Lighting for parking area | Daylight Adaptation Zones**
2022 | 0.1 | 1
2019 | 0.1 | 0.5
2016 | 0.14 | 0.6
**Daylight Adaptation Zones shall be no farther than 66 feet from the entrance to the parking garage
Exterior Lighting - OfficeLarge (CEUS 2022 data)
Building Type | Planning Area & Forecast Zone | End Use Saturation or Penetration
OfficeLarge | Statewide | 96.52%
| FCZ1 | 97.34%
| FCZ2 | 100%
| FCZ3 | 85.48%
| FCZ4 | 85.48%
| FCZ5 | 100%
| FCZ6 | 100%
| FCZ7 | 97.22%
| FCZ8 | 100%
| FCZ9 | 100%
| FCZ10 | 89.87%
| FCZ11 | 100%
| FCZ12c | 91.55%
| FCZ12i | 94.56%
| FCZ13 | 100%
| FCZ16 | 100%
| FCZ17 | 100%
| DEER OFS Prototype -7/2024 | PNNL OfficeMedium 02-2024
Exterior Lights W | None | 542.49 | 3002.07 | 280.18
Schedule |  | 0-5 am: 0 | 0-5am: 0.5 | 0-5am: 0.5
|  | 6 am-12am:1 | 6am-6pm: 1 | 6am-24: 1
7pm:12am: 0.5
T24, part6, 2025, 130.2(c)3

## Equipment
Equipment - OfficeMedium
Space Type | Plug load Power Density (W/ft²) | Gas Power Density (Btu/hr-ft²) | Refrigeration Power Density (W/ft²) | Source
Office Area (>250 square feet) | 0.7 |  |  | Plug load and schedules project with CEC , 2025
Convention, Conference, Multipurpose and Meeting Area | 0.8 |  |  | T24 2022 - Appendix 5.4A
Lobby, Main Entry | 0.5
Storage (General) | 0.2
Electrical, Mechanical, Telephone Rooms | 3
IT Room (EPD 12) | 12 |  |  | Feedback from TAG team
Restrooms | 0 |  |  | T24 2022 - Appendix 5.4A
Lounge, Breakroom, or Waiting Area | 0.5
Stairwell | 0
Corridor Area | 0
Plenum | 0
Elevator
Vintages | No of Elevator | Design Load (W) | Source
New Construction and Existing | 2 | 13930 | CEC Medium Office prototype in CBEC 2022
PNNL Medium Office prototype has lower load for elevator ( 61% of the CEC). We've considered two elevators for Medium Office prototype and therefore prefer CEC's assumptions.
Background Data [To be deleted prior to publication]
Equipment (Plug Load )- Prototypes comparison
|  |  |  | CEC | PNNL | Note
|  |  | Core Zones | 1.5 W/ft2 | 7937.16 W
|  |  | Perimeter 3,1 |  | 1673.21 W
|  |  | Perimeter 2,4 |  | 1059.22 W
|  |  | Elevator | 10000 W | 8517.82 W
|  |  | Elevatoir_lights_Fan |  | 105.31 W |  | 61.9%
|  |  | Escalator | 3930 W
Yearly Load multiplier
|  | Office Area | [6 empty] | Elevator | [5 empty] | Escalator (only CEC) |  |  | Lights_Fan (ONLY PNNL)
|  | CEC 2022 |  |  |  | PNNL 2022 |  |  | CEC 2022 |  |  | PNNL 2022 |  |  | CEC 2022 |  |  | PNNL 2022
Hour |  | CEC-Weekday | CEC-Saturday | CEC-Sunday |  | PNNL-Weekday | PNNL-Saturday | PNNL-Sunday | CEC-Weekday | CEC-Saturday | CEC-Sunday | PNNL-Weekday | PNNL-Saturday | PNNL-Sunday | CEC-Weekday | CEC-Saturday | CEC-Sunday | PNNL-Weekday | PNNL-Saturday | PNNL-Sunday
1 |  | 0.05 | 0.05 | 0.05 |  | 0.30767 | 0.23076 | 0.23076 | 0 | 0 | 0 | 0.12 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 |  | 0.05 | 0.05 | 0.05 |  | 0.30767 | 0.23076 | 0.23076 | 0 | 0 | 0 | 0.12 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 |  | 0.05 | 0.05 | 0.05 |  | 0.30767 | 0.23076 | 0.23076 | 0 | 0 | 0 | 0.12 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 |  | 0.05 | 0.05 | 0.05 |  | 0.30767 | 0.23076 | 0.23076 | 0 | 0 | 0 | 0.12 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 |  | 0.05 | 0.05 | 0.05 |  | 0.30767 | 0.23076 | 0.23076 | 0 | 0 | 0 | 0.12 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 |  | 0.1 | 0.05 | 0.05 |  | 0.30767 | 0.23076 | 0.23076 | 0 | 0 | 0 | 0.12 | 0.12 | 0 | 1 | 1 | 0 | 0 | 0 | 0
7 |  | 0.1 | 0.1 | 0.05 |  | 0.38123 | 0.38123 | 0.28593 | 0 | 0 | 0 | 0.12 | 0.12 | 0 | 1 | 1 | 0 | 0 | 0 | 0
8 |  | 0.3 | 0.1 | 0.05 |  | 0.38123 | 0.38123 | 0.28593 | 0.35 | 0.16 | 0 | 0.35 | 0.16 | 0 | 1 | 1 | 0 | 0.35 | 0.16 | 0
9 |  | 0.9 | 0.3 | 0.05 |  | 0.85778 | 0.47654 | 0.28593 | 0.69 | 0.14 | 0 | 0.69 | 0.14 | 0 | 1 | 1 | 0 | 0.69 | 0.14 | 0
10 |  | 0.9 | 0.3 | 0.05 |  | 0.85778 | 0.47654 | 0.28593 | 0.43 | 0.21 | 0 | 0.43 | 0.21 | 0 | 1 | 1 | 0 | 0.43 | 0.21 | 0
11 |  | 0.9 | 0.3 | 0.05 |  | 0.85778 | 0.47654 | 0.28593 | 0.37 | 0.18 | 0 | 0.37 | 0.18 | 0 | 1 | 1 | 0 | 0.37 | 0.18 | 0
12 |  | 0.9 | 0.3 | 0.05 |  | 0.85778 | 0.47654 | 0.28593 | 0.43 | 0.25 | 0 | 0.43 | 0.25 | 0 | 1 | 1 | 0 | 0.43 | 0.25 | 0
13 |  | 0.9 | 0.15 | 0.05 |  | 0.76247 | 0.33358 | 0.28593 | 0.58 | 0.21 | 0 | 0.58 | 0.21 | 0 | 1 | 1 | 0 | 0.58 | 0.21 | 0
14 |  | 0.9 | 0.15 | 0.05 |  | 0.85778 | 0.33358 | 0.28593 | 0.48 | 0.13 | 0 | 0.48 | 0.13 | 0 | 1 | 1 | 0 | 0.48 | 0.13 | 0
15 |  | 0.9 | 0.15 | 0.05 |  | 0.85778 | 0.33358 | 0.28593 | 0.37 | 0.08 | 0 | 0.37 | 0.12 | 0 | 1 | 1 | 0 | 0.37 | 0.08 | 0
16 |  | 0.9 | 0.15 | 0.05 |  | 0.85778 | 0.33358 | 0.28593 | 0.37 | 0.04 | 0 | 0.37 | 0.12 | 0 | 1 | 1 | 0 | 0.37 | 0.04 | 0
17 |  | 0.9 | 0.15 | 0.05 |  | 0.85778 | 0.33358 | 0.28593 | 0.46 | 0.05 | 0 | 0.46 | 0.12 | 0 | 1 | 1 | 0 | 0.46 | 0.05 | 0
18 |  | 0.5 | 0.05 | 0.05 |  | 0.47654 | 0.28593 | 0.28593 | 0.62 | 0.06 | 0 | 0.62 | 0.12 | 0 | 1 | 1 | 0 | 0.62 | 0.06 | 0
19 |  | 0.3 | 0.05 | 0.05 |  | 0.38123 | 0.28593 | 0.23076 | 0.2 | 0 | 0 | 0.12 | 0.12 | 0 | 1 | 1 | 0 | 0.12 | 0 | 0
20 |  | 0.3 | 0.05 | 0.05 |  | 0.38123 | 0.23076 | 0.23076 | 0.12 | 0 | 0 | 0.12 | 0.12 | 0 | 1 | 0 | 0 | 0.04 | 0 | 0
21 |  | 0.2 | 0.05 | 0.05 |  | 0.38123 | 0.23076 | 0.23076 | 0.04 | 0 | 0 | 0.12 | 0.12 | 0 | 1 | 0 | 0 | 0.04 | 0 | 0
22 |  | 0.2 | 0.05 | 0.05 |  | 0.38123 | 0.23076 | 0.23076 | 0.04 | 0 | 0 | 0.12 | 0.12 | 0 | 1 | 0 | 0 | 0 | 0 | 0
23 |  | 0.1 | 0.05 | 0.05 |  | 0.38123 | 0.23076 | 0.23076 | 0 | 0 | 0 | 0.12 | 0.12 | 0 | 1 | 0 | 0 | 0 | 0 | 0
24 |  | 0.05 | 0.05 | 0.05 |  | 0.38123 | 0.23076 | 0.23076 | 0 | 0 | 0 | 0.12 | 0.12 | 0 | 1 | 0 | 0 | 0 | 0 | 0
|  | 10.5 | 2.8 | 1.2 |  | 12.9972 | 7.4467 | 6.2002

## Schedules
Schedules - OfficeMedium
Zone | Schedule Category | Schedule | Source | Type | Hour
[5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
All zones | Office | Occupancy | T24 2022 - Appendix 5.4B, [Office] Updated base on Plug load and schedules project with CEC, 2025 | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
All zones | Office | Lights | T24 2022 - Appendix 5.4B, [Office] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.35 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
All zones | Office | ElecEquipment | Plug load and schedules project with CEC, 2025 | Weekday | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.74 | 0.87 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.5 | 0.45 | 0.45 | 0.45
|  |  |  | Saturday | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43
|  |  |  | Sunday | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43
All zones | Office | HVACAvail | T24 2022 - Appendix 5.4B, [Office] Updated base on Plug load and schedules project with CEC, 202 | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
All zones | Office | ServiceHotWater | T24 2022 - Appendix 5.4B, [Office] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.12 | 0.14 | 0.07 | 0.07 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05
|  |  |  | Sunday | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04
All zones | Office | Infiltration | T24 2022 - Appendix 5.4B, [Office] Updated base on Plug load and schedules project with CEC, 202 | Weekday | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
All zones | Office | HtgSetpt |  | Weekday | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
|  |  |  | Saturday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  |  | Sunday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
All zones | Office | ClgSetpt |  | Weekday | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
|  |  |  | Saturday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
|  |  |  | Sunday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
Data
IT room | Data | Occupancy | T24 2022 - Appendix 5.4B, [Data] Updated base on office schedule | Weekday | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.25 | 0.65 | 0.65 | 0.65 | 0.65 | 0.6 | 0.6 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.25 | 0.1 | 0.05 | 0.05 | 0.05 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0
IT room | Data | Lights | T24 2022 - Appendix 5.4B, [Data] Updated base on office schedule | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.7 | 0.8 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.8 | 0.35 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05
IT room | Data | HVACAvail | T24 2022 - Appendix 5.4B, [Data] | Weekday | bar: Hour 1 to Hour 24
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
IT room | Data | ServiceHotWater | T24 2022 - Appendix 5.4B, [Data] | Weekday | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.9 | 0.9 | 0.5 | 0.5 | 0.7 | 0.5 | 0.5 | 0.5 | 0.1 | 0.1 | 0.1 | 0.1 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IT room | Data | Infiltration | T24 2022 - Appendix 5.4B, [Data] | Weekday | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  |  | Saturday | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  |  | Sunday | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
IT room | Data | ClgSetpt | Based on Activity level and thermostat setpoint | Weekday | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
|  |  |  | Saturday | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
|  |  |  | Sunday | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
Other
Stairway | Building | Elevator | T24 2022 - Appendix 5.4B, [Office] Updated base on Plug load and schedules project with CEC, 202 | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Building | ExtLightingNonMotionCtrl |  | Weekday | bar: Hour 1 to Hour 24
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
| Building | ExtLightingMotionCtrl |  | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Office | Building | FunctionalAreaPeopleActivityLevel | Based on Activity level schedules in CEC Prototypes | Weekday | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
|  |  |  | Saturday | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
|  |  |  | Sunday | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
IT room | Building | ComputerRoomPeopleActivityLevel | Based on Activity level schedules in CEC Prototypes | Weekday | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
|  |  |  | Saturday | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
|  |  |  | Sunday | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
Conference room | Building | MeetingAreaPeopleActivityLevel | Based on Activity level schedules in CEC Prototypes | Weekday | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117
|  |  |  | Saturday | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117
|  |  |  | Sunday | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117
Corridor, Stair, Lobby, Restroom, Mech, Storage, Break | Building | CommonAreaPeopleActivityLevel | Based on Activity level schedules in CEC Prototypes | Weekday | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147
|  |  |  | Saturday | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147
|  |  |  | Sunday | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147
Background Data [To be deleted prior to publication] | bar: Hour 1
Operating Schedule
| System Capacity fraction | Developed based on CEC and CEUS | Office Zones | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.7 | 0.5 | 0.3 | 0.2 | 0.2 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.005 | 0 | 0 | 0 | 0 | 0
Alternative HVAC System Operating
| Alternative HVAC System Operating | Developed based on CEC schedules and CEUS operating hours | Office Closed Zones | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Otherday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Office Open Zones | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Otherday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Equipment (Plug load) (Nees to be updated based on the Plug load project with CEC) | T24 2022 - Appendix 5.4A | Office | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05
|  |  |  | Saturday | 0.43 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  |  |  | Sunday | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43
Background Data [To be deleted prior to publication] | bar: Hour 1
| Equipment | PNNL | Office Zones | Weekday | 0.40948 | 0.40948 | 0.40948 | 0.40948 | 0.40948 | 0.40948 | 0.47975 | 0.47975 | 0.95951 | 0.95951 | 0.95951 | 0.95951 | 0.90193 | 0.95951 | 0.95951 | 0.95951 | 0.95951 | 0.47975 | 0.1919 | 0.1919 | 0.1919 | 0.1919 | 0.1919 | 0.16379
|  |  |  | Saturday | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379
|  |  |  | Sunday | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379

## Weights
% of floor area per CZ and vintage bin - OfficeLarge | [6 empty] | We don't have Medium Office specific data from CEUS. The data copied here belongs to the CEUS large office data which our Medium Office prototype falls within that group
Prototype | CZ | Pre-1978 | 1978-1997 | 1998-2007 | 2008-2018 | Not available
OfficeLarge | 1 | 58.42% | 23.37% | 8.059% | 3.566% | 6.59% |  |  | Floor area distribution of CA office buildings (CEUS 2022)
| 2 | 49.15% | 36.42% | 14.39% | 0.01642% | 0.03034% |  |  | Office, Small | Office, Medium | Office, Large
| 3 | 39.04% | 34.62% | 15.64% | 7.994% | 2.703% |  |  | 35.39% | 29.43% | 35.18%
| 4 | 39.42% | 34.19% | 15.72% | 8.051% | 2.62%
| 5 | 18.23% | 72.98% | 3.482% | 3.023% | 2.286%
| 6 | 33.04% | 40.09% | 15.45% | 6.416% | 5.004%
| 7 | 16.64% | 53.22% | 21.55% | 6.978% | 1.606%
| 8 | 35.09% | 41.33% | 11.31% | 5.179% | 7.09%
| 9 | 38.4% | 40.67% | 9.23% | 6.323% | 5.384%
| 10 | 16.2% | 41.33% | 26.42% | 9.855% | 6.194%
| 11 | 46.79% | 16.13% | 14.62% | 8.828% | 13.62%
| 12 | 37.43% | 31.21% | 16.49% | 8.794% | 6.067%
| 13 | 68.74% | 13.07% | 3.979% | 4.987% | 9.218%
| 14 | 21.03% | 41.59% | 21.25% | 6.024% | 10.11%
| 15 | 30.2% | 16.76% | 25.29% | 17.74% | 10.02%
| 16 | 27.08% | 30.95% | 23.93% | 6.613% | 11.43%
| Statewide | 34.88% | 38.18% | 15.17% | 7.116% | 4.65%
Source: CEUS 2022 dataset
Background Data [To be deleted prior to publication]
CEUS 2022 data | Office, Small | Medium office | Office, Large | All Office
floor area (sqft) | 582249224.8542 | 484234913.3262 | 578752976.2841 | 1645237114.4645
% of floor area | 35.39% | 29.43% | 35.18% | 100%
Directly from the CEUS 2022 data
FZ | Building Type | Pre-1978 | 1978-1997 | 1998-2007 | 2008-2018 |  |  |  |  | Pre-1978 | 1978-1997 | 1998-2007 | 2008-2017 | Year-Built Not Available | Total | Total available
Statewide | Office, Large | 482973.3611 | 528782.3997 | 210118.6188 | 98538.6062 | 36.58% | 40.05% | 15.91% | 7.463% | 460513.399 | 504192.1559 | 200347.3631 | 93956.214 | 61403.8539 | 1320412.9859 | 1259009.132
1 | Office, Large | 182191.7274 | 154537.0491 | 72923.6137 | 37264.4478 | 40.77% | 34.58% | 16.32% | 8.338% | 177411.7833 | 150482.6474 | 71010.405 | 36286.7856 | 11725.2166 | 446916.838 | 435191.6214
2 | Office, Large | 7571.3771 | 5624.5187 | 2223.205 | 0 | 49.1% | 36.48% | 14.42% | 0% | 7571.3771 | 5624.5187 | 2223.205 | 0 | 0 | 15419.1009 | 15419.1009
3 | Office, Large | 3436.5747 | 428.8986 | 0 | 0 | 88.9% | 11.1% | 0% | 0% | 3436.5747 | 428.8986 | 0 | 0 | 0 | 3865.4733 | 3865.4733
4 | Office, Large | 2414.0808 | 7826.0618 | 13832.4128 | 6688.0788 | 7.848% | 25.44% | 44.97% | 21.74% | 1840.1633 | 5965.5136 | 10543.9298 | 5098.0718 | 7312.9557 | 30760.6342 | 23447.6785
5 | Office, Large | 12891.5662 | 2958.0294 | 779.8862 | 1178.3494 | 72.39% | 16.61% | 4.379% | 6.617% | 11486.752 | 2635.6883 | 694.9007 | 1049.9428 | 1940.5472 | 17807.8311 | 15867.2839
6 | Office, Large | 2178.4635 | 8792.1068 | 358.4383 | 344.6399 | 18.66% | 75.32% | 3.07% | 2.952% | 2127.987 | 8588.3876 | 350.133 | 336.6543 | 270.4865 | 11673.6485 | 11403.1619
7 | Office, Large | 84200.1702 | 130447.5674 | 46949.7964 | 18081.3699 | 30.11% | 46.64% | 16.79% | 6.465% | 75637.172 | 117181.2963 | 42175.0908 | 16242.5287 | 28442.8159 | 279678.9038 | 251236.0879
8 | Office, Large | 5216.0149 | 8383.195 | 10955.9881 | 3728.9537 | 18.44% | 29.64% | 38.74% | 13.18% | 5216.0149 | 8383.195 | 10955.9881 | 3728.9537 | 0 | 28284.1517 | 28284.1517
9 | Office, Large | 3606.3119 | 140.3434 | 172.5384 | 0 | 92.02% | 3.581% | 4.402% | 0% | 3606.3119 | 140.3434 | 172.5384 | 0 | 0 | 3919.1937 | 3919.1937
10 | Office, Large | 0 | 10120.9561 | 9089.6703 | 1656.7405 | 0% | 48.5% | 43.56% | 7.939% | 0 | 8879.8801 | 7975.0551 | 1453.5837 | 2558.8479 | 20867.3668 | 18308.5189
11 | Office, Large | 6470.8688 | 3637.3583 | 5678.2324 | 3980.4481 | 32.74% | 18.4% | 28.73% | 20.14% | 5820.8179 | 3271.9564 | 5107.8082 | 3580.58 | 1985.7451 | 19766.9076 | 17781.1625
12c | Office, Large | 17953.6205 | 53677.2042 | 25403.5227 | 7511.6283 | 17.17% | 51.34% | 24.3% | 7.185% | 17617.9411 | 52673.6001 | 24928.5524 | 7371.1832 | 1954.699 | 104545.9758 | 102591.2768
12i | Office, Large | 2638.9051 | 12116.5603 | 1310.5699 | 1122.9048 | 15.35% | 70.49% | 7.624% | 6.533% | 2638.9051 | 12116.5603 | 1310.5699 | 1122.9048 | 0 | 17188.94 | 17188.94
13 | Office, Large | 14195.2896 | 19129.9554 | 7286.6221 | 3466.2278 | 32.2% | 43.4% | 16.53% | 7.864% | 14195.2896 | 19129.9554 | 7286.6221 | 3466.2278 | 0 | 44078.0949 | 44078.0949
16 | Office, Large | 101961.2898 | 72970.9395 | 3430.8468 | 6661.2222 | 55.11% | 39.44% | 1.854% | 3.6% | 101961.2898 | 72970.9395 | 3430.8468 | 6661.2222 | 0 | 185024.2983 | 185024.2983
17 | Office, Large | 5453.356 | 9228.339 | 1433.0749 | 2720.702 | 28.95% | 48.99% | 7.608% | 14.44% | 4910.6369 | 8309.9329 | 1290.455 | 2449.9372 | 1874.5099 | 18835.4718 | 16960.9619
Statewide | Office, Small | 335232.7507 | 281904.977 | 113281.9028 | 40606.8787 | 43.48% | 36.56% | 14.69% | 5.267% | 306649.5896 | 257868.7354 | 103623.0766 | 37144.5888 | 65740.5187 | 771026.5092 | 705285.9905
1 | Office, Small | 65229.4632 | 35998.9927 | 12971.4101 | 5353.9987 | 54.56% | 30.11% | 10.85% | 4.478% | 61053.0759 | 33694.1181 | 12140.9015 | 5011.2031 | 7654.5661 | 119553.8648 | 111899.2987
2 | Office, Small | 15927.0379 | 11699.6686 | 4233.5411 | 1756.7409 | 47.38% | 34.8% | 12.59% | 5.226% | 15539.8856 | 11415.2747 | 4130.6328 | 1714.0383 | 817.1571 | 33616.9885 | 32799.8314
3 | Office, Small | 3807.0755 | 3222.0878 | 1730.7407 | 645.2602 | 40.48% | 34.26% | 18.4% | 6.861% | 3304.382 | 2796.6371 | 1502.2104 | 560.0588 | 1241.8759 | 9405.1641 | 8163.2882
4 | Office, Small | 5167.4817 | 16215.7659 | 21623.2566 | 2242.8183 | 11.42% | 35.84% | 47.79% | 4.957% | 4769.6281 | 14967.2851 | 19958.4434 | 2070.1397 | 3483.8264 | 45249.3226 | 41765.4963
5 | Office, Small | 12851.3214 | 15793.9386 | 10394.1351 | 4113.7175 | 29.78% | 36.6% | 24.09% | 9.533% | 11964.5169 | 14704.0791 | 9676.8886 | 3829.8507 | 2977.7772 | 43153.1126 | 40175.3354
6 | Office, Small | 16204.5187 | 13781.3788 | 3564.9044 | 1404.0198 | 46.36% | 39.43% | 10.2% | 4.017% | 12953.6378 | 11016.6178 | 2849.7286 | 1122.3513 | 7012.4862 | 34954.8218 | 27942.3355
7 | Office, Small | 92999.7803 | 56772.5851 | 11980.6201 | 6324.2125 | 55.33% | 33.78% | 7.128% | 3.763% | 83838.388 | 51179.9276 | 10800.4113 | 5701.2154 | 16557.2558 | 168077.1981 | 151519.9423
8 | Office, Small | 6996.8101 | 12420.7993 | 2486.6478 | 2298.1209 | 28.91% | 51.32% | 10.27% | 9.495% | 6673.1279 | 11846.1958 | 2371.612 | 2191.8066 | 1119.6359 | 24202.3782 | 23082.7423
9 | Office, Small | 3737.4394 | 3424.3261 | 3268.1209 | 1262.5898 | 31.96% | 29.29% | 27.95% | 10.8% | 3111.3842 | 2850.7203 | 2720.6809 | 1051.0945 | 1958.5964 | 11692.4763 | 9733.8799
10 | Office, Small | 8928.9349 | 12484.5906 | 9269.594 | 2980.9381 | 26.52% | 37.09% | 27.54% | 8.855% | 7915.6093 | 11067.7413 | 8217.6077 | 2642.6378 | 3820.4616 | 33664.0576 | 29843.596
11 | Office, Small | 6195.8664 | 14718.2416 | 9675.3401 | 4998.7414 | 17.41% | 41.36% | 27.19% | 14.05% | 5363.5935 | 12741.1828 | 8375.6796 | 4327.2749 | 4780.4586 | 35588.1895 | 30807.7308
12c | Office, Small | 19492.1075 | 37335.7163 | 6810.7175 | 2801.0121 | 29.34% | 56.2% | 10.25% | 4.216% | 18662.937 | 35747.5006 | 6520.9979 | 2681.8604 | 2826.2574 | 66439.5534 | 63613.2959
12i | Office, Small | 10012.2744 | 8109.6762 | 2815.1428 | 190.4866 | 47.39% | 38.38% | 13.32% | 0.9016% | 7747.8096 | 6275.5198 | 2178.4451 | 147.4044 | 4778.4011 | 21127.58 | 16349.1789
13 | Office, Small | 9873.6859 | 12446.6034 | 5696.7273 | 1083.3003 | 33.93% | 42.77% | 19.58% | 3.723% | 9694.1976 | 12220.3434 | 5593.1696 | 1063.6076 | 528.9987 | 29100.3169 | 28571.3182
16 | Office, Small | 29359.5895 | 8324.2587 | 966.105 | 0 | 75.96% | 21.54% | 2.5% | 0% | 28946.7507 | 8207.2074 | 952.5201 | 0 | 543.4749 | 38649.9531 | 38106.4783
17 | Office, Small | 9827.4066 | 3632.7925 | 0 | 1176.8686 | 67.14% | 24.82% | 0% | 8.04% | 8440.6119 | 3120.1509 | 0 | 1010.7948 | 2065.5101 | 14637.0677 | 12571.5576

## Energy Usage
CalBEM Energy Consumption - OfficeMedium | [7 empty] | National Average (EnergyStar Portfolio Manager) |  |  |  | CEUS Energy Consumption - OfficeLarge
Prototype | CZ | CalBEM Electricity EUI (KBTU/ft²) | CalBEM Gas EUI (KBTU/ft²) | CalBEM Total EUI (KBTU/ft²) | New Construction Electricity EUI (KBTU/ft²) | New Construction Gas EUI (KBTU/ft²) | New Construction Total EUI (KBTU/ft²) | National Average | Acceptable RangeRange (25% Higher) | Acceptable RangeRange (25% Lower) | National Average Acceptable Range | Prototype | CZ | Total Floorspace (Thousand of ft2) | CEUS 2022 Electric Energy Intensity (kWh/ft²) | CEUS 2022 Annual Gas Intensity (kWh/ft²) | CEUS 2022 Total EUI (kBtu/ft²) | Acceptable Range (25% Higher) | Acceptable Range (25% Lower) | CEUS 2022 Acceptable Range
HotelSmall | 1 | 53.2 | 2.5 | 55.8 | 43.3 | 1.3 | 44.5 | 59.8 | 74.75 | 44.85 | 29.9 | OfficeLarge | 1 | 5279 | 16.7 | 5.01 | 74.0745 | 92.5932 | 55.5559 | 37.0373
| 2 | 64 | 2 | 65.9 | 46.4 | 1.2 | 47.6 | 65.5 | 81.875 | 49.125 | 32.75 |  | 2 | 12449 | 15.2 | 6.24 | 73.1533 | 91.4416 | 54.865 | 36.5766
| 3 | 55.2 | 1.6 | 56.9 | 45.8 | 1.2 | 47 | 62.2 | 77.75 | 46.65 | 31.1 |  | 3 | 242565 | 14.3 | 4.83 | 65.2716 | 81.5895 | 48.9537 | 32.6358
| 4 | 61.7 | 1.9 | 63.6 | 47.6 | 1.2 | 48.7 | 67.7 | 84.625 | 50.775 | 33.85 |  | 4 | 137610 | 14.4 | 4.76 | 65.3739 | 81.7174 | 49.0304 | 32.687
| 5 | 54.7 | 1.7 | 56.4 | 45.6 | 1.2 | 46.8 | 59.7 | 74.625 | 44.775 | 29.85 |  | 5 | 3834 | 8.6 | 9.32 | 61.143 | 76.4288 | 45.8573 | 30.5715
| 6 | 53.9 | 1.2 | 55.1 | 47.2 | 1.2 | 48.3 | 69 | 86.25 | 51.75 | 34.5 |  | 6 | 109980 | 10.9 | 4.88 | 53.8414 | 67.3017 | 40.381 | 26.9207
| 7 | 56.1 | 1.2 | 57.2 | 47.3 | 1.1 | 48.4 | 64.9 | 81.125 | 48.675 | 32.45 |  | 7 | 76710 | 14.8 | 9.36 | 82.4339 | 103.0424 | 61.8254 | 41.217
| 8 | 58 | 1.1 | 59.1 | 48.5 | 1.1 | 49.7 | 65.9 | 82.375 | 49.425 | 32.95 |  | 8 | 177013 | 10.4 | 4.24 | 49.9517 | 62.4396 | 37.4638 | 24.9758
| 9 | 58.2 | 1.2 | 59.4 | 47.7 | 1.1 | 48.9 | 65.9 | 82.375 | 49.425 | 32.95 |  | 9 | 240000 | 10.9 | 4.38 | 52.1354 | 65.1692 | 39.1015 | 26.0677
| 10 | 54.1 | 1.3 | 55.4 | 48.8 | 1.1 | 49.9 | 66.4 | 83 | 49.8 | 33.2 |  | 10 | 65927 | 11.9 | 7.21 | 65.2033 | 81.5041 | 48.9025 | 32.6017
| 11 | 58.3 | 1.5 | 59.7 | 48 | 1.2 | 49.2 | 68.6 | 85.75 | 51.45 | 34.3 |  | 11 | 18413 | 11.4 | 4.29 | 53.5343 | 66.9179 | 40.1507 | 26.7671
| 12 | 58.4 | 1.7 | 60.1 | 47.2 | 1.2 | 48.3 | 67.8 | 84.75 | 50.85 | 33.9 |  | 12 | 171620 | 14.4 | 6.12 | 70.0142 | 87.5178 | 52.5107 | 35.0071
| 13 | 60.4 | 1.4 | 61.8 | 48.6 | 1.2 | 49.8 | 68.3 | 85.375 | 51.225 | 34.15 |  | 13 | 19959 | 15.9 | 3.71 | 66.9093 | 83.6366 | 50.182 | 33.4547
| 14 | 56.6 | 1.6 | 58.2 | 48.8 | 1.2 | 50 | 69 | 86.25 | 51.75 | 34.5 |  | 14 | 18934 | 9.8 | 4.4 | 48.4504 | 60.563 | 36.3378 | 24.2252
| 15 | 55 | 1 | 56 | 52.5 | 1 | 53.5 | 67.7 | 84.625 | 50.775 | 33.85 |  | 15 | 23127 | 9.7 | 5.14 | 50.6341 | 63.2926 | 37.9756 | 25.317
| 16 | 57.4 | 2.2 | 59.6 | 47.4 | 1.3 | 48.7 | 70.6 | 88.25 | 52.95 | 35.3 |  | 16 | 39406 | 11.6 | 4.42 | 54.6602 | 68.3253 | 40.9952 | 27.3301
Source: CEUS 2022 Report/Data
And applying FZ-CZ multipliers for converting FZ data to CZ data
We don't have Medium Office specific data from CEUS. The data copied here belongs to the CEUS large office data which our Medium Office prototype falls within that group
[17 empty] | Gas Energy Intensity (kBTU/SqFt) | Electricity Usage (GWh) | Electric Energy Intensity (kWh/SqFt)
[17 empty] | 18.0173 | 15658.045 | 12.5271
[17 empty] | 16.0424 | 6463.1841 | 14.4617
[17 empty] | 21.3256 | 234.8134 | 15.1691
[17 empty] | 19.9748 | 5.6631 | 1.465
[17 empty] | 18.7413 | 272.79 | 8.6727
[17 empty] | 14.3249 | 315.6994 | 17.7281
[17 empty] | 31.9458 | 100.1791 | 8.5653
[17 empty] | 14.0764 | 2883.9083 | 10.3115
[17 empty] | 21.1421 | 331.7014 | 11.7275
[17 empty] | 3.7151 | 21.8777 | 5.5822
[17 empty] | 15.8881 | 166.8221 | 7.9944
[17 empty] | 17.5222 | 186.7593 | 9.4481
[17 empty] | 34.1347 | 1550.5291 | 14.7746
[17 empty] | 20.3743 | 261.2341 | 15.1978
[17 empty] | 34.5546 | 669.1849 | 15.1395
[17 empty] | 14.7867 | 1946.4624 | 10.52
[17 empty] | 15.9763 | 247.2365 | 13.1261
[17 empty] | Gas Energy Intensity (kBTU/SqFt) | Electricity Usage (GWh) | Electric Energy Intensity (kWh/SqFt)
[17 empty] | 18.4127 | 6497.9293 | 8.9108
[17 empty] | 22.8529 | 1095.5807 | 9.1607
[17 empty] | 19.118 | 251.6359 | 7.4854
[17 empty] | 28.2865 | 115.1927 | 12.2478
[17 empty] | 12.1512 | 463.1475 | 10.2381
[17 empty] | 15.1928 | 479.8668 | 11.1201
[17 empty] | 36.4148 | 235.2296 | 6.7295
[17 empty] | 10.4627 | 1257.7502 | 7.4809
[17 empty] | 9.9915 | 172.0269 | 7.0998
[17 empty] | 13.051 | 96.7898 | 8.278
[17 empty] | 15.5313 | 252.1703 | 7.4908
[17 empty] | 6.7586 | 317.4788 | 8.9209
[17 empty] | 24.2601 | 714.6554 | 10.7565
[17 empty] | 19.8576 | 214.7859 | 10.1661
[17 empty] | 37.3694 | 304.3703 | 10.4593
[17 empty] | 28.2419 | 399.4066 | 10.3339
[17 empty] | 12.2524 | 127.842 | 8.7341
Note on P32: Participating Utilities Only Weighted by "Weight-2018" & scaled to 2022 economy
Note on Q32: Participating Utilities Only Weighted by Gas-Weights & scaled to 2022 economy
Note on R32: Participating Utilities Only + Nonparticipating Utilities Weighted by Gas-Weights & scaled to 2022 economy
Note on T32: Participating Utilities Only + Nonparticipating Utilities Weighted & scaled to 2022 economy
Note on P50: Participating Utilities Only Weighted by "Weight-2018" & scaled to 2022 economy
Note on Q50: Participating Utilities Only Weighted by Gas-Weights & scaled to 2022 economy
Note on R50: Participating Utilities Only + Nonparticipating Utilities Weighted by Gas-Weights & scaled to 2022 economy
Note on T50: Participating Utilities Only + Nonparticipating Utilities Weighted & scaled to 2022 economy

## PV (hidden)
PV - TBD

## EV Charger (hidden)
EV Charger - OfficeMedium (TBD)
According To CEUS 2022 and their survey around 2018-2020, only 0.5% of large office buildings have EV chargers
Background Data [To be deleted prior to publication]
CEUS 2022 (Base on Survey 2018) | [7 empty] | The data presented in this worksheet represents the projected number of EV charger ports, or the number of cars that can be charged at the same time, for the year 2022 (last year of CEUC)
|  |  | Has EV Chargers |  |  |  |  | Level 1, 120 volt Charger (No. ports/SqFT) | [8 empty] | Level 2, 240 volt Charger (No. ports/SqFT) | [8 empty] | Level 3, DC fast (No. ports/SqFT) | [8 empty] | Charger Type Unkown (No. ports/SqFT) | [8 empty] | All Chargers Totals (No. ports/SqFT)
Calculation Method | Statewide/ Utility/ FCZ | Building Type | No | Yes | Total | Statewide/ Utility/ FCZ | Building Type | Public Only | Public & Employee | Public & Fleet | Employee Only | Employee & Fleet | Fleet Only | All 3 Types | Unknown | Level 1 Total | Public Only | Public & Employee | Public & Fleet | Employee Only | Employee & Fleet | Fleet Only | All 3 Types | Unknown | Level 2 Total | Public Only | Public & Employee | Public & Fleet | Employee Only | Employee & Fleet | Fleet Only | All 3 Types | Unknown | Level 3 Total | Public Only | Public & Employee | Public & Fleet | Employee Only | Employee & Fleet | Fleet Only | All 3 Types | Unknown | Unkonwn Total | Public Only | Public & Employee | Public & Fleet | Employee Only | Employee & Fleet | Fleet Only | All 3 Types | Unknown | Total
Floorspace-Based | Statewide | Office, Small | 91.63% | 8.371% | 100% | Statewide | Office, Small | 234.6311 | 257.2607 | 0 | 514.2646 | 0 | 22.2217 | 197.9831 | 0 | 1226.3611 | 108.945 | 831.3199 | 0 | 1332.4399 | 101.1641 | 78.5024 | 360.406 | 0 | 2812.7774 | 21.3759 | 0 | 0 | 15.7138 | 0 | 0 | 0 | 0 | 37.0897 | 56.9499 | 42.1476 | 0 | 212.1101 | 0 | 25.742 | 0 | 0 | 336.9496 | 421.9019 | 1130.7282 | 0 | 2074.5284 | 101.1641 | 126.466 | 558.3891 | 0 | 4413.1778
Floorspace-Based | FCZ01 Tot | Office, Small | 88.47% | 11.53% | 100% | FCZ01 Tot | Office, Small | 0 | 0 | 0 | 92.1148 | 0 | 0 | 5.6273 | 0 | 97.7421 | 0 | 290.1537 | 0 | 73.0277 | 95.6646 | 65.7399 | 24.3426 | 0 | 548.9286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9748 | 0 | 24.3426 | 0 | 0 | 52.3174 | 0 | 290.1537 | 0 | 193.1173 | 95.6646 | 90.0824 | 29.9699 | 0 | 698.988
Floorspace-Based | FCZ02 Tot | Office, Small | 87.66% | 12.34% | 100% | FCZ02 Tot | Office, Small | 0 | 0 | 0 | 0 | 0 | 21.0137 | 0 | 0 | 21.0137 | 0 | 189.1229 | 0 | 21.1561 | 0 | 0 | 0 | 0 | 210.279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189.1229 | 0 | 21.1561 | 0 | 21.0137 | 0 | 0 | 231.2926
Floorspace-Based | FCZ03 Tot | Office, Small | 93.39% | 6.61% | 100% | FCZ03 Tot | Office, Small | 0 | 78.751 | 0 | 0 | 0 | 0 | 0 | 0 | 78.751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.8719 | 0 | 0 | 0 | 0 | 0 | 0 | 12.8719 | 0 | 91.6228 | 0 | 0 | 0 | 0 | 0 | 0 | 91.6228
Floorspace-Based | FCZ04 Tot | Office, Small | 82.7% | 17.3% | 100% | FCZ04 Tot | Office, Small | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.11 | 0 | 0 | 0 | 0 | 44.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.9845 | 0 | 0 | 0 | 0 | 0 | 0 | 26.9845 | 0 | 26.9845 | 0 | 44.11 | 0 | 0 | 0 | 0 | 71.0945
Floorspace-Based | FCZ05 Tot | Office, Small | 96.4% | 3.601% | 100% | FCZ05 Tot | Office, Small | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.6347 | 0 | 0 | 0 | 0 | 19.6347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.6347 | 0 | 0 | 0 | 0 | 19.6347
Floorspace-Based | FCZ06 Tot | Office, Small | 93.41% | 6.592% | 100% | FCZ06 Tot | Office, Small | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2848 | 0 | 0 | 0 | 0 | 50.2848 | 0 | 0 | 0 | 50.2848 | 0 | 0 | 0 | 0 | 50.2848
Floorspace-Based | FCZ07 Tot | Office, Small | 91.77% | 8.231% | 100% | FCZ07 Tot | Office, Small | 0 | 0 | 0 | 199.1172 | 0 | 0 | 0 | 0 | 199.1172 | 0 | 229.2222 | 0 | 397.4995 | 0 | 0 | 0 | 0 | 626.7218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229.2222 | 0 | 596.6167 | 0 | 0 | 0 | 0 | 825.839
Floorspace-Based | FCZ08 Tot | Office, Small | 86.72% | 13.28% | 100% | FCZ08 Tot | Office, Small | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.6289 | 0 | 0 | 0 | 0 | 0 | 0 | 77.6289 | 0 | 0 | 0 | 14.8596 | 0 | 0 | 0 | 0 | 14.8596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.6289 | 0 | 14.8596 | 0 | 0 | 0 | 0 | 92.4885
Floorspace-Based | FCZ09 Tot | Office, Small | 90.94% | 9.064% | 100% | FCZ09 Tot | Office, Small | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Floorspace-Based | FCZ10 Tot | Office, Small | 95.6% | 4.399% | 100% | FCZ10 Tot | Office, Small | 0 | 0 | 0 | 27.5268 | 0 | 0 | 0 | 0 | 27.5268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.1608 | 0 | 0 | 0 | 0 | 50.1608 | 0 | 0 | 0 | 77.6876 | 0 | 0 | 0 | 0 | 77.6876
Floorspace-Based | FCZ11 Tot | Office, Small | 87.59% | 12.41% | 100% | FCZ11 Tot | Office, Small | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.1762 | 0 | 0 | 0 | 0 | 89.1762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.1762 | 0 | 0 | 0 | 0 | 89.1762
Floorspace-Based | FCZ12c Tot | Office, Small | 84.94% | 15.06% | 100% | FCZ12c Tot | Office, Small | 148.2736 | 164.5245 | 0 | 144.7477 | 0 | 0 | 181.593 | 0 | 639.1388 | 6.1825 | 0 | 0 | 246.2021 | 0 | 8.495 | 316.4711 | 0 | 577.3507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.3574 | 0 | 0 | 0 | 0 | 49.3574 | 154.456 | 164.5245 | 0 | 440.3072 | 0 | 8.495 | 498.0641 | 0 | 1265.8469
Floorspace-Based | FCZ12i Tot | Office, Small | 94.56% | 5.436% | 100% | FCZ12i Tot | Office, Small | 73.6026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.6026 | 0 | 0 | 0 | 369.1995 | 0 | 0 | 0 | 0 | 369.1995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.854 | 127.4565 | 0 | 0 | 369.1995 | 0 | 0 | 0 | 0 | 496.6561
Floorspace-Based | FCZ13 Tot | Office, Small | 96.48% | 3.519% | 100% | FCZ13 Tot | Office, Small | 0 | 0 | 0 | 22.8017 | 0 | 0 | 0 | 0 | 22.8017 | 36.1985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.1985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8017 | 0 | 0 | 0 | 0 | 22.8017 | 36.1985 | 0 | 0 | 45.6034 | 0 | 0 | 0 | 0 | 81.802
Floorspace-Based | FCZ16 Tot | Office, Small | 99.34% | 0.6613% | 100% | FCZ16 Tot | Office, Small | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.6415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.6415 | 20.2138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.2138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.8554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.8554
Floorspace-Based | FCZ17 Tot | Office, Small | 98.53% | 1.474% | 100% | FCZ17 Tot | Office, Small | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Data (hidden)
Space Function | Electric Equipment Load Intensity | Electric Equipment Load Intensity | LPD
Aging Eye/Low-vision (Corridor Area) |  |  | 2013 | 2016 | 2019 | 2025
Aging Eye/Low-vision (Dining)
Aging Eye/Low-vision (Lobby, Main Entry)
Aging Eye/Low-vision (Lounge/Waiting Area)
Aging Eye/Low-vision (Multipurpose Room)
Aging Eye/Low-vision (Religious Worship Area)
Aging Eye/Low-vision (Restroom)
Aging Eye/Low-vision (Stairwell)
Audience Seating Area
Auditorium Area
Auto Repair / Maintenance Area
Barber, Beauty Salon, Spa Area
Civic Meeting Place Area
Classroom, Lecture, Training, Vocational Areas
Concourse and Atria Area
Convention, Conference, Multipurpose and Meeting Area
Copy Room
Corridor Area
Dining Area (Bar/Lounge and Fine Dining)
Dining Area (Cafeteria/Fast Food)
Dining Area (Family and Leisure)
Electrical, Mechanical, Telephone Rooms
Exercise/Fitness Center and Gymnasium Areas
Financial Transaction Area
Healthcare Facility and Hospitals (Exam/Treatment Room)
Healthcare Facility and Hospitals (Imaging Room)
Healthcare Facility and Hospitals (Medical Supply Room)
Healthcare Facility and Hospitals (Nursery)
Healthcare Facility and Hospitals (Nurse's Station)
Healthcare Facility and Hospitals (Operating Room)
Healthcare Facility and Hospitals (Patient Room)
Healthcare Facility and Hospitals (Physical Therapy Room)
Healthcare Facility and Hospitals (Recovery Room)
Hotel Function Area
Kitchen/Food Preparation Area
Kitchenette or Residential Kitchen
Laboratory, Scientific
Laundry Area
Library (Reading Area)
Library (Stacks Area)
Lobby, Main Entry
Locker Room
Lounge, Breakroom, or Waiting Area
Manufacturing, Commercial & Industrial Work Area (Low Bay)
Manufacturing, Commercial & Industrial Work Area (High Bay)
Manufacturing, Commercial & Industrial Work Area (Precision)
Museum Area (Exhibition/Display)
Museum Area (Restoration Room)
Office Area (>250 square feet)
Office Area (<250 square feet)
Parking Garage Area (Parking Zone and Ramps)
Parking Garage Area (Daylight Adaptation Zones)
Pharmacy Area
Retail Sales Area (Grocery Sales)
Retail Sales Area (Retail Merchandise Sales)
Retail Sales Area (Fitting Room)
Religious Worship Area
Restrooms
Stairwell
Storage, Commercial/Industrial (Warehouse)
Storage, Commercial/Industrial (Refrigerated)
Storage, Commercial/Industrial (Shipping & Handling)
Storage (General)
Sports Arena - Playing Area (> 5,000 Spectators)
Sports Arena - Playing Area (2,000 - 5,000 Spectators)
Sports Arena - Playing Area (< 2,000 Spectators)
Sports Arena - Playing Area (Recreational)
Theater Area (Motion Picture)
Theater Area (Performance)
Transportation Function (Baggage Area)
Transportation Function (Ticketing Area)
Videoconferencing Studio
High-Rise Residential Living Spaces
Hotel/Motel Guest Room
All other
Attic
Reception Area
Elevator
Plenum
IT Room (EPD 12)
Computer Room (EPD 20)
Server Room (EPD 45)