## Notes
Data Sources
Dataset | Dodge 2023
CEUS 2022
ComStock 2023
Prototype | CEC Open parking garage prototype (CBECC 2022.3.1) | https://bees.noresco.com/software2022.html
Codes | Title 24, part 6, referred to as T24 (1984, 2001, 2007, 2013, 2016, 2022, 2025)
ASHRAE 90.1 (2022)
CFR Title 10 (2008, 2010, 2025)
ACM 2022
| T24 2022 - Appendix 5.4A and Appendix 5.4B | https://www.energy.ca.gov/publications/2022/2022-nonresidential-and-multifamily-alternative-calculation-method-reference
Other | 2022 Reduced infiltration CASE report | https://title24stakeholders.com/wp-content/uploads/2020/10/2022-T24-Final-CASE-Report_Reduce-Infiltration.pdf
| 2019 Outdoor Lighting CASE Report | https://title24stakeholders.com/wp-content/uploads/2016/10/T24-2019-CASE-Study-Results-Report-Outdoor-Sources_Final_with-Attachments.pdf
| 2019 High Efficiency Fume Hoods in Laboratory Spaces CASE Report | https://title24stakeholders.com/wp-content/uploads/2017/09/2019-T24-CASE-Report_Fume-Hoods_Final_September-2017.pdf?
| PNNL 20405, 2010 | file:///N:/Prj_SUS/2023/S23668%20SCE%20CA%20Prototypes%20Development/Technical/NR/0_Input%20data/Lighting/PNNL-20405.pdf
| Air leakage Memo, NORESCO, 2025 | Infiltration_rate_report_14May2025-Short-Version.docx
Construction Rate
Notes
*Definitions are from T24 2025 | Parking Garage Building is a building with building floor areas used for parking vehicles, and consists of at least a roof over the parking area enclosed with walls on all sides. The building includes areas for vehicle maneuvering to reach designated parking spaces. If the roof of a parking structure is also used for parking, the section without an overhead roof is considered an outdoor parking lot instead of a parking garage.
Daylight Adaptation Zone in a Parking Garage is the interior path of travel for vehicles adjacent to the entrance or exit of a parking garage as needed for visual adaptation to transition from exterior daylight levels to interior light levels. Daylight Adaptation Zones only include the path of vehicular travel and do not include adjacent Parking Areas.
Parking Zone and Ramps in a Parking Garage is used for the purpose of parking and maneuvering of vehicles. Parking areas include sloping floors of a parking garage. Ramps and driveways specifically for the purpose of moving vehicles between floors of a parking garage. Parking areas and ramps do not include Daylight Adaptation Zones or the roof of a Parking Garage, which may be present in a Parking Garage.

## Prototype
NORESCO, Updated August 2025
ParkingOpen
Characteristic | Value | Data Sources
Building Type | Open Parking
Building Category | Nonresidential
Vintages | 4 Vintages: Pre-1978 , 1978-1997 ,1998-2007 , 2008-2018 New Construction (2019+) | Based on the vintage bin analysis | NonRes-Vintage bins-Draft Report-30Nov2023-Final.docx
Shape |  | The analysis uses prototype geometry originally developed by CEC. This is an open parking garage, there are no actual windows—the space is fully open to ambient air and therefore unconditioned.
Total Floor Area (ft²) | 185627.8 | Same as CEC
Aspect Ratio | 1 | Same as CEC
Number of Floors | 3 | Same as CEC
Roof type | Flat | Same as CEC
WWR | n/a (50% openings all around the building) | Same as CEC
Shading Geometry | No Shades | Same as CEC
Floor to floor height (feet) | 13 | Same as CEC
Floor to ceiling height (feet) | 13 | Same as CEC
Glazing sill height (feet) | n/a | Same as CEC
Above grade wall area (ft²) | 27302.66
Gross wall area (ft²) | 27302.66
Roof area (ft²) | 63116
Underground Gross Wall Area (ft²) | 0

## Zones
Proposed Layout - ParkingOpen
Space Type | Space/Thermal Zone | HVAC System Name/AHU Name | Schedule Category | Conditioned (Y/N) | Area Fraction | Area (ft²) | Volume (ft³) | Multipliers | Number of People | People (Persons/1,000 ft²) [T24, 2025,Table 120.1-A]
Parking Garage Area (Parking Zone and Ramps) | Core | n/a | Parking | Yes | 3.26% | 6050.55 | 13110.37 | 3 | 30.2527 | 5
Parking Garage Area (Daylight Adaptation Zones) | Daylight adaption | n/a | Parking | Yes | 0.9805% | 1820.14 | 23663.58 | 1 | 9.1007 | 5
Parking Garage Area (Parking Zone and Ramps) | East perimeter | n/a | Parking | Yes | 7.435% | 13801.33 | 29904.25 | 3 | 69.0066 | 5
Parking Garage Area (Parking Zone and Ramps) | North perimeter | n/a | Parking | Yes | 7.435% | 13801.33 | 29904.25 | 3 | 69.0066 | 5
Retail Sales Area (Retail Merchandise Sales) | Parking attendant | AHU-1 | TicketAttendant | Yes | 0.02158% | 40.05 | 320 | 1 | 0.68085 | 17
Parking Garage Area (Parking Zone and Ramps) | South perimeter | n/a | Parking | Yes | 7.435% | 13801.33 | 29904.25 | 3 | 69.0066 | 5
Parking Garage Area (Parking Zone and Ramps) | West perimeter | n/a | Parking | Yes | 7.435% | 13801.33 | 29904.25 | 3 | 69.0066 | 5
Total (3 Space types) | Total ( 8 spaces) | Total ( 1Thermal Zones) |  | Total (1 Conditioned zones) |  | 185627.8 |  |  | 316.0609
Background Data [To be deleted prior to publication]
N

## Envelope
Envelope - ParkingOpen
Element | Prototype | Assembly Type | Construction | Thermal properties | Vintage | Selected T24 | Note | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
External Wall | ParkingOpen | ExtWall_Concrete4in_Insulated | 4 in. Concrete- Insulation (insulation only for ticket attendance ext wall) | U-value IP | Pre 1978 | N/A | ASHRAE 90.1, 2022 Table A3.1-2, 4", R-0, 135 lb/ft3 Density | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87
[5 empty] | 1978-1997 | 1986 | Package A/ Heat Capacity was considered ~10 (BTU/F/ft²) | 0.39968 | 0.39968 | 0.39968 | 0.39968 | 0.39968 | 0.39968 | 0.39968 | 0.39968 | 0.39968 | 0.39968 | 0.39968 | 0.39968 | 0.39968 | 0.39968 | 0.39968 | 0.39968
[5 empty] | 1998-2007 | 2001 | Table 1-H | 0.34 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.34
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.196 | 0.17 | 0.278 | 0.227 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.17 | 0.138 | 0.227 | 0.196 | 0.364 | 0.364 | 0.364 | 0.364 | 0.364 | 0.138 | 0.138 | 0.138 | 0.138 | 0.138 | 0.138 | 0.138
Roof | ParkingOpen | FlatRoof_Concrete8in_Insulated | Built-up Roof 8 in concrete deck + isulation ((insulation only for ticket attendant ceiling) | U-value IP | Pre 1978 | N/A | Considering 30 years for roof/ insulation replacement. | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 1978-1997 | 1992 |  | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 1998-2007 | 2001 | Table 1-H | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.049 | 0.039 | 0.039 | 0.039 | 0.049 | 0.075 | 0.067 | 0.067 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038
**The unconditioned portion of the parking garage should only have concrete walls. However, there is also a small conditioned area served by an AHU system which should still use insulation in the assembly.

## HVAC System
HVAC system - ParkingOpen
Vintage | Zones | Heating | Cooling | Air Distribution | Source | Note
Exisiting | Conditioned zones-Parking Attendant Zone | Electric Unit heater | n/a | n/a | Engineering judgement
New Construction | Conditioned zones-Parking Attendant Zone | Electric Unit heater | n/a | n/a | Engineering judgement
Efficiency of HVAC system
Vintage | Upgrade/Installed year | Electric Unit heater | Heating DX | Cooling DX | Sources | Note
Pre 1978 | 2008 | Thermal Efficiency of 1 | n/a | n/a
1978-1997
1998-2007
2008-2018 | 2013 | Thermal Efficiency of 1 | n/a | n/a
New Construction | 2025 | Thermal Efficiency of 1 | n/a | n/a
|  | * Et = Combustion efficiency | * Et = Thermal efficiency
Fan power
Vintage | Approach | System | Total Static Pressure (TSP) in w.c. [PNNL 20405, 2010, Table 5.11] | Fan Efficiency [ACM, 2025] | Fan Motor and Drive Efficiency [ACM 2025, Table 13] | W/cfm [ACM 2025, Table 14 and 15] | Data Source | Note
Existing | PNNL TSP | PTAC, PTHP, or FCUs | 1.33 | 0.65 | 0.9 |  | PNNL 2010 TSD
Brake horse power (bhp)=(Supply cfm*TSP in w.c.)/(6356*Fan efficiency)
Fan power (w/cfm) = bhp/motor and drive efficiency *746
New Construction | ACM 2025 | PTAC, PTHP, or FCUs | 1.33 | 0.65 | 0.9 | 0.53 | 2025 ACM
* 0.9 is an average fan efficiency according to ACM 2025, Table 13
Fan total eff (E+ input) = 0.65 x Motor_eff
TSP (E+ input) in w.c. = Motor_eff/746 x (6356 x Fan_eff) x W/cfm
Fan_eff=0.65
Background Data [To be deleted prior to publication]

## Ventilation
Outdoor Airflow Rate - ParkingOpen
Space Type | Space/Thermal Zone | Number of People | Floor Area (ft²) | cfm/person [T24, 2025, Equation 120.1-F and Table 120.1-A] | cfm/ft² [T24, 2025, Equation 120.1-F and Table 120.1-A] | Required exhaust rate-CFM/ft²- [T24, 2025, Table 120.1-B – minimum exhaust rates] | Total cfm driven by people | Total cfm driven by area | Total cfm driven by exhaust | Total cfm | Notes
Parking Garage Area (Parking Zone and Ramps) | Core | 30.2527 | 6050.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Parking Garage Area (Daylight Adaptation Zones) | Daylight adaption | 9.1007 | 1820.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Parking Garage Area (Parking Zone and Ramps) | East perimeter | 69.0066 | 13801.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Parking Garage Area (Parking Zone and Ramps) | North perimeter | 69.0066 | 13801.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Retail Sales Area (Retail Merchandise Sales) | Parking attendant | 0.68085 | 40.05 | 15 | 0.2 | 0 | 10.2127 | 8.01 | 0 | 10.2127 | Exhaust shall not be required where two or more sides comprise walls that are at least 50% open to the outside.
Parking Garage Area (Parking Zone and Ramps) | South perimeter | 69.0066 | 13801.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Parking Garage Area (Parking Zone and Ramps) | West perimeter | 69.0066 | 13801.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Background Data [To be deleted prior to publication]
Requirement | Description | Criterion | Value / Standard
Airflow Modulation | Reduce to minimum 10 ACH or pressurization limit | Pressure relationship | Negative relative to adjacent spaces
Variable Exhaust/Makeup Air | Coordinated VAV systems for pressurization | Pressure differential target | 0.01–0.05 in. w.c.
Fan Power Limit | ≤ 0.65 W/CFM (standard); ≤ 0.85 W/CFM (with filtration) | Infiltration modeling | Not the primary OA source; modeled as tightly controlled
Sash Closure Controls | Auto-close after 5 min inactivity with safety features | Envelope air barrier | Required per T24 standards
Makeup Air Compliance | Must meet Section 140.4(o) standards | Standard reference | ANSI Z9.5-2022, ASHRAE 62.1, ASHRAE 90.1
Outdoor Airflow Rate - Open Parking
Space Type | Total ft² | Min. occupancy load (persons/1000 ft²) | Total Number of Occupants | cfm/ft² (Table 120.1-A – Minimum Ventilation Rates) | Required Exhaust Rate-CFM/ft² (Table 120.1-B – Minimum Exhaust Rates) | cfm | Source
Parking Garage Area (Parking Zone and Ramps) | 0 | 5 | 0 | 0.15 | 1 | 0 | T24, 2025, Equation 120.1-F and Table 120.1-A
#REF! | 0 | #REF! | #REF! | 0.15 |  | #REF!
Total | 0 |  | #REF! |  |  | #REF!

## Thermostat
Thermostat Setpoints - ParkingOpen
Setpoint | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16 | Source | Note
Parking Attendant Heating Setpoint (F) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | T24 2022 - Appendix 5.4B | The parking attendant area is fully conditioned in the CEC model, this is the setpoint requirement for that area.
Parking AttendantSetback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Parking Attendant Setpoint (F) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
Parking Attendant Setback (F) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
Office Cooling Setback (F) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
Source: PNNL Healthcare-Outpaitiet prototype use this setpoints: Administration zones: 72°F Cooling/70°F Heating, Critical zones: 72°F Cooling/70°F Heating, Operating rooms: 65°F Cooling/65°F Heating
PNNL Healthcare-Outpaitiet prototype use this setbacks: 77°F Cooling/65°F Heating, Critical zones: no setback, Operating rooms: 72°F Cooling/65°F Heating

## Water Heater
Water Heater - ParkingOpen
Vintage | WH Type | Efficiency | Tank Volume (gal) | Tank Loss | Unit | Note
Existing | Electric | 1 | 30 | 1.2 | (%/hr) | Engineering judgement
New Construction | Electric | 1 | 30 | 1.2 | (%/hr) | According to 2025 ACM
Peak Hot Water Consumption
Space Name | Baseline WH Type [CEUS 2022] | Total Area (ft²) | Number of People | Hot Water Usage Specification (gal/hr per person) [T24, 2022, Appendix 5.4A , sheet: "2022 SpaceFuncData-Input"] | Peak Hot Water Usage (gal/hr) | Peak Hot Water Usage (gal/min)
Core | Electric | 6050.55 | 30.2527 | 0 | 0 | 0
Daylight adaption | Electric | 1820.14 | 9.1007 | 0 | 0 | 0
East perimeter | Electric | 13801.33 | 69.0066 | 0 | 0 | 0
North perimeter | Electric | 13801.33 | 69.0066 | 0 | 0 | 0
Parking attendant | Electric | 40.05 | 0.68085 | 0.18 | 0.12255 | 0.0020425
South perimeter | Electric | 13801.33 | 69.0066 | 0 | 0 | 0
West perimeter | Electric | 13801.33 | 69.0066 | 0 | 0 | 0
Total |  | 7870.69 | 39.3535 |  | 0.12255 | 0.0020425
Water Heater Capacity, Tank Capacity, and Tank Loss
WH Type | Peak Hot Water Usage (gal/hr) | Heat Output (Btu/hr) [ACM, 2025, 5.9.2: Rated capacity section] | WH Capacity (Btu/hr) [ACM, 2025, 5.9.2: Rated capacity section] | Required Energy Input (Btu/hr) | Storage Volume (ga) | Standby Loss | Unit | Off/On Cycle Loss Coefficient to Ambient Temp (Btu/h-F) | Source
Electric | 75 | 49726.2 | 29835.72 | 31412.6342 | 30 | 1.2 | %/hr | 3.0024 | Standby loss equation: Title 20, §1605.1 Table F-4 WH capacity equation: ACM, 2025, 5.9.2: Rated capacity section)
Total | 75 | 49726.2 | 29835.72 | 31412.6342
Design supply temperature (F) | 135 | Ref: T24 2022 - Appendix 5.4B |  |  | Standby Loss for Existing | 1.2 | Btu/hr | 3.0024
Cold Water supply temperature (F) | 55 | Ref: ACM, 2025, 5.9.2: Rated capacity section
WH system factor | 0.6 | Ref: ACM, 2025, 5.9.2: Rated capacity section
Reheat multiplier | 0.4
* The 0.40 multiplier is a storage sizing factor used to account for the fact that the water heater doesn't need to store the full peak hour demand—it can reheat water during that time. This factor assumes that the heater will recover part of the hot water used during the peak hour, so only 40% of the peak hour demand needs to be stored at any given moment.
**For Gas Water Heater: UA(Btu/h-°F)​=Q˙​SL​ (Btu/h)/ΔT (∘F)​
Ambient temp | 68
Delta T | 67
** For Electric Water Heater: UA(Btu/h-°F)​= 0.0834 *SL​ (%/hr)*V gal
Background Data [To be deleted prior to publication]

## Interior Lights
Interior Lighting - ParkingOpen
Space Type | New Construction |  |  | Existing
| Lighting density (W/ft²) | Additional lighting power for porTable lighting (W/ft²) | Source | LPD (W/ft²) | Additional LPD for PorTable Lighting (W/ft²) | Source
Parking Garage Area (Parking Zone and Ramps) | 0.1 |  | T24, 2025, Table 140.6 C (Area category method) | 0.14 |  | T24, 2016, Table 140.6 C (Area category method)
Parking Garage Area (Daylight Adaptation Zones) | 1 |  |  | 0.75
Retail Sales Area (Retail Merchandise Sales) | 0.95 |  |  | 1.2 |  |  | *Parking attendant zone

## Ext Lighting
Exterior Lighting - ParkingOpen
Motion Controlled Luminaires (W) | Non-motion Controlled Luminaires (W) | Total (W) | Source
200 | 782.541 | 982.541 | T24, 2022 & 2025 2019 Outdoor Lighting CASE report PNNL 90.1-2010 TSD
Exterior Lighting
Items (Assume LZ2) | Assumptions [2019 Outdoor Lighting CASE Report & PNNL 90.1-2010 TSD] |  | Unit | Lighting Power Allowance [T24, 2025, Table 140.7-A & 140.7-B] | Unit | Exterior Lighting Power (W)
IWA (Initial Wattage Allowance) |  |  |  | 200 | (W) | 200
Parking area | 400 ft² for every parking space 1 parking space per 830 ft² of gross building area | 0 | (ft²) | 0.019 | (W/ft²)
Building Entrance | 14 building entrance per PNNL Model |  | (count) | 15 | (W/ea) | 0
Hardscape Ornamental Light | 0.1 ft² per 1 ft² of gross building area for hardscape ornamental light | 18563 | (ft²) | 0.007 | (W/ft²) | 129.941
Building façade | 0.1 W per 1 ft² of facade area Façade Area = Perimeter × 0.5 × 13 ft * The 0.5 factor assumes that only half of the perimeter walls are lit. -Formula ia developed based on the 2019 Outdoor Lighting CASE report | 6526 | (ft²) | 0.1 | (W/ft²) | 652.6
Security lighting for retail parking | 1 sf per 100 sf of gross building area |  | (ft²) | 0.005 | (W/ft²) | 0
Non-sales canopy |  |  | (ft²) | 0.137 | (W/ft²) | 0
Motion Controlled Luminaires (W) | [5 empty] | 200
Non-motion-controlled Luminaires | [5 empty] | 782.541
Total | [5 empty] | 982.541
Total floor area | 185627.8
Perimeter | 1004
Floors | 3
Background Data [To be deleted prior to publication]

## Equipment
Equipment - ParkingOpen
Spaces | Plug load Power Density (W/ft²) | Gas Power Density (Btu/hr-ft²) | Refrigeration Power Density (W/ft²) | Source | Note
Parking Garage Area (Parking Zone and Ramps) | 0 | 0 | 0 | T24 2022 - Appendix 5.4A
Parking Garage Area (Daylight Adaptation Zones) | 0 | 0 | 0
Retail Sales Area (Retail Merchandise Sales) | 0.4 | 0 | 0 |  | Parking attendant zone - Plug load and schedules project with CEC, 2025
Background Data [To be deleted prior to publication]

## Schedules
Schedules - ParkingOpen
Zone | Schedule Category | Schedule | Source | Type | Hour
[5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Parking Zones | Parking | Occupancy | T24 2022 - Appendix 5.4B, [Parking] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Parking Zones | Parking | Lights | T24 2022 - Appendix 5.4B, [Parking] | Weekday | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5
|  |  |  | Saturday | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  |  | Sunday | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Parking Zones | Parking | ElecEquipment | T24 2022 - Appendix 5.4B, [Parking] | Weekday | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5
|  |  |  | Saturday | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  |  | Sunday | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Parking Zones | Parking | GasEquipment | T24 2022 - Appendix 5.4B, [Parking] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Parking Attendant
Ticket Attendant Zone | TicketAttendant | Occupancy | T24 2022 - Appendix 5.4B, [Parking] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ticket Attendant Zone | TicketAttendant | Lights | T24 2022 - Appendix 5.4B, [Parking] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ticket Attendant Zone | TicketAttendant | ElecEquipment | T24 2022 - Appendix 5.4B, [Parking] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ticket Attendant Zone | TicketAttendant | ServiceHotWater | T24 2022 - Appendix 5.4B, [Parking] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ticket Attendant Zone | TicketAttendant | HVACAvail | T24 2022 - Appendix 5.4B, [Parking] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ticket Attendant Zone | TicketAttendant | Infiltration | T24 2022 - Appendix 5.4B, [Parking] | Weekday | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Saturday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Sunday | bar: Hour 1 to Hour 24
Ticket Attendant Zone | TicketAttendant | HtgSetpt | T24 2022 - Appendix 5.4B, [Parking] | Weekday | 60 | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  |  | Saturday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  |  | Sunday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Ticket Attendant Zone | TicketAttendant | ClgSetpt | T24 2022 - Appendix 5.4B, [Parking] | Weekday | 85 | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 85 | 85 | 85 | 85 | 85 | 85 | 85
|  |  |  | Saturday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
|  |  |  | Sunday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
Other
| Building | Elevator | T24 2022 - Appendix 5.4B, [Parking] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.69 | 0.43 | 0.37 | 0.43 | 0.58 | 0.48 | 0.37 | 0.37 | 0.46 | 0.62 | 0.2 | 0.12 | 0.04 | 0.04 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.14 | 0.21 | 0.18 | 0.25 | 0.21 | 0.13 | 0.08 | 0.04 | 0.05 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Building | ExtLightingNonMotionCtrl | Siimlar | Weekday | bar: Hour 1 to Hour 24
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
| Building | ExtLightingMotionCtrl | PNNL Hospital Prototype (2022) Modified to 0 for 11 pm to 5 am during weekday and 12 am to 5 am during weekend | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Parking Zones | Building | ParkingPeopleActivityLevel | same as stairs | Weekday | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5
|  |  |  | Saturday | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5
|  |  |  | Sunday | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5
Ticket Attendant Zone | Building | TicketAttendantPeopleActivityLevel | assumed same as meeting room | Weekday | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2
|  |  |  | Saturday | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2
|  |  |  | Sunday | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2
Background Data [To be deleted prior to publication] | bar: Hour 1 to Hour 2
Parkig Attendance | Retail Occupancy | T24 2022 - Appendix 5.4B | T24 2022 - Appendix 5.4B, [Parking] | Weekday
Saturday
Sunday
Parkig Attendance | Retail Lighting | T24 2022 - Appendix 5.4B | T24 2022 - Appendix 5.4B, [Parking] | Weekday
Saturday
Sunday
Parkig Attendance | ElecEquipment | Plug load and schedules project with CEC, 2025 | Plug load and schedules project with CEC, 2025 | Weekday
Saturday
Sunday
Parking Zones | Parking | GasEquipment | T24 2022 - Appendix 5.4B, [Parking] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.75 | 0.75 | 0.75 | 0.75 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.75 | 0.75 | 0.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Parking Zones | Parking | Refrigeration | T24 2022 - Appendix 5.4B, [Parking] | Weekday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Saturday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Sunday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9

## Energy Usage
CalBEM Energy Consumption - ParkingOpen | [11 empty] | Energy Consumption - ParkingOpen
Prototype | CZ | CalBEM Electricity EUI (KBTU/ft²) | CalBEM Gas EUI (KBTU/ft²) | CalBEM Total EUI (KBTU/ft²) | New Construction Electricity EUI (KBTU/ft²) | New Construction Gas EUI (KBTU/ft²) | New Construction Total EUI (KBTU/ft²) | National Average | Acceptable Range (25% Higher) | Acceptable Range (25% Lower) | National Average Acceptable EUI Range | Prototype | CZ | Total Floorspace (Thousand of ft²) | CEUS 2023 Electricity EUI (kBtu/ft²) | CEUS 2023 Gas EUI (kBtu/ft²) | CEUS 2023 Total EUI (kBtu/ft²) | Acceptable Range (20% Higher) | Acceptable Range (20% Lower) | CEUS 2022 Acceptable EUI Range
ParkingOpen | 1 | 3.9 | 0 | 3.9 | 3.1 | 0 | 3.1 | 4.2 | 5.25 | 3.15 | 2.1 | ParkingOpen | 1
| 2 | 3.7 | 0 | 3.7 | 2.9 | 0 | 2.9 | 4.2 | 5.25 | 3.15 | 2.1 |  | 2
| 3 | 3.7 | 0 | 3.7 | 2.9 | 0 | 2.9 | 4.2 | 5.25 | 3.15 | 2.1 |  | 3
| 4 | 3.6 | 0 | 3.6 | 2.8 | 0 | 2.8 | 4.2 | 5.25 | 3.15 | 2.1 |  | 4
| 5 | 3.6 | 0 | 3.6 | 2.8 | 0 | 2.8 | 4.2 | 5.25 | 3.15 | 2.1 |  | 5
| 6 | 3.5 | 0 | 3.5 | 2.7 | 0 | 2.7 | 4.2 | 5.25 | 3.15 | 2.1 |  | 6
| 7 | 3.5 | 0 | 3.5 | 2.7 | 0 | 2.7 | 4.2 | 5.25 | 3.15 | 2.1 |  | 7
| 8 | 3.4 | 0 | 3.4 | 2.6 | 0 | 2.6 | 4.2 | 5.25 | 3.15 | 2.1 |  | 8
| 9 | 3.5 | 0 | 3.5 | 2.7 | 0 | 2.7 | 4.2 | 5.25 | 3.15 | 2.1 |  | 9
| 10 | 3.5 | 0 | 3.5 | 2.7 | 0 | 2.7 | 4.2 | 5.25 | 3.15 | 2.1 |  | 10
| 11 | 3.6 | 0 | 3.6 | 2.8 | 0 | 2.8 | 4.2 | 5.25 | 3.15 | 2.1 |  | 11
| 12 | 3.6 | 0 | 3.6 | 2.8 | 0 | 2.8 | 4.2 | 5.25 | 3.15 | 2.1 |  | 12
| 13 | 3.6 | 0 | 3.6 | 2.8 | 0 | 2.8 | 4.2 | 5.25 | 3.15 | 2.1 |  | 13
| 14 | 3.6 | 0 | 3.6 | 2.8 | 0 | 2.8 | 4.2 | 5.25 | 3.15 | 2.1 |  | 14
| 15 | 3.4 | 0 | 3.4 | 2.6 | 0 | 2.6 | 4.2 | 5.25 | 3.15 | 2.1 |  | 15
| 16 | 3.8 | 0 | 3.8 | 3 | 0 | 3 | 4.2 | 5.25 | 3.15 | 2.1 |  | 16
chrome-extension://efaidnbmnnnibpcajpcglclefindmkaj/https://www.energystar.gov/sites/default/files/tools/Parking%20Adjustment%20Technical%20Reference_508.pdf | [11 empty] | Ref: CEUS 2022 Report
And converted FZ level data to CZ level
Background Data [To be deleted prior to publication]

## Weights (hidden)
% of Floor Area per CZ and Vintage Bin - ParkingOpen | [7 empty] | % of Floor Area per CZ and Vintage Bin - ParkingOpen
Prototype | CZ | Vintage Bin | [5 empty] | Prototype | Vintage Bin | CZ
|  | Pre-1978 | 1978-1997 | 1998-2007 | 2008-2018 | Not available |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
Open Parking | 1 | [5 empty] | 0% | Open Parking | Pre-1978 | [16 empty] | 0%
| 2 | [5 empty] | 0% |  | 1978-1997 | [16 empty] | 0%
| 3 | [5 empty] | 0% |  | 1998-2007 | [16 empty] | 0%
| 4 | [5 empty] | 0% |  | 2008-2018 | [16 empty] | 0%
| 5 | [5 empty] | 0% |  | Not available | [16 empty] | 0%
| 6 | [5 empty] | 0% |  | Total
| 7 | [5 empty] | 0%
| 8 | [5 empty] | 0%
| 9 | [5 empty] | 0%
| 10 | [5 empty] | 0%
| 11 | [5 empty] | 0%
| 12 | [5 empty] | 0%
| 13 | [5 empty] | 0%
| 14 | [5 empty] | 0%
| 15 | [5 empty] | 0%
| 16 | [5 empty] | 0%
Statewide
Ref: CEUS 2022 dataset
Background Data [To be deleted prior to publication]

## PV (hidden)
PV - ParkingOpen
TBD

## EV Charger (hidden)
EV Charger - ParkingOpen
TBD
Background Data [To be deleted prior to publication]

## Data (hidden)
Space Function | Electric Equipment Load Intensity | Electric Equipment Load Intensity | LPD
Aging Eye/Low-vision (Corridor Area) |  |  | 2013 | 2016 | 2019 | 2025
Aging Eye/Low-vision (Dining)
Aging Eye/Low-vision (Lobby, Main Entry)
Aging Eye/Low-vision (Lounge/Waiting Area)
Aging Eye/Low-vision (Multipurpose Room)
Aging Eye/Low-vision (Religious Worship Area)
Aging Eye/Low-vision (Restroom)
Aging Eye/Low-vision (Stairwell)
Audience Seating Area
Auditorium Area
Auto Repair / Maintenance Area
Barber, Beauty Salon, Spa Area
Civic Meeting Place Area
Classroom, Lecture, Training, Vocational Areas
Concourse and Atria Area
Convention, Conference, Multipurpose and Meeting Area
Copy Room
Corridor Area
Dining Area (Bar/Lounge and Fine Dining)
Dining Area (Cafeteria/Fast Food)
Dining Area (Family and Leisure)
Electrical, Mechanical, Telephone Rooms
Exercise/Fitness Center and Gymnasium Areas
Financial Transaction Area
Healthcare Facility and Hospitals (Exam/Treatment Room)
Healthcare Facility and Hospitals (Imaging Room)
Healthcare Facility and Hospitals (Medical Supply Room)
Healthcare Facility and Hospitals (Nursery)
Healthcare Facility and Hospitals (Nurse's Station)
Healthcare Facility and Hospitals (Operating Room)
Healthcare Facility and Hospitals (Patient Room)
Healthcare Facility and Hospitals (Physical Therapy Room)
Healthcare Facility and Hospitals (Recovery Room)
Hotel Function Area
Kitchen/Food Preparation Area
Kitchenette or Residential Kitchen
Laboratory, Scientific
Laundry Area
Library (Reading Area)
Library (Stacks Area)
Lobby, Main Entry
Locker Room
Lounge, Breakroom, or Waiting Area
Manufacturing, Commercial & Industrial Work Area (Low Bay)
Manufacturing, Commercial & Industrial Work Area (High Bay)
Manufacturing, Commercial & Industrial Work Area (Precision)
Museum Area (Exhibition/Display)
Museum Area (Restoration Room)
Office Area (>250 square feet)
Office Area (<250 square feet)
Parking Garage Area (Parking Zone and Ramps)
Parking Garage Area (Daylight Adaptation Zones)
Pharmacy Area
Retail Sales Area (Grocery Sales)
Retail Sales Area (Retail Merchandise Sales)
Retail Sales Area (Fitting Room)
Religious Worship Area
Restrooms
Stairwell
Storage, Commercial/Industrial (Warehouse)
Storage, Commercial/Industrial (Refrigerated)
Storage, Commercial/Industrial (Shipping & Handling)
Storage (General)
Sports Arena - Playing Area (> 5,000 Spectators)
Sports Arena - Playing Area (2,000 - 5,000 Spectators)
Sports Arena - Playing Area (< 2,000 Spectators)
Sports Arena - Playing Area (Recreational)
Theater Area (Motion Picture)
Theater Area (Performance)
Transportation Function (Baggage Area)
Transportation Function (Ticketing Area)
Videoconferencing Studio
High-Rise Residential Living Spaces
Hotel/Motel Guest Room
All other
Attic
Reception Area
Elevator
Plenum
IT Room (EPD 12)
Computer Room (EPD 20)
Server Room (EPD 45)