## Notes
Data Sources
Dataset | Dodge 2023
| CEUS 2022 | https://www.energy.ca.gov/publications/2023/2022-california-commercial-end-use-survey-ceus-final-report
| CBECS 2018 | https://www.eia.gov/consumption/commercial/data/2018/index.php?view=microdata
| ComStock 2023 | https://data.openei.org/s3_viewer?bucket=oedi-data-lake&prefix=nrel-pds-building-stock%2Fend-use-load-profiles-for-us-building-stock%2F2023%2Fcomstock_amy2018_release_2%2Fmetadata_and_annual_results%2Fby_state%2Fstate%3DCA%2F
Prototype |  | https://bees.noresco.com/software2022.html
https://www.energycodes.gov/prototype-building-models#Commercial
| DEER prototypes (June 2023) | https://github.com/sound-data/DEER-Prototypes-EnergyPlus
Codes | Title 24, part 6, referred to as T24 (1984, 1992, 2001, 2007, 2013, 2022, 2025)
ASHRAE 90.1 (2022)
| CFR Title 10 (2010) | https://www.govinfo.gov/content/pkg/FR-2009-03-23/pdf/FR-2009-03-23.pdf
| CFR Title 10 ( 2024) | https://www.govinfo.gov/content/pkg/CFR-2024-title10-vol3/pdf/CFR-2024-title10-vol3-part431-subpartF.pdf
Title 20
Others | ACM (2022)
| T24 2022 - Appendix 5.4A and Appendix 5.4B | https://www.energy.ca.gov/publications/2022/2022-nonresidential-and-multifamily-alternative-calculation-method-reference
| 2022 Reduced infiltration CASE report | https://title24stakeholders.com/wp-content/uploads/2020/10/2022-T24-Final-CASE-Report_Reduce-Infiltration.pdf
| 2019 Outdoor Lighting CASE Report | https://title24stakeholders.com/wp-content/uploads/2016/10/T24-2019-CASE-Study-Results-Report-Outdoor-Sources_Final_with-Attachments.pdf
| PNNL 20405, 2010 | https://www.pnnl.gov/main/publications/external/technical_reports/PNNL-20405.pdf
| Air leakage Memo, NORESCO, 2025 | https://2050partners.sharepoint.com/:w:/r/sites/CalBEMCollaborativeEfforts/_layouts/15/Doc.aspx?sourcedoc=%7B3BEF8F74-7FAC-44F2-A70C-D76617660066%7D&file=Infiltration_rate_report_14May2025-Short-Version.docx&action=default&mobileredirect=true
| Proposed Updates to Equipment Power Densities and Building Schedules for the 2028 Energy Code, referred to as "Plug load and schedules project with CEC, 2025" (Docket Number =25-BSTD-03 & TN=265693) | https://efiling.energy.ca.gov/GetDocument.aspx?tn=265693&DocumentContentId=102545
Background Data [To be deleted prior to publication]
Dodge categories 1, 4, and 101
Store only

## Prototype
NORESCO, Updated October 2025
RetailGrocery
Characteristic | Value | Data Sources
Building Type | Grocery
Building Category | Nonresidential
Vintages | 4 Vintages: Pre-1978 , 1978-1997 ,1998-2007 , 2008-2018 New Construction (2019+) | Based on the vintage bin analysis _ Link | NonRes-Vintage bins-Draft Report-30Nov2023-Final.docx
Shape |  | PNNL Retail_Standalone
Total Floor Area (ft²) | 50,000 (250 ft x 200 ft) | PNNL Retail_Standalone
Aspect Ratio | 1.25 | Proposed Plan Based on Typical Grocery Store
Number of Floors | 1 | Proposed Plan Based on Typical Grocery Store
Roof type | Flat | Proposed Plan Based on Typical Grocery Store
WWR | 7.75% | Proposed Plan Based on Typical Grocery Store
Shading Geometry | N/A | Proposed Plan Based on Typical Grocery Store
Floor to floor height (feet) | N/A | Proposed Plan Based on Typical Grocery Store
Floor to ceiling height (feet) | 25 | CPUC (DEER 2023) Grocery prototype
Glazing sill height (feet) | 3 ft (top of the window is 10 ft high with 7 ft high glass) | CPUC (DEER 2023) Grocery prototype
Background Data [To be deleted prior to publication]
Existing Grocery Prototypes
CPUC: Retail_Grocery
Geometry/ Floor plan |  |  | Zones of DEER prototype | Floor area | Share
Total floor area (ft²) | 49997 |  | IndLoadDock | 2850.9 | 5.702%
|  |  | RefWalkInCool | 1559.65 | 3.119%
|  |  | RefWalkInFreeze | 812.23 | 1.625%
|  |  | RefFoodPrep | 1267.01 | 2.534%
|  |  | Grocery Sale | 40007.28 | 80.02%
|  |  | Office | 3499.89 | 7%
49996.96
Other Existing Retail Prototypes
Large size prototype
| CEC: Retail_Large | CPUC: Retail_Multistory Large (Rt3) | CPUC: Retail_Single-Story Large (RtL)
Geometry
Total floor area (ft²) | 240000 | 120000 | 130502
Medium size prototype
| CEC: Retail_Medium |  |  | PNNL : Retail_Standalone | PNNL: Retail_Stripmall
Geometry | zoning same as PNNL Stand alone with more skylight
Total floor area (ft²) | 24692 |  |  | 24692 | 22500
Small size prototype
| CEC: Retail_Stripmall (Mixed use) | CPUC: Retail_Small (RtS)
Geometry
Total floor area (ft²) | 9375 | 8001

## Zones
Proposed Layout - RetailGrocery | [12 empty] | Spaces and Zoning layout - "Rn" indicates which refrigerated cases are in each zone.
Space/Thermal Zone | Space Type | HVAC System Name/AHU Name | Schedule Category | Conditioned (Y/N) | Area Fraction | Area (ft²) | Volume (ft³) | Multipliers | Number of People | People (Persons/1,000 ft²) [T24, 2025,Table 120.1-A] | --- 40 ft --- | --- 70ft --- | N --- 34 ft --- | 250' North Façade | --- 106 ft ---
Checkout Area | Retail Sales Area (Grocery Sales) | SZVAV HP_Checkout Area_NC PSZAC_Checkout Area_Existing | Retail | Y | 20% | 10000 | 250000 | 1 | 170 | 17 | Back Office | Refr Food Prep | Walk-in Freezers | Loading Dock - Semi-Conditioned |  | 30 ft
Produce | Retail Sales Area (Grocery Sales) | SZVAV HP_Produce_NC PSZAC_Produce_Existing | Retail | Y | 8.8% | 4400 | 110000 | 1 | 74.8 | 17 | (1200 sf) | 2100 sf) | Walk-in Coolers | (stock area) | 3200 sf
General Merch | Retail Sales Area (Grocery Sales) | SZVAV HP_General Merch_NC PSZAC_General Merch_Existing | Retail | Y | 15.4% | 7700 | 192500 | 1 | 130.9 | 17 |  | 5000 sf (250'x20') | Meat and Dairy |  | R1, R2 | 20'
Frozen | Retail Sales Area (Grocery Sales) | SZVAV HP_Frozen_NC SPSZAC_Frozen_Existing | Retail | Y | 13.2% | 6600 | 165000 | 1 | 112.2 | 17
Beverage | Retail Sales Area (Grocery Sales) | SZVAV HP_Beverage_NC PSZAC_Beverage_Existing | Retail | Y | 8.8% | 4400 | 110000 | 1 | 74.8 | 17 | Produce | Grocery - General | Grocery - Frozen | Beverage | Bakery and Deli
Bakery and Deli | Retail Sales Area (Grocery Sales) | SZVAV HP_Bakery and Deli PSZAC_Bakery and Deli_Existing | Retail | Y | 8.8% | 4400 | 110000 | 1 | 74.8 | 17
Meat and Dairy | Retail Sales Area (Grocery Sales) | SZVAV HP_Meat and Dairy PSZAC_Meat and Dairy_Existing | Retail | Y | 10% | 5000 | 125000 | 1 | 85 | 17 | [5 empty] | 200' totalEastFacade
Back Office | Lounge, Breakroom, or Waiting Area | SZVAV HP_Back Office PSZAC_Back Office_Existing | Retail | Y | 2.4% | 1200 | 30000 | 1 | 6 | 5 | R4, R7 |  | R5 | R6, R9 | R3,R10
Loading Dock EL1 | Storage, Commercial/Industrial (Warehouse) | SZVAV HP_Loading Dock EL1 PSZAC_Loading Dock EL1_Existing | Retail | Y | 6.4% | 3200 | 80000 | 1 | 0 | 0 | 4400 sf | 7700 sf | 6600 sf | 4400 sf | 4400 sf | 110'
RefFoodPRep Core | Storage, Commercial/Industrial (Refrigerated) | SZVAV HP_RefFoodPRep Core PSZAC_RefFoodPRep Core_Existing | Retail | Y | 4.2% | 2100 | 52500 | 1 | 0 | 0 | (40'x110') | (70'x110') | (60'x110') | (40'x110') | (40'x110')
RefWalkInCool Core | Storage, Commercial/Industrial (Refrigerated) | - | Always On | Y | 1% | 500 | 12500 | 1 | 0 | 0
Ref WalkInFreezer Core | Storage, Commercial/Industrial (Refrigerated) | - | Always On | Y | 1% | 500 | 12500 | 1 | 0 | 0
Total (12 Thermal zones) | Total (4 Space Types) |  |  | Total (12 Conditioned zones) | 100% | 50000 | 1250000 |  | 728.5
[13 empty] | Cashier area and front of the store |  |  | 40'
10,000 sf (250'*40')
250' south façade
Background Data [To be deleted prior to publication]
Floorspace-Types-30Oct2024
Retail (CEUS 2022, statewide %)
Conditioned | Unconditioned |  |  | Ventilated | [6 empty] | Zoning based on ~50,000 sf prototype total floor area assumption. If different area desired, scale zone size accordingly.
82.62% | 17.37% |  |  | 0.8344
Assumed semi-heated storage
Fan Power: References
1. Equipment plan schedules for multiple retail / grocery stores. (Target)
2. Cross-Reference Summary (AI) Below:
For a rooftop heat pump (RTU) system serving a grocery store, the typical external static pressure (ESP) value depends on the ductwork design and the size of the unit. However, here are the standard industry ranges and a good rule of thumb for modeling or specification purposes:
🧰 Typical External Static Pressure Ranges
System Size | External Static Pressure (ESP)
5–10 tons | 0.5 to 1.0 inches w.g. (125–250 Pa)
10–20 tons | 1.0 to 2.0 inches w.g. (250–500 Pa)
20–50+ tons | 2.0 to 3.0 inches w.g. (500–750 Pa)
✅ Typical for Grocery Store RTUs:
A typical value used in grocery store design (especially when using EnergyPlus, Trane Trace, or Carrier HAP) is:
🔹 ESP = 2.0 inches w.g. (500 Pa)
This accommodates:
Long duct runs
Multiple branches/zones (e.g., deli, produce, checkout)
Filtration (e.g., MERV 8–13)
Return duct static loss
📚 References:
ASHRAE Handbook — HVAC Applications (Supermarkets)
Manufacturer Data (e.g., Carrier WeatherMaker, Trane Voyager, Lennox L Series)
ENERGY STAR RTU specifications
CEE Commercial HVAC Tier 2 performance criteria
| R1 | Open Multideck Dairy Case | Dairy Aisle | Medium Temp | 12' x 42" x 84" | 34–38
| R2 | Service Deli Case | Deli Counter | Medium Temp | 8' x 36" x 50" | 36–40
| R3 | Meat Self-Service Case | Meat Department | Medium Temp | 12' x 42" x 84" | 28–32
| R4 | Produce Case (Refrigerated) | Produce Aisle | Medium Temp | 8' x 42" x 84" | 36–40
| R5 | Frozen Food Upright Case | Frozen Foods Aisle | Low Temp | 12' x 36" x 84" | -5 to 0
| R6 | Ice Cream Low-Temp Case | Frozen Foods Aisle | Low Temp | 6' x 36" x 84" | -10 to -20
| R7 | Walk-In Cooler (Produce) | Back of House | Low Temp | 10' x 12' x 8' | 34–38
| R8 | Walk-In Freezer | Back of House | Low Temp | 10' x 10' x 8' | -10 to -20
| R9 | Beverage Case | Front of Store | Medium Temp | 8' x 36" x 84" | 34–38
| R10 | Grab-n-Go Sandwich Cooler | Front Grab-n-Go Area | Medium Temp | 6' x 30" x 60" | 36–40
N

## Envelope
Envelope - RetailGrocery
Element | Prototype | Assembly Type | Construction | Thermal Properties | Vintage | Selected T24 | Note | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
External Wall | RetailGrocery | Metal frame Wall | Metal frame + insulation + Gypsum board | U-factor IP | Pre 1978 | N/A | ASHRAE 90.1, 2022, Table A3.3.3.1, 3.5", R-0 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352
[5 empty] | 1978-1997 | 1986 | Package A with Heat Capacity 10.0-14.99 (Btu/F-ft²) - Still are lower than the next vintage! | 0.15083 | 0.15748 | 0.15748 | 0.14368 | 0.14368 | 0.21645 | 0.21645 | 0.21645 | 0.21645 | 0.21645 | 0.18622 | 0.18622 | 0.18622 | 0.15873 | 0.15873 | 0.15083
[5 empty] | 1998-2007 | 2001 | Table 1-H | 0.182 | 0.182 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.098 | 0.062 | 0.082 | 0.062 | 0.062 | 0.098 | 0.098 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.06 | 0.055 | 0.071 | 0.055 | 0.055 | 0.06 | 0.06 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055
Roof | RetailGrocery | Metal decking | Built-up roof: Roof membrane+ insulation+metal decking | U-factor IP | Pre 1978 | N/A | Considering 30 years for roof/ insulation replacement. | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 1978-1997 | 1992 |  | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 1998-2007 | 2001 | Table 1-H | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.049 | 0.039 | 0.039 | 0.039 | 0.049 | 0.075 | 0.067 | 0.067 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.047 | 0.047 | 0.047 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028
Window | RetailGrocery | Fixed windows | CBECS 2018 shows that ~ 50 % of retail that were built before 2000 are single pane | U-factor IP | Pre 1978 | N/A | ASHRAE Handbook of Fundamentals for single pane & T24, 2013 for double pane (50%-50%) | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74
[5 empty] | 1978-1997 | N/A |  | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74
|  |  | Double pane |  | 1998-2007 | 2001 | Table 1-H | 0.49 | 0.49 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.34 | 0.36 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.36
|  | Fixed windows | CBECS 2018 shows that ~ 50 % of retail that were built before 2000 are single pane | SHGC | Pre 1978 | N/A | ASHRAE Handbook of Fundamentals for single pane & T24, 2013 , for double pane (50%-50%) | 0.525 | 0.525 | 0.525 | 0.525 | 0.525 | 0.525 | 0.525 | 0.525 | 0.525 | 0.525 | 0.525 | 0.525 | 0.525 | 0.525 | 0.525 | 0.525
[5 empty] | 1978-1997 | N/A |  | 0.525 | 0.525 | 0.525 | 0.525 | 0.525 | 0.525 | 0.525 | 0.525 | 0.51 | 0.525 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.525
|  |  | Double pane |  | 1998-2007 | 2001 | Table 1-H (Non north 0-10%) | 0.49 | 0.47 | 0.61 | 0.61 | 0.61 | 0.61 | 0.61 | 0.61 | 0.61 | 0.47 | 0.47 | 0.47 | 0.47 | 0.46 | 0.46 | 0.49
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.22 | 0.25 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.25
Infiltration
[5 empty] | Vintage | I_75 (cfm/ft²) 6-sdied Infiltration rate @ 75 pa | Note | I-design (cfm/ft²) (4-sided Infiltration rate at normal pressure) (Design flow rate approach and Flow/Exterior Wall Area calculation method)
|  |  |  | Infiltration | Pre 1978 | 1.1 | 2022 CASE report (Table 38) | 0.67076
[5 empty] | 1978-1997 | 1.1 | 2022 CASE report (Table 38) | 0.67076
[5 empty] | 1998-2007 | 1.1 | 2022 CASE report (Table 38) | 0.67076
[5 empty] | 2008-2018 | 1 | 2022 CASE report (Table 38) & T24, part 6, 2008-2016 (Table 140.3-B), Dodge 2023 data | 0.60978
[5 empty] | 2019+ | 0.6 (barrier in all CZ) | 2022 CASE report (Table 38) & T24, part 6, 2025 (Table 140.3-B) | 0.36587
Source: T24 air barrier requirements (all editions) , the standardized infiltration rate reported in the 2022 CASE report, and Dodge 2023 data
Infiltration_rate_report_14May2025-Short-Version.docx
Background Data [To be deleted prior to publication]
Retail Standalone
in.comstock_building_type | Sum of calc.weighted.sqft | %
Mass | 150093118.8493 | 30.48%
SteelFramed | 200520458.7347 | 40.72%
WoodFramed | 141841314.0574 | 28.8%
Grand Total | 492454891.6415 | 100%
|  |  |  | 6 sided area | 122500
|  |  |  | 4 sided area | 22500
|  |  |  | Side multiplier | 5.4444

## HVAC System
HVAC system - RetailGrocery
Vintage | Heating | Cooling | Air Distribution | Source
Existing | PSZAC (furnace) | PSZAC (DX cooling) | PSZAC | CEUS 2022 | PTAC
New Construction | SZVAVHP | SZVAVHP | PSZVAVHP | Title 24, 2025, Engineering judgement
Efficiency of HVAC system (Efficiency is capacity-dependent. The following table provides a general estimate of system efficiency based on what we saw in the existing prototype runs, or assuming cooling load base on rule of thumbs)
Vintage | Upgrade/Installed year | Heating | Cooling | Source
Pre 1978 | 2008 | Thermal Efficiency of 80%; | EER 9 for <65 kBtu/h EER 10.3 for 65-135 kBtu/h EER 9.7 for 135-240 kBtu/h EER 9.5 for 240-760 kBtu/h | 2005 Title 20 Appliance Efficiency Regulations, 2005 T24 Standards, Tables 112-A, 112-B
1978-1997
1998-2007
2008-2018 | 2013 | Thermal Efficiency of 80%; | SEER 13, EER 11.2 for <65 kBtu/h EER 11.2 for 65-135 kBtu/h EER 11 for 135-240 kBtu/h EER 10 for 240-760 kBtu/h | 2013 Title 20 Appliance Efficiency Regulations, 2013 T24 Tables 112-A, 112-B
New Construction | 2025 | SEER 14 for <65 kBtu/h EER 11, COP fed min for 65-135 kBtu/h EER 10.6, COP fed min 135-240 kBtu/h EER 9.5 for >240 kBtu/h | EER 11 for <65 kBtu/h EER 11, COP fed min for 65-135 kBtu/h EER 10.6, COP fed min 135-240 kBtu/h EER 9.5 for >240 kBtu/h | Title 20 Appliance Efficiency Regulations (Tsble 18) , T24, 2025, Tables 110.2-A, 110.2-B
Fan Power
Vintage | Approach | System | Total Static Pressure (TSP) (in w.c.) | Fan Efficiency [ACM 2025] | Fan Motor and Drive Efficiency [ACM 2025, Table 13] | W/cfm [ACM 2025, Table 14 and 15] | Data Source
Existing | PNNL TSP | Zones should be sized so that design airflow is 10,000 cfm or less | 4.00 if VAV< 4,648 cfm 5.58 if VAV ≥ 4,648 cfm | 0.65 | ~0.9 (The full-load efficiency of the motor serving the fan- will be determined based on ACM 2025, Table 13) |  | ACM 2025, PNNL 2010 TSD
Brake horse power (bhp)=(Supply cfm*TSP in w.c.)/(6356*Fan efficiency)
Fan power (w/cfm) = bhp/motor and drive efficiency *746
New Construction | ACM 2025 | SZVAVHP System <= 10,000 cfm | 3.5887 | 0.65 | 0.9 | 0.72 | ACM 2025
* 0.9 is an average fan efficiency according to ACM 2025, Table 13
Fan total eff (E+ input) = 0.65 x Motor_eff
TSP (E+ input) in w.c. = Motor_eff/746 x (6356 x Fan_eff) x W/cfm
Fan_eff=0.65
Background Data [To be deleted prior to publication]
CEUS 2022 | Heating |  |  | Cooling |  | Air Distribution | Water Heater
| Floorspace Heated | Primary Heating | Fuel Type | Floorspace Cooled | Primary Cooling | Primary Air Dis | Fuel Type
|  | The default is the floorspace method unless otherwise specified |  |  | The default is the floorspace method unless otherwise specified | The default is the floorspace method unless otherwise specified
Retail | 79% | Package System / Heat Pump (80.2%) | Gas (58%) Elec ( 41%) | 80% | Package System / Heat Pump (80.2%) | Single Duct CAV (92.1%) | Elec (51%), Gas (34%)
ACM 2025

## Ventilation
Outdoor Airflow Rate - RetailGrocery
Space/Thermal Zone | Number of People | Floor Area (ft²) | cfm/person [T24, 2025, Equation 120.1-F and Table 120.1-A] | cfm/ft² [T24, 2025, Equation 120.1-F and Table 120.1-A] | Required Exhaust Rate [T24, 2025, Table 120.1-B – minimum exhaust rates] | Total cfm Driven by People | Total cfm Driven by Area | Total cfm Driven by Exhaust | Total cfm | Notes
Checkout Area | 170 | 10000 | 15 | 0.2 | 25/50 cfm/unit | 2550 | 2000 | 75 | 2550
Produce | 74.8 | 4400 | 15 | 0.2 | _ | 1122 | 880 | _ | 1122
General Merch | 130.9 | 7700 | 15 | 0.2 | _ | 1963.5 | 1540 | _ | 1963.5
Frozen | 112.2 | 6600 | 15 | 0.2 | _ | 1683 | 1320 | _ | 1683
Beverage | 74.8 | 4400 | 15 | 0.2 | _ | 1122 | 880 | _ | 1122
Bakery and Deli | 74.8 | 4400 | 15 | 0.2 | _ | 1122 | 880 | _ | 1122
Meat and Dairy | 85 | 5000 | 15 | 0.2 | _ | 1275 | 1000 | _ | 1275
Back Office | 6 | 1200 | 15 | 0.15 | _ | 90 | 180 | _ | 180
Loading Dock EL1 | 0 | 3200 | 15 | 0.15 | _ | 0 | 480 | _ | 480
RefFoodPRep Core | 0 | 2100 |  |  |  | 0 | 0 |  | 0
RefWalkInCool Core | 0 | 500 |  |  |  | 0 | 0 |  | 0
Ref WalkInFreezer Core | 0 | 500 |  | 0 | _ | 0 | 0 | _ | 0
Background Data [To be deleted prior to publication]
Currently assuming the entry is not actively ventilated due to doors (and connection to core) providing air.

## Thermostat
Thermostat Setpoints - RetailGrocery
Setpoint | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16 | Source
Produce Heating Setpoint (F) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | T24 2022 - Appendix 5.4B, [Retail]
Produce Heating Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Produce Cooling Setpoint (F) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
Produce Cooling Setback (F) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
Grocery - Frozen Heating Setpoint (F) | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | T24 2022 - Appendix 5.4B, [Retail]
Grocery - Frozen Heating Setback (F) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Grocery - Frozen Cooling Setpoint (F) | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78
Grocery - Frozen Cooling Setback (F) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
Storage Heating Setpoint (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | T24 2022 - Appendix 5.4B, [Retail]
Storage Heating Setback (F) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
Storage Cooling Setpoint (F) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
Storage Cooling Setback (F) | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90

## Water Heater
Water Heater Summary - RetailGrocery
Vintage | WH Type | Efficiency | Tank Volume (gal) | Tank Loss | Unit | Source
Existing | Electric | 1 | 52.236 | 0.81688 | % hr | Loss per hour, 10 CFR 431.110(a) Table F-4
New Construction | Electric | 1 | 52.236 | 0.81688 | % hr
Peak Hot Water Consumption
Space Name | Baseline WH Type [CEUS 2022] | Total Area (ft²) | Number of People | Hot Water Usage Specification (gal/hr per person) [T24, 2022, Appendix 5.4A , sheet: "2022 SpaceFuncData-Input"] | Peak Hot Water Usage (gal/hr) | Peak Hot Water Usage (gal/min)
Checkout Area | Electric resistance WH | 10000 | 170 | 0.18 | 30.6 | 0.51
Produce | Electric resistance WH | 4400 | 74.8 | 0.18 | 13.464 | 0.2244
General Merch | Electric resistance WH | 7700 | 130.9 | 0.18 | 23.562 | 0.3927
Frozen | Electric resistance WH | 6600 | 112.2 | 0.18 | 20.196 | 0.3366
Beverage | Electric resistance WH | 4400 | 74.8 | 0.18 | 13.464 | 0.2244
Bakery and Deli | Electric resistance WH | 4400 | 74.8 | 0.18 | 13.464 | 0.2244
Meat and Dairy | Electric resistance WH | 5000 | 85 | 0.18 | 15.3 | 0.255
Back Office | Electric resistance WH | 1200 | 6 | 0.09 | 0.54 | 0.009
Loading Dock EL1 | Electric resistance WH | 3200 | 0 | 0.18 | 0 | 0
RefFoodPRep Core | Electric resistance WH | 2100 | 0 | 0.18 | 0 | 0
RefWalkInCool Core | Electric resistance WH | 500 | 0 | 0.18 | 0 | 0
Ref WalkInFreezer Core | Electric resistance WH | 500 | 0 | 0.18 | 0 | 0
Total (12 Thermal zones) | Electric resistance WH | 50000 | 728.5 | 0 | 130.59 | 2.1765
Water Heater Capacity, Tank Capacity, and Tank Loss
WH Type | Peak Hot Water Usage (gal/hr) | Heat Output (Btu/hr) [ACM, 2025, 5.9.2: Rated capacity section] | WH Capacity (Btu/hr) [ACM, 2025, 5.9.2: Rated capacity section] | Required Energy Input (Btu/hr) | Storage Volume (gal) | Standby Loss | Unit | Off/On Cycle Loss Coefficient to Ambient Temp (Btu/h-F) | Source
Electric resistance WH | 130.59 | 86583.2594 | 51949.9557 | 51949.9557 | 52.236 | 0.81688 | %hr | 3.5587
Total | 130.59 | 86583.2594 | 51949.9557 | 51949.9557 | 52.236 | 0.81688
Design supply temperature (F) | 135 | Ref: T24 2022 - Appendix 5.4B
Cold Water supply temperature (F) | 55 | Ref: ACM, 2025, 5.9.2: Rated capacity section
WH system factor | 0.6 | Ref: ACM, 2025, 5.9.2: Rated capacity section
Reheat multiplier | 0.4
* The 0.40 multiplier is a storage sizing factor used to account for the fact that the water heater doesn't need to store the full peak hour demand—it can reheat water during that time. This factor assumes that the heater will recover part of the hot water used during the peak hour, so only 40% of the peak hour demand needs to be stored at any given moment.
**For Gas Water Heater: UA(Btu/h-°F)​=Q˙​SL​ (Btu/h)/ΔT (∘F)​
Ambient temp | 68
Delta T | 67
** For Electric Water Heater: UA(Btu/h-°F)​= 0.0834 *SL​ (%/hr)*V gal
Background Data [To be deleted prior to publication]
Fuel should match HVAC decision for new construction.

## Interior Lights
Interior Lighting - RetailGrocery
Space Type | New Construction |  |  | Existing
| LPD (W/ft²) | Additional LPD for Portable Lighting (W/ft²) | Source | LPD (W/ft²) | Additional LPD for Portable Lighting (W/ft²) | Source
Retail Sales Area (Grocery Sales) | 1 |  | T24, part 6, 2025, Table 140.6-C (Area category method) | 1.2 |  | T24, part 6, 2016, Table 140.6-C (Area category method) LPD of "All other spaces" is considered for Back_Space
Lounge, Breakroom, or Waiting Area | 0.55 |  |  | 0.9
Storage, Commercial/Industrial (Warehouse) | 0.4 |  |  | 0.6
Storage, Commercial/Industrial (Refrigerated) | 0.4 |  |  | 0.7
Storage (General) | 0.4 |  |  | 0.6
Background Data [To be deleted prior to publication]
2016
All other area=0.5
Commercial and Industrial Storage Areas (conditioned and unconditioned)=0.6

## Equipment
Equipment - RetailGrocery
Space Type | Plug Load Power Density (W/ft²) | Source | Note
Retail Sales Area (Grocery Sales) | 0.4 | Plug load and schedules project with CEC, 2025 T24 2022 - Appendix 5.4A: Space Use Data-T24N-2022 | Matches Retail/All Other; PNNL prototype =~0.7; T24 Appendix 5.4A =0.2
Lounge, Breakroom, or Waiting Area | 1
Storage, Commercial/Industrial (Warehouse) | 0.2
Storage, Commercial/Industrial (Refrigerated) | 0.2
Storage (General) | 0.2
Refrigeration Equipment
Tag | Equipment Type | Location | Duty / Type | Dimensions (LxDxH) | Temp Range (°F) | Refrigerant | Compressor Type | Lighting | Defrost Type | Rated Power | Defrost Power | Notes
R1 | Open Multideck Dairy Case | Dairy Aisle | Medium Temp | 12' x 42" x 84" | 34–38 | R-448A | Remote | LED canopy/shelves | Off-cycle | 3500 |  | Glass end panels, night curtain
R2 | Service Deli Case | Deli Counter | Medium Temp | 8' x 36" x 50" | 36–40 | R-448A | Remote | LED top light | Off-cycle | 2000 |  | Dual temp option for meats/cheeses
R3 | Meat Self-Service Case | Meat Department | Medium Temp | 12' x 42" x 84" | 28–32 | R-448A | Remote | LED lighting | Off-cycle | 3800 |  | Gravity coil, low temp
R4 | Produce Case (Refrigerated) | Produce Aisle | Medium Temp | 8' x 42" x 84" | 36–40 | R-448A | Remote | LED canopy light | Off-cycle | 2500 |  | Mist system optional
R5 | Frozen Food Upright Case | Frozen Foods Aisle | Low Temp | 12' x 36" x 84" | -5 to 0 | R-448A | Remote | LED door lighting | Electric | 4200 | 400 | Glass doors, anti-sweat heaters
R6 | Ice Cream Low-Temp Case | Frozen Foods Aisle | Low Temp | 6' x 36" x 84" | -10 to -20 | R-448A or CO₂ | Remote | LED lighting | Electric | 4500 | 450 | Critical temp holding, tight door seals
R7 | Walk-In Cooler (Produce) | Back of House | Low Temp | 10' x 12' x 8' | 34–38 | R-448A | Remote condensing unit | LED ceiling | Off-cycle | 2800 |  | Floorless, strip curtain at door
R8 | Walk-In Freezer | Back of House | Low Temp | 10' x 10' x 8' | -10 to -20 | R-448A | Remote condensing unit | LED ceiling | Electric | 4800 |  | Insulated floor, heated door frame
R9 | Beverage Case | Front of Store | Medium Temp | 8' x 36" x 84" | 34–38 | R-448A | Remote | LED shelves | Off-cycle | 2200 |  | Reach-in with glass doors
R10 | Grab-n-Go Sandwich Cooler | Front Grab-n-Go Area | Medium Temp | 6' x 30" x 60" | 36–40 | R-448A | Self-contained | LED canopy | Off-cycle | 1500 |  | Plug-in, casters for mobility
Condenser and Compressor Rack
Tag | Service | Rated Power | Condensing Temp (deg C) | Subcooling Delta (deg C) | Fan Power (W/W) | Notes
C1 | Medium Temp | 35000 | 35 | 25 | 0.1 | Condenser and Compressor Rack
C2 | Low Temp | 28000 | 30 | 25 | 0.1 | Condenser and Compressor Rack
Background Data [To be deleted prior to publication]
[5 empty] | ~W PNNL | ft² | W/ft² PNNL | W/ft² CEC
|  |  |  | BACK_SPACE | 3000 | 4089.1018 | 0.73366 | 0.2
|  |  |  | CORE_RETAIL | 5000 | 17227.4227 | 0.29023 | 0.4
|  |  |  | POINT_OF_SALE | 3000 | 1623.3053 | 1.8481 | 0.4
|  |  |  | FRONT_RETAIL | 500 | 1623.3053 | 0.30801 | 0.4
it is reasonable to leave the current 5.0 W/ft² assumption in the NMACM for refrigeration loads in Grocery Sales area

## Schedules
Schedules - RetailGrocery
Zone | Schedule Category | Schedule | Source | Type | Hour
[5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
All the zones | Retail | Occupancy | T24 2022 - Appendix 5.4B | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0
All the zones | Retail | Lights | T24 2022 - Appendix 5.4B | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.55 | 0.55 | 0.5 | 0.2 | 0.05 | 0.05
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.55 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.4 | 0.4 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
All the zones | Retail | ElecEquipment | Plug load and schedules project with CEC, 2025 | Weekday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.4 | 0.4 | 0.4
|  |  |  | Saturday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.4 | 0.4
|  |  |  | Sunday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
All the zones | Retail | HVACAvail | T24 2022 - Appendix 5.4B, [Retail] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
All the zones | Retail | ServiceHotWater | T24 2022 - Appendix 5.4B, [Retail] | Weekday | 0.04 | 0.05 | 0.05 | 0.04 | 0.04 | 0.04 | 0.04 | 0.15 | 0.23 | 0.32 | 0.41 | 0.57 | 0.62 | 0.61 | 0.5 | 0.45 | 0.46 | 0.47 | 0.42 | 0.34 | 0.33 | 0.23 | 0.13 | 0.08
|  |  |  | Saturday | 0.11 | 0.1 | 0.08 | 0.06 | 0.06 | 0.06 | 0.07 | 0.2 | 0.24 | 0.27 | 0.42 | 0.54 | 0.59 | 0.6 | 0.49 | 0.48 | 0.47 | 0.46 | 0.44 | 0.36 | 0.29 | 0.22 | 0.16 | 0.13
|  |  |  | Sunday | 0.07 | 0.07 | 0.07 | 0.06 | 0.06 | 0.06 | 0.07 | 0.1 | 0.12 | 0.14 | 0.29 | 0.31 | 0.36 | 0.36 | 0.34 | 0.35 | 0.37 | 0.34 | 0.25 | 0.27 | 0.21 | 0.16 | 0.1 | 0.06
All the zones | Retail | Infiltration | T24 2022 - Appendix 5.4B, [Retail] | Weekday | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1
|  |  |  | Saturday | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1
|  |  |  | Sunday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1
All the zones | Retail | Refrigeration | T24 2022 - Appendix 5.4B, [Retail] | Weekday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Saturday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Sunday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
All the zones | Retail | HtgSetpt | T24 2022 - Appendix 5.4B, [Retail] | Weekday | 60 | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 60 | 60 | 60
|  |  |  | Saturday | 60 | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 60 | 60
|  |  |  | Sunday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 60 | 60 | 60 | 60 | 60
All the zones | Retail | ClgSetpt | T24 2022 - Appendix 5.4B, [Retail] | Weekday | 85 | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 85 | 85 | 85
|  |  |  | Saturday | 85 | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 85 | 85
|  |  |  | Sunday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 85 | 85 | 85 | 85 | 85
Zones with Refrigeration systems | Retail | Defrost |  | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | Note: The defrost cycle runs for 20 minutes, followed by a roughly 10-minute drip-down period during which the system remains off to allow residual meltwater to drain from the coils into the pan.
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
Zones with Refrigeration systems | Retail | DefrostDripDown | ` | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
Zones with Refrigeration systems | Retail | CaseRestock |  | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zones with Refrigeration systems | Retail | CaseCredit |  | Weekday | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.2 | 0.2 | 0.2
|  |  |  | Saturday | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.2 | 0.2 | 0.2
|  |  |  | Sunday | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.2 | 0.2 | 0.2
Other
| Building | ExtLightingNonMotionCtrl |  | Weekday | bar: Hour 1 to Hour 24
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
| Building | ExtLightingMotionCtrl |  | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Retails | Building | RetailSalePeopleActivityLevel | Based on Activilty level schedules in CEC Prototypes | Weekday | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
|  |  |  | Saturday | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
|  |  |  | Sunday | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
Back Office | Building | CommonAreaPeopleActivityLevel | Based on Activilty level schedules in CEC Prototypes | Weekday | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5
|  |  |  | Saturday | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5
|  |  |  | Sunday | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5
RefFoodPRep Core, RefWalkInCool Core, Ref WalkInFreezer Core | Building | RefStoragePeopleActivityLevel | Based on Activilty level schedules in CEC Prototypes | Weekday | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8
|  |  |  | Saturday | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8
|  |  |  | Sunday | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8
Loading Dock EL1 | Building | SaleStoragePeopleActivityLevel | Based on Activilty level schedules in CEC Prototypes | Weekday | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8
|  |  |  | Saturday | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8
|  |  |  | Sunday | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8
Background Data [To be deleted prior to publication]

## Ext Lighting
Exterior Lighting - RetailGrocery
Motion Controlled Luminaires (W) | Non-motion Controlled Luminaires (W) | Total (W) | Source
3680.5556 | 1160 | 4840.5556 | T24, 2022
Exterior Lighting
Items (Assume LZ2) | Assumptions [2019 Outdoor Lighting CASE Report & PNNL 90.1-2010 TSD] |  | Unit | Lighting Power Allowance [T24, 2025, Table 140.7-A & 140.7-B] | Unit | Exterior lighting power (w)
IWA (Initial Wattage Allowance) |  |  |  | 200 | W | 200
Parking area | 400 ft² for every parking space 1 parking space per 360 ft² of gross building area | 55555.5556 | (ft²) | 0.019 | (W/ft²) | 1055.5556
Building Entrance | 1 per 10,000sf footprint | 5 | (count) | 15 | (W/ea) | 75
Hardscape Ornamental Light | 0.1 ft² per 1 ft² of gross bldg area for hardscape ornamental light | 5000 | (ft²) | 0.007 | (W/ft²) | 35
Building façade | 0.1 W per 1 ft² of facade area Façade Area = Perimeter × 0.5 × 25 ft The 0.5 factor assumes that only half of the perimeter walls are lit. -Formula ia developed based on the 2019 Outdoor Lighting CASE report | 11250 | (ft²) | 0.1 | (W/ft²) | 1125
Sales canopy | 0.1 ft² per ft² of gross bldg area | 5000 | (ft²) | 0.47 | (W/ft²) | 2350
Motion controlled Luminaires | [5 empty] | 3680.5556
Non-motion-controlled Luminaires | [5 empty] | 1160
Total | [5 empty] | 4840.5556
*Developed based on 2019 Outdoor Lighting CASE Report
Perimeter | 900
Total floor area | 50000
Floors | 1
Background Data [To be deleted prior to publication]

## Energy Usage
CalBEM Energy Consumption - RetailGrocery | [7 empty] | National Average (EnergyStar Portfolio Manager) |  |  |  |  | CEUS Energy Consumption - Retail
Prototype | CZ | CalBEM Electricity EUI (KBTU/ft²) | CalBEM Gas EUI (KBTU/ft²) | CalBEM Total EUI (KBTU/ft²) | New Construction Electricity EUI (KBTU/ft²) | New Construction Gas EUI (KBTU/ft²) | New Construction Total EUI (KBTU/ft²) | National Average | Acceptable eRange (25% Higher) | Acceptable Range (25% Lower) | National Average Acceptable Range | Zip code | Prototype | CZ | Total Floorspace (Thousand of ft²) | CEUS 2022 Electric Energy Intensity (kWh/ft²) | CEUS 2022 Annual Gas Intensity (kWh/ft²) | CEUS 2022 Total EUI (kBtu/ft²) | Acceptable Range (25% Higher) | Acceptable Range (25% Lower) | CEUS 2022 Acceptable Range
HotelSmall | 1 | 36.3 | 46.3 | 82.5 | 50.2 | 0 | 50.2 | 58.5 | 73.125 | 43.875 | 29.25 | 95519 | Retail | 1 | 13814 | 11.1 | 3.06 | 48.3139 | 60.3924 | 36.2354 | 24.157
| 2 | 40.5 | 31.7 | 72.2 | 47.8 | 0 | 47.8 | 68.9 | 86.125 | 51.675 | 34.45 | 95403 |  | 2 | 25239 | 7.8 | 4.35 | 41.4558 | 51.8197 | 31.0918 | 20.7279
| 3 | 36.2 | 25.5 | 61.7 | 43.1 | 0 | 43.1 | 63.5 | 79.375 | 47.625 | 31.75 | 94621 |  | 3 | 88648 | 10.2 | 3.48 | 46.6762 | 58.3452 | 35.0071 | 23.3381
| 4 | 45.6 | 22.5 | 68.1 | 49.8 | 0 | 49.8 | 71.2 | 89 | 53.4 | 35.6 | 93446 |  | 4 | 44551 | 10.4 | 3.38 | 47.0174 | 58.7717 | 35.263 | 23.5087
| 5 | 33.8 | 14.5 | 48.3 | 42.4 | 0 | 42.4 | 61.8 | 77.25 | 46.35 | 30.9 | 93455 |  | 5 | 9847 | 9.3 | 4.28 | 46.335 | 57.9187 | 34.7512 | 23.1675
| 6 | 36.1 | 7.8 | 43.9 | 39.2 | 0 | 39.2 | 68.4 | 85.5 | 51.3 | 34.2 | 90045 |  | 6 | 92562 | 8.6 | 1.35 | 33.9494 | 42.4367 | 25.462 | 16.9747
| 7 | 35.2 | 6 | 41.2 | 38.1 | 0 | 38.1 | 68.4 | 85.5 | 51.3 | 34.2 | 92101 |  | 7 | 63471 | 10.3 | 0.93 | 38.3168 | 47.8959 | 28.7376 | 19.1584
| 8 | 43.4 | 8.2 | 51.6 | 45.8 | 0 | 45.8 | 69.4 | 86.75 | 52.05 | 34.7 | 92832 |  | 8 | 147354 | 8.5 | 1.31 | 33.4717 | 41.8396 | 25.1038 | 16.7359
| 9 | 44.9 | 11.1 | 56 | 46.3 | 0 | 46.3 | 70.1 | 87.625 | 52.575 | 35.05 | 91505 |  | 9 | 212697 | 9.4 | 1.4 | 36.8496 | 46.062 | 27.6372 | 18.4248
| 10 | 46.2 | 10.3 | 56.5 | 48.6 | 0 | 48.6 | 70.6 | 88.25 | 52.95 | 35.3 | 92501 |  | 10 | 149832 | 9.3 | 1.54 | 36.9861 | 46.2326 | 27.7396 | 18.493
| 11 | 45.9 | 33.9 | 79.7 | 57.5 | 0 | 57.5 | 72.5 | 90.625 | 54.375 | 36.25 | 96080 |  | 11 | 45934 | 10.6 | 2.72 | 45.4478 | 56.8098 | 34.0859 | 22.7239
| 12 | 42.1 | 28.9 | 71 | 51 | 0 | 51 | 71.6 | 89.5 | 53.7 | 35.8 | 95822 |  | 12 | 195816 | 11 | 2.87 | 47.3244 | 59.1556 | 35.4933 | 23.6622
| 13 | 47.3 | 22.3 | 69.6 | 56.8 | 0 | 56.8 | 72.5 | 90.625 | 54.375 | 36.25 | 93727 |  | 13 | 67122 | 12.4 | 2.61 | 51.2141 | 64.0177 | 38.4106 | 25.6071
| 14 | 53.1 | 26.9 | 80 | 60.8 | 0 | 60.8 | 72.8 | 91 | 54.6 | 36.4 | 93550 |  | 14 | 39049 | 8.6 | 1.28 | 33.7106 | 42.1382 | 25.2829 | 16.8553
| 15 | 62.9 | 7 | 69.9 | 66 | 0 | 66 | 70.5 | 88.125 | 52.875 | 35.25 | 92262 |  | 15 | 73160 | 10 | 2.42 | 42.377 | 52.9713 | 31.7828 | 21.1885
| 16 | 49.3 | 58.4 | 107.7 | 69.4 | 0 | 69.4 | 71.5 | 89.375 | 53.625 | 35.75 | 95726 |  | 16 | 149464 | 9.6 | 1.56 | 38.0779 | 47.5974 | 28.5584 | 19.039
Ref: CEUS 2022 Report
And converted FZ level data to CZ level
CEUS has only one category for all the retails
Background Data [To be deleted prior to publication]
Using Supermarket/Grocery Store use type
[7 empty] | Alternative One | 130 | Alternative Two | 68.7
[8 empty] | 139 |  | 80.3
[8 empty] | 135 |  | 74.2
[8 empty] | 141.5 |  | 82.8
[8 empty] | 133.6 |  | 72.3
[8 empty] | 139.1 |  | 79.7 |  |  |  |  | CEUS 2022 Electric Energy Intensity (kWh/ft²) | CEUS 2022 Annual Gas Intensity (kWh/ft²)
[8 empty] | 139.1 |  | 79.7 |  |  |  |  | Food Store
[8 empty] | 139.9 |  | 80.8 |  |  |  |  | Electricity Usage (kWh/SqF) | Gas Usage (kWh/SqF)
[8 empty] | 140.4 |  | 81.5 |  |  |  |  | 40.9 | 16.31 |  | 195.2005
[8 empty] | 140.9 |  | 82.1 |  |  |  |  | 39.8 | 13.63
[8 empty] | 142.5 |  | 84.2 |  |  |  |  | 38 | 13.46
[8 empty] | 141.7 |  | 83.2 |  |  |  |  | 37.6 | 13.59
[8 empty] | 142.4 |  | 84.2 |  |  |  |  | 41.2 | 12.4
[8 empty] | 142.7 |  | 84.5 |  |  |  |  | 33.4 | 15.7
[8 empty] | 140.8 |  | 82 |  |  |  |  | 39.4 | 17.66
[8 empty] | 141.6 |  | 83.1 |  |  |  |  | 34.7 | 16.15
[15 empty] | 33.2 | 12.45
[15 empty] | 38.8 | 27.69
[8 empty] | CA Climate Zone | Climate Character (short) | HDD vs CDD Balance | HVAC Dominance |  |  |  | 39.1 | 15.49
[8 empty] | CZ 1 | Cool coastal / marine | HDD ≫ CDD | Heating-dominated |  |  |  | 38.9 | 15.11
[8 empty] | CZ 2 | Coastal, slightly inland | HDD > CDD | Heating-leaning |  |  |  | 40 | 18.25
[8 empty] | CZ 3 | Mild coastal | HDD > CDD | Heating-leaning |  |  |  | 36.4 | 29.45
[8 empty] | CZ 4 | Mild coastal / near inland | HDD ≈ CDD (low total) | Balanced (slight heating) |  |  |  | 39 | 21.06
[8 empty] | CZ 5 | Mildest CA climate | HDD ≈ CDD (low both) | Balanced |  |  |  | 39.4 | 30.04
[8 empty] | CZ 6 | Southern coastal | CDD > HDD | Cooling-leaning
[8 empty] | CZ 7 | Inland SoCal | CDD > HDD | Cooling-dominated
[8 empty] | CZ 8 | Inland SoCal (hotter) | CDD ≫ HDD | Cooling-dominated
[8 empty] | CZ 9 | LA Basin / inland | CDD ≫ HDD | Cooling-dominated
[8 empty] | CZ 10 | Inland valleys | CDD ≫ HDD | Cooling-dominated
[8 empty] | CZ 11 | Inland north / foothills | HDD > CDD | Heating-dominated
[8 empty] | CZ 12 | Inland north (milder) | HDD > CDD | Heating-leaning
[8 empty] | CZ 13 | Central Valley | HDD ≈ CDD (both high) | Mixed (high energy)
[8 empty] | CZ 14 | Desert | CDD ≫≫ HDD | Strongly cooling-dominated
[8 empty] | CZ 15 | Hot desert | CDD ≫≫ HDD | Extremely cooling-dominated
[8 empty] | CZ 16 | Extreme desert | CDD ≫≫≫ HDD | Extreme cooling-dominated

## Weights
% of Floor Area per CZ and Vintage Bin - Retail | [7 empty] | % of Floor Area per CZ and Vintage Bin - Retail
Prototype | CZ | Vintage Bin | [5 empty] | Prototype | Vintage Bin | CZ
|  | Pre-1978 | 1978-1997 | 1998-2007 | 2008-2018 | Not available |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
Retail | 1 | 31.2% | 28.3% | 16.2% | 8.6% | 15.7% | 100% | Retail | Pre-1978 | 1.032% | 2.937% | 8.47% | 4.478% | 0.5123% | 9.245% | 3.959% | 15.15% | 22.77% | 4.38% | 2.941% | 12.32% | 3.411% | 1.762% | 2.238% | 4.382% | 100%
| 2 | 48.6% | 29.2% | 6.8% | 2.6% | 12.8% | 100% |  | 1978-1997 | 0.9654% | 1.82% | 4.898% | 2.391% | 0.6523% | 6.121% | 6.717% | 8.877% | 13.6% | 12.82% | 2.873% | 13.56% | 4.426% | 2.92% | 5.583% | 11.78% | 100%
| 3 | 40% | 22.4% | 14.3% | 9.4% | 14% | 100.1% |  | 1998-2007 | 0.8936% | 0.6854% | 5.065% | 2.378% | 0.8837% | 5.233% | 3.57% | 8.596% | 13.11% | 10.33% | 3.788% | 18.44% | 7.631% | 2.796% | 5.919% | 10.69% | 100%
| 4 | 42% | 21.7% | 13.4% | 10.1% | 12.8% | 100% |  | 2008-2018 | 0.698% | 0.3836% | 4.893% | 2.637% | 0.261% | 2.686% | 1.16% | 4.394% | 4.996% | 21.7% | 2.94% | 10.57% | 3.94% | 5.328% | 9.302% | 24.11% | 100%
| 5 | 21.8% | 26.8% | 22.5% | 4.5% | 24.5% | 100.1% |  | Not available | 1.237% | 1.838% | 7.068% | 3.252% | 1.373% | 6.534% | 5.026% | 10.87% | 12.04% | 9.643% | 4.293% | 14.42% | 5.217% | 2.174% | 6.037% | 8.982% | 100%
| 6 | 41.8% | 26.8% | 14.2% | 4.9% | 12.4% | 100.1% |  | Total | 0.9739% | 1.779% | 6.248% | 3.14% | 0.6942% | 6.525% | 4.474% | 10.39% | 14.99% | 10.56% | 3.238% | 13.8% | 4.732% | 2.753% | 5.158% | 10.54% | 100%
| 7 | 26.1% | 42.8% | 14.1% | 3.1% | 13.9% | 100%
| 8 | 43% | 24.4% | 14.6% | 5.1% | 12.9% | 100%
| 9 | 44.8% | 25.9% | 15.4% | 4% | 9.9% | 100%
| 10 | 12.2% | 34.6% | 17.2% | 24.6% | 11.3% | 99.9%
| 11 | 26.8% | 25.3% | 20.6% | 10.9% | 16.4% | 100%
| 12 | 26.3% | 28% | 23.6% | 9.2% | 12.9% | 100%
| 13 | 21.2% | 26.7% | 28.5% | 10% | 13.6% | 100%
| 14 | 18.9% | 30.3% | 17.9% | 23.2% | 9.8% | 100.1%
| 15 | 12.8% | 30.9% | 20.2% | 21.6% | 14.5% | 100%
| 16 | 12.3% | 31.9% | 17.9% | 27.4% | 10.5% | 100%
| Statewide | 32.9% | 28% | 17.2% | 9.7% | 12.1% | 99.9%
Ref: CEUS 2022 dataset
And converted FZ level data to CZ level
CEUS has only one category for all the retails
Background Data [To be deleted prior to publication]

## PV (hidden)
PV - RetailGrocery
TBD

## EV Charger (hidden)
EV Charger - RetailGrocery
TBD
Background Data [To be deleted prior to publication]

## Data (hidden)
Space Function | Electric Equipment Load Intensity | Electric Equipment Load Intensity | LPD
Aging Eye/Low-vision (Corridor Area) |  |  | 2013 | 2016 | 2019 | 2025
Aging Eye/Low-vision (Dining)
Aging Eye/Low-vision (Lobby, Main Entry)
Aging Eye/Low-vision (Lounge/Waiting Area)
Aging Eye/Low-vision (Multipurpose Room)
Aging Eye/Low-vision (Religious Worship Area)
Aging Eye/Low-vision (Restroom)
Aging Eye/Low-vision (Stairwell)
Audience Seating Area
Auditorium Area
Auto Repair / Maintenance Area
Barber, Beauty Salon, Spa Area
Civic Meeting Place Area
Classroom, Lecture, Training, Vocational Areas
Concourse and Atria Area
Convention, Conference, Multipurpose and Meeting Area
Copy Room
Corridor Area
Dining Area (Bar/Lounge and Fine Dining)
Dining Area (Cafeteria/Fast Food)
Dining Area (Family and Leisure)
Electrical, Mechanical, Telephone Rooms
Exercise/Fitness Center and Gymnasium Areas
Financial Transaction Area
Healthcare Facility and Hospitals (Exam/Treatment Room)
Healthcare Facility and Hospitals (Imaging Room)
Healthcare Facility and Hospitals (Medical Supply Room)
Healthcare Facility and Hospitals (Nursery)
Healthcare Facility and Hospitals (Nurse's Station)
Healthcare Facility and Hospitals (Operating Room)
Healthcare Facility and Hospitals (Patient Room)
Healthcare Facility and Hospitals (Physical Therapy Room)
Healthcare Facility and Hospitals (Recovery Room)
Hotel Function Area
Kitchen/Food Preparation Area
Kitchenette or Residential Kitchen
Laboratory, Scientific
Laundry Area
Library (Reading Area)
Library (Stacks Area)
Lobby, Main Entry
Locker Room
Lounge, Breakroom, or Waiting Area
Manufacturing, Commercial & Industrial Work Area (Low Bay)
Manufacturing, Commercial & Industrial Work Area (High Bay)
Manufacturing, Commercial & Industrial Work Area (Precision)
Museum Area (Exhibition/Display)
Museum Area (Restoration Room)
Office Area (>250 square feet)
Office Area (<250 square feet)
Parking Garage Area (Parking Zone and Ramps)
Parking Garage Area (Daylight Adaptation Zones)
Pharmacy Area
Retail Sales Area (Grocery Sales)
Retail Sales Area (Retail Merchandise Sales)
Retail Sales Area (Fitting Room)
Religious Worship Area
Restrooms
Stairwell
Storage, Commercial/Industrial (Warehouse)
Storage, Commercial/Industrial (Refrigerated)
Storage, Commercial/Industrial (Shipping & Handling)
Storage (General)
Sports Arena - Playing Area (> 5,000 Spectators)
Sports Arena - Playing Area (2,000 - 5,000 Spectators)
Sports Arena - Playing Area (< 2,000 Spectators)
Sports Arena - Playing Area (Recreational)
Theater Area (Motion Picture)
Theater Area (Performance)
Transportation Function (Baggage Area)
Transportation Function (Ticketing Area)
Videoconferencing Studio
High-Rise Residential Living Spaces
Hotel/Motel Guest Room
All other
Attic
Reception Area
Elevator
Plenum
IT Room (EPD 12)
Computer Room (EPD 20)
Server Room (EPD 45)