## Notes
Data Sources
Dataset | Dodge 2023
| CEUS 2022 | https://www.energy.ca.gov/publications/2023/2022-california-commercial-end-use-survey-ceus-final-report
| CBECS 2018 | https://www.eia.gov/consumption/commercial/data/2018/index.php?view=microdata
| ComStock 2023 | https://data.openei.org/s3_viewer?bucket=oedi-data-lake&prefix=nrel-pds-building-stock%2Fend-use-load-profiles-for-us-building-stock%2F2023%2Fcomstock_amy2018_release_2%2Fmetadata_and_annual_results%2Fby_state%2Fstate%3DCA%2F
Prototype | CEC prototypes (CBECC 2022.3.1) | https://bees.noresco.com/software2022.html
| PNNL prototypes (90.1-2022) | https://www.energycodes.gov/prototype-building-models#Commercial
| DEER prototypes (June 2023) | https://github.com/sound-data/DEER-Prototypes-EnergyPlus
Codes | Title 24, part 6 , referred to as T24 (1984, 1992, 2001, 2007, 2013, 2022, 2025)
ASHRAE 90.1 (2022)
| CFR Title 10 (2010, 2024) | https://www.ecfr.gov/current/title-10/chapter-II/subchapter-D/part-431/subpart-D
Others | ACM (2022)
| T24 2022 - Appendix 5.4A and Appendix 5.4B | https://www.energy.ca.gov/publications/2022/2022-nonresidential-and-multifamily-alternative-calculation-method-reference
| 2022 Reduced infiltration CASE report | https://title24stakeholders.com/wp-content/uploads/2020/10/2022-T24-Final-CASE-Report_Reduce-Infiltration.pdf
| 2019 Outdoor Lighting CASE Report | https://title24stakeholders.com/wp-content/uploads/2016/10/T24-2019-CASE-Study-Results-Report-Outdoor-Sources_Final_with-Attachments.pdf
| PNNL 20405, 2010 | https://www.pnnl.gov/main/publications/external/technical_reports/PNNL-20405.pdf
| Air leakage Memo, NORESCO, 2025 | https://2050partners.sharepoint.com/:w:/r/sites/CalBEMCollaborativeEfforts/_layouts/15/Doc.aspx?sourcedoc=%7B3BEF8F74-7FAC-44F2-A70C-D76617660066%7D&file=Infiltration_rate_report_14May2025-Short-Version.docx&action=default&mobileredirect=true
| Proposed Updates to Equipment Power Densities and Building Schedules for the 2028 Energy Code, referred to as "Plug load and schedules project with CEC, 2025" (Docket Number =25-BSTD-03 & TN=265693) | https://efiling.energy.ca.gov/GetDocument.aspx?tn=265693&DocumentContentId=102545
Construction Rate
Notes
This prototype represents a partitioned strip mall typology for retail up to approximately 100,000 ft².
Background Data [To be deleted prior to publication]

## Prototype
NORESCO, Updated August 2025
RetailStripMall
Characteristic | Value | Data Sources
Building Type | Small Retail
Building Category | Nonresidential
Vintages | 4 Vintages: Pre-1978 , 1978-1997 ,1998-2007 , 2008-2018 New Construction (2019+) | Based on the vintage bin analysis | NonRes-Vintage bins-Draft Report-30Nov2023-Final.docx
Shape |  | CBECC
Total Floor Area (ft²) | 9,375 (125 ft x 75 ft) | CBECC
Aspect Ratio | 1.67 overall (0.33 for small store & 0.67 for large store) | CBECC
Number of Floors | 1 | CBECC
Roof type | Roof membrane+Roof insulation+metal decking | CBECC
WWR | 8.24% | CBECC
Shading Geometry | none | CBECC
Floor to floor height (feet) | N/A | CBECC
Floor to ceiling height (feet) | 17 | CBECC
Glazing sill height (feet) | 3.0 ft (top of the window is 8 ft high) | CBECC
Background Data [To be deleted prior to publication]
Existing Retail Prototypes
Large size prototype | CEC: Retail_Large | CPUC: Retail_Multistory Large (Rt3) | CPUC: Retail_Single-Story Large (RtL)
Geometry
Total floor area (ft²) | 240000 | 120000 | 130502
Medium size prototype | CEC: Retail_Medium | PNNL : Retail_Stand alone | PNNL: Retail_Stripmall | CPUC: Retail_Grocery
Geometry | zoning same as PNNL Stand alone with more skylight
Total floor area (ft²) | 24692 | 24692 | 22500 | 49997
Small size prototype | CEC: Retail_Stripmall (Mixed use) | CPUC: Retail_Small (RtS)
Geometry
Total floor area (ft²) | 9375 | 8001

## Zones
Proposed Layout - RetailStripMall
Space Type | Space/Thermal Zone | Schedule Category | Conditioned (Y/N) | Area Fraction | Area (ft²) | Volume (ft³) | Multipliers | Number of People | People (Persons/1,000 ft²) [T24, 2025,Table 120.1-A] | Spaces and Zoning layout
Retail Sales Area (Retail Merchandise Sales) | LG_Store_1 | Retail | Y | 40% | 3750.0386 | 63750.0423 | 1 | 31.8753 | 17
Retail Sales Area (Retail Merchandise Sales) | SM_Store_1 | Retail | Y | 20% | 1874.9655 | 31875.0211 | 1 | 15.9372 | 17
Retail Sales Area (Retail Merchandise Sales) | SM_Store_2 | Retail | Y | 20% | 1874.9655 | 31875.0211 | 1 | 15.9372 | 17
Retail Sales Area (Retail Merchandise Sales) | SM_Store_3 | Retail | Y | 20% | 1874.9655 | 31875.0211 | 1 | 15.9372 | 17
Total (1 Space type) | Total (4 Space)s |  | Total (4 Conditioned zones) | 100% | 9374.9351 | 159375.1057 |  | 79.6869
Plan from CBECC 2022, Retail_Stripmall prototype
Background Data [To be deleted prior to publication]
Floorspace-Types-30Oct2024
Retail (CEUS 2022, statewide %)
Conditioned | Unconditioned |  | Ventilated
82.62% | 17.37% |  | 0.8344
Likely storage in larger Retail (see Medium/Standalone)
N

## Envelope
Envelope - RetailStripMall
Element | Prototype | Assembly Type | Construction | Thermal Properties | Vintage | Selected T24 | Note | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
External Wall | RetailStripmall | ExtWall_MetalFramed_NonRes | Metal-frame walls + insulation + Gypsum board | U-factor IP | Pre 1978 | N/A | ASHRAE 90.1, 2022, Table A3.3.3.1, 3.5", R-0 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352
[5 empty] | 1978-1997 | 1986 | Heat Capacity was considered 10.0-14.99 (Btu/F-ft²) | 0.15083 | 0.15748 | 0.15748 | 0.14368 | 0.14368 | 0.21645 | 0.21645 | 0.21645 | 0.21645 | 0.21645 | 0.18622 | 0.18622 | 0.18622 | 0.15873 | 0.15873 | 0.15083
[5 empty] | 1998-2007 | 2001 | TABLE 1-H-NonRes Bldgs | 0.182 | 0.182 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182
[5 empty] | 2008-2018 | 2013 | TABLE 140.3-B-NonRes Bldgs | 0.098 | 0.062 | 0.082 | 0.062 | 0.062 | 0.098 | 0.098 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062
[5 empty] | 2019+ | 2025 | TABLE 140.3-B-NonRes Bldgs | 0.06 | 0.055 | 0.071 | 0.055 | 0.055 | 0.06 | 0.06 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055
Roof | RetailStripmall | FlatRoof_WoodFramedAndOther_NonRes | Built-up roof (Metal Decking Roof): Roof membrane+roof insulation+metal decking | U-factor IP | Pre 1978 | N/A | Considering 30 years for roof/ insulation replacement. | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 1978-1997 | 1992 |  | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 1998-2007 | 2001 | Table 1-H | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.049 | 0.039 | 0.039 | 0.039 | 0.049 | 0.075 | 0.067 | 0.067 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.047 | 0.047 | 0.047 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028
Windows | RetailStripmall | FixedWindow_NonRes | CBECS 2018 shows that ~ 50 % of retail that were built before 2000 are single pane | U-factor IP | Pre 1978 | N/A | ASHRAE Handbook of Fundamentals for single pane & T24, 2013 for double pane (50%-50%) | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74
[5 empty] | 1978-1997 | N/A |  | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74
|  |  | Double pane |  | 1998-2007 | 2001 | Table 1-H | 0.49 | 0.49 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.34 | 0.36 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.36
| RetailStripmall | FixedWindow_NonRes | CBECS 2018 shows that ~ 50 % of retail that were built before 2000 are single pane | SHGC | Pre 1978 | N/A | ASHRAE Handbook of Fundamentals for single pane & T24, 2013 for double pane (50%-50%) | 0.525 | 0.525 | 0.525 | 0.525 | 0.525 | 0.525 | 0.525 | 0.525 | 0.525 | 0.525 | 0.525 | 0.525 | 0.525 | 0.525 | 0.525 | 0.525
[5 empty] | 1978-1997 | N/A |  | 0.525 | 0.525 | 0.525 | 0.525 | 0.525 | 0.525 | 0.525 | 0.525 | 0.51 | 0.525 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.525
|  |  | Double pane |  | 1998-2007 | 2001 | Table 1-H (Non north 0-10%) | 0.49 | 0.47 | 0.61 | 0.61 | 0.61 | 0.61 | 0.61 | 0.61 | 0.61 | 0.47 | 0.47 | 0.47 | 0.47 | 0.46 | 0.46 | 0.49
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.22 | 0.25 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.25
Infiltration
[5 empty] | Vintage | I_75 (cfm/ft²) 6-sdied Infiltration rate @ 75 pa | Note | I-design (cfm/ft²) (4-sided Infiltration rate at normal pressure) (Design flow rate approach and Flow/Exterior Wall Area calculation method)
|  |  |  | Infiltration | Pre 1978 | 1.1 | 2022 CASE report (Table 38) | 0.4629
[5 empty] | 1978-1997 | 1.1 | 2022 CASE report (Table 38) | 0.4629
[5 empty] | 1998-2007 | 1.1 | 2022 CASE report (Table 38) | 0.4629
[5 empty] | 2008-2018 | 1 | 2022 CASE report (Table 38) & T24, 2008-2016 (TABLE 140.3-B) | 0.42082
[5 empty] | 2019+ | 0.6 (barrier in all CZ) | 2022 CASE report (Table 38) & T24, 2025 (TABLE 140.3-B) | 0.25249
Source: Title 24 air barrier requirements (all editions) and the standardized infiltration rate reported in the 2022 CASE report and Dodge 2023 data
|  |  |  | Air Leakage Memo: |  | Infiltration_rate_report_14May2025-Short-Version.docx
Background Data [To be deleted prior to publication]
RetailStripmall
in.comstock_building_type | Sum of calc.weighted.sqft | %
Mass | 143492115.1243 | 29.19%
SteelFramed | 197402439.681 | 40.16%
WoodFramed | 150608075.9354 | 30.64%
Grand Total | 491502630.7407 | 100%

## HVAC System
HVAC system - RetailStripMall
Vintage | Heating | Cooling | Air Distribution | Source
Existing | PSZAC (furnace) | PSZAC (DX cooling) | PSZAC | CEUS 2022
New Construction | SZVAVHP | SZVAVHP | PSZVAVHP | Title 24, 2025, Engineering judgement
Efficiency of HVAC system (Efficiency is capacity-dependent. The following table provides a general estimate of system efficiency based on what we saw in the existing prototype runs, or assuming cooling load base on rule of thumbs
Vintage | Upgrade year | Heating | Cooling | Source
Pre 1978 | 2008 | Thermal Efficiency of 80%; | SEER 13 for <65 kBtu/h EER 10.3 for 65-135 kBtu/h EER 9.7 for 135-240 kBtu/h EER 9.5 for 240-760 kBtu/h | 2005 Title 20 Appliance Efficiency Regulations, 2005 T24, Tables 112-A, 112-B
1978-1997
1998-2007
2008-2018 | 2013 | Thermal Efficiency of 80%; | SEER 13, EER 11.2 for <65 kBtu/h EER 11.2 for 65-135 kBtu/h EER 11 for 135-240 kBtu/h EER 10 for 240-760 kBtu/h | 2013 Title 20 Appliance Efficiency Regulations, 2013 T24 Tables 112-A, 112-B
New Construction | 2025 | SEER 14 for <65 kBtu/h EER 11, COP fed min for 65-135 kBtu/h EER 10.6, COP fed min 135-240 kBtu/h EER 9.5 for >240 kBtu/h | SEER 14 for <65 kBtu/h EER 11, COP fed min for 65-135 kBtu/h EER 10.6, COP fed min 135-240 kBtu/h EER 9.5 for >240 kBtu/h | Title 20 Appliance Efficiency Regulations, 2025 T24, 2025 -Tables 110.2-A, 110.2-B
Fan Power
Vintage | Approach | System | Total Static Pressure (TSP) (in w.c.) [PNNL 20405, 2010, Table 5.11] | Fan Efficiency [ACM 2025] | Fan Motor and Drive Efficiency [ACM 2025, Table 13] | W/cfm [ACM 2025, Table 14 and 15] | Data Source
Existing | PNNL TSP | CAV | 2.5 for CAV <7,437 cfm 4.09 for CAV >=7,437 cfm | 0.65 | ~0.9 (The full-load efficiency of the motor serving the fan- will be determined based on ACM 2025, Table 13) |  | ACM 2025, PNNL 2010 TSD
Brake horse power (bhp)=(Supply cfm*TSP in w.c.)/(6356*Fan efficiency)
Fan power (w/cfm) = bhp/motor and drive efficiency *746
New Construction | ACM 2025 | SZVAVHP System >10,000 cfm | 3.3694 | 0.65 | 0.9 | 0.676 | ACM 2025
* 0.9 is an average fan efficiency according to ACM 2025, Table 13
Fan total eff (E+ input) = 0.65 x Motor_eff
TSP (E+ input) in w.c. = Motor_eff/746 x (6356 x Fan_eff) x W/cfm
Fan_eff=0.65
Background Data [To be deleted prior to publication]
Retail Stripmall
in.comstock | Sum of calc.weighted.sqft | %
Electricity | 69787484.7522 | 14.2%
NaturalGas | 421715145.9885 | 85.8%
Grand Total | 491502630.7407 | 100%
CEUS 2022 | Heating |  |  | Cooling |  | Air Distribution | Water Heater
| Floorspace Heated | Primary Heating | Fuel Type | Floorspace Cooled | Primary Cooling | Primary Air Dis | Fuel Type
|  | The default is the floorspace method unless otherwise specified |  |  | The default is the floorspace method unless otherwise specified | The default is the floorspace method unless otherwise specified
Retail | 79% | Package System / Heat Pump (80.2%) | Gas (58%) Elec ( 41%) | 80% | Package System / Heat Pump (80.2%) | Single Duct CAV (92.1%) | Elec (51%), Gas (34%)

## Thermostat
Thermostat Setpoints - RetailStripMall
Setpoint | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16 | Source
Heating Setpoint (F) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | T24 2022 - Appendix 5.4B
Heating Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Cooling Setpoint (F) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
Cooling Setback (F) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85

## Ventilation
Outdoor Airflow Rate - RetailStripMall
Space/Thermal Zone | Number of People | Floor Area (ft²) | cfm/person [T24, 2025, Equation 120.1-F and Table 120.1-A] | cfm/ft² [T24, 2025, Equation 120.1-F and Table 120.1-A] | Required Exhaust Rate [T24, 2025, Table 120.1-B – minimum exhaust rates] | Total cfm Driven by People | Total cfm Driven by Area | Total cfm Driven by Exhaust | Total cfm | Notes
LG_Store_1 | 31.8753 | 3750.0386 | 15 | 0.2 | 25/50 | 478.1299 | 750.0077 | 50 | 750.0077 | Exhaust rate for restroom
SM_Store_1 | 15.9372 | 1874.9655 | 15 | 0.2 |  | 239.0581 | 374.9931 | 0 | 374.9931
SM_Store_2 | 15.9372 | 1874.9655 | 15 | 0.2 |  | 239.0581 | 374.9931 | 0 | 374.9931
SM_Store_3 | 15.9372 | 1874.9655 | 15 | 0.2 |  | 239.0581 | 374.9931 | 0 | 374.9931
Background Data [To be deleted prior to publication]

## Water Heater
Water Heater - RetailStripMall
Vintage | WH Type | Efficiency | Tank Volume (gal) | Tank Loss | Unit | Source
Existing | Electric | 1 | 50 | 0.84% | %/hr | Loss per hour, 10 CFR 431.110(a) Table F-4
New Construction | Electric | 1 | 50 | 0.84% | %/hr
Peak Hot Water Consumption
Space Name | Baseline WH Type [CEUS 2022] | Total Area (ft²) | Number of People | Hot Water Usage Specification (gal/hr per person) [T24, 2022, Appendix 5.4A , sheet: "2022 SpaceFuncData-Input"] | Peak Hot Water Usage (gal/hr) | Peak Hot Water Usage (gal/min)
LG_Store_1 | Electric | 3750.0386 | 31.8753 | 0.18 | 5.7376 | 0.095626
SM_Store_1 | Electric | 1874.9655 | 15.9372 | 0.18 | 2.8687 | 0.047812
SM_Store_2 | Electric | 1874.9655 | 15.9372 | 0.18 | 2.8687 | 0.047812
SM_Store_3 | Electric | 1874.9655 | 15.9372 | 0.18 | 2.8687 | 0.047812
Total (4 Space)s |  | 9374.9351 | 79.6869 | 0 |  | 0.23906
Water Heater Capacity, Tank Capacity, and Tank Loss
WH Type | Peak Hot Water Usage (gal/hr) | Heat Output (Btu/hr) [ACM, 2025, 5.9.2: Rated capacity section] | WH Capacity (Btu/hr) [ACM, 2025, 5.9.2: Rated capacity section] | Required Energy Input (Btu/hr) | Storage Volume (gal) | Standby Loss | Unit | Off/On Cycle Loss Coefficient to Ambient Temp (Btu/h-F) | Source
Gas Storage WH | 0 | 0 | 0 | 0 | 0 | 0 | Btu/hr | 0 | Standby loss equation: Title 20, §1605.1 Table F-4 WH capacity equation: ACM, 2025, 5.9.2: Rated capacity section)
Electric resistance WH | 125 | 82877 | 70445.45 | 70445.45 | 50 | 0.84 | %/hr | 3.5028
Total | 125 | 82877 | 70445.45 | 70445.45 | 50
Design supply temperature (F) | 135 | Ref: T24 2022 - Appendix 5.4B |  |  | Standby Loss for Existing | 0.84 | %/hr | 3.5028
Cold Water supply temperature (F) | 55 | Ref: ACM, 2025, 5.9.2: Rated capacity section
WH system factor | 0.6 | Ref: ACM, 2025, 5.9.2: Rated capacity section
Reheat multiplier | 0.4
* The 0.40 multiplier is a storage sizing factor used to account for the fact that the water heater doesn't need to store the full peak hour demand—it can reheat water during that time. This factor assumes that the heater will recover part of the hot water used during the peak hour, so only 40% of the peak hour demand needs to be stored at any given moment.
**For Gas Water Heater: UA(Btu/h-°F)​=Q˙​SL​ (Btu/h)/ΔT (∘F)​
Ambient temp | 68
Delta T | 67
** For Electric Water Heater: UA(Btu/h-°F)​= 0.0834 *SL​ (%/hr)*V gal

## Interior Lights
Interior Lighting - RetailStripMall
Space Type | New Construction |  |  | Existing
| LPD (W/ft²) | Additional LPD for Portable Lighting (W/ft²) | Source | LPD (W/ft²) | Additional LPD for Portable Lighting (W/ft²) | Source
Retail Sales Area (Retail Merchandise Sales) | 0.95 |  | T24, part 6, 2025, Table 140.6-C | 1.2 |  | T24, part 6, 2016, Table 140.6-C
Background Data [To be deleted prior to publication]

## Ext Lighting
Exterior Lighting - RetailStripMall
Motion Controlled Luminaires (W) | Non-motion Controlled Luminaires (W) | Total (W) | Source
913.5372 | 346.5625 | 1260.0997 | T24, 2022
Exterior Lighting
Items (Assume LZ2) | Assumptions [2019 Outdoor Lighting CASE Report & PNNL 90.1-2010 TSD] |  | Unit | Lighting Power Allowance [T24, 2025, Table 140.7-A & 140.7-B] | Unit | Exterior lighting power (w)
IWA (Initial Wattage Allowance) |  |  |  | 200 | W | 200
Parking area | 400 ft² for every parking space 1 parking space per 360 ft² of gross building area | 10416.5945 | (ft²) | 0.019 | (W/ft²) | 197.9153
Building Entrance | 5 building entrance | 5 | (count) | 15 | (W/ea) | 75
Hardscape Ornamental Light | 0.1 ft² per 1 ft² of gross bldg area for hardscape ornamental light | 937.4935 | (ft²) | 0.007 | (W/ft²) | 6.5625
Building façade | 0.1 W per 1 ft² of facade area Façade Area = Perimeter × 0.5 × 17' The 0.5 factor assumes that only half of the perimeter walls are lit. -Formula ia developed based on the 2019 Outdoor Lighting CASE report | 3400 | (ft²) | 0.1 | (W/ft²) | 340
Sales canopy | 0.1 ft² per ft² of gross bldg area | 937.4935 | (ft²) | 0.47 | (W/ft²) | 440.6219
Motion controlled Luminaires | [5 empty] | 913.5372
Non-motion-controlled Luminaires | [5 empty] | 346.5625
Total | [5 empty] | 1260.0997
*Developed based on 2019 Outdoor Lighting CASE Report
Perimeter | 400
Total floor area | 9374.9351
Floors | 1
Background Data [To be deleted prior to publication]

## Equipment
Equipment - RetailStripMall
Space Type | Plug Load Power Density (W/ft²) | Refrigerator Power Density (W/ft²) | Gas Power Density (Btu/hr-ft²) | Source
Retail Sales Area (Retail Merchandise Sales) | 0.4 |  |  | Plug load and schedules project with CEC, 2025 T24 2022 - Appendix 5.4A: Space Use Data-T24N-2022
Background Data [To be deleted prior to publication]

## Schedules
Schedules - RetailStripMall
Zone | Schedule Category | Schedule | Source | Type | Hour
[5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
All Zones | Retail | Occupancy | T24 2022 - Appendix 5.4B, [Retail] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0
All Zones | Retail | Lights | T24 2022 - Appendix 5.4B, [Retail] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.55 | 0.55 | 0.5 | 0.2 | 0.05 | 0.05
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.55 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.4 | 0.4 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
All Zones | Retail | ElecEquipment | Plug load and schedules project with CEC, 2025 | Weekday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.4 | 0.4 | 0.4
|  |  |  | Saturday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.4 | 0.4
|  |  |  | Sunday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
All Zones | Retail | HVACAvail | T24 2022 - Appendix 5.4B, [Retail] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
All Zones | Retail | ServiceHotWater | T24 2022 - Appendix 5.4B, [Retail] | Weekday | 0.04 | 0.05 | 0.05 | 0.04 | 0.04 | 0.04 | 0.04 | 0.15 | 0.23 | 0.32 | 0.41 | 0.57 | 0.62 | 0.61 | 0.5 | 0.45 | 0.46 | 0.47 | 0.42 | 0.34 | 0.33 | 0.23 | 0.13 | 0.08
|  |  |  | Saturday | 0.11 | 0.1 | 0.08 | 0.06 | 0.06 | 0.06 | 0.07 | 0.2 | 0.24 | 0.27 | 0.42 | 0.54 | 0.59 | 0.6 | 0.49 | 0.48 | 0.47 | 0.46 | 0.44 | 0.36 | 0.29 | 0.22 | 0.16 | 0.13
|  |  |  | Sunday | 0.07 | 0.07 | 0.07 | 0.06 | 0.06 | 0.06 | 0.07 | 0.1 | 0.12 | 0.14 | 0.29 | 0.31 | 0.36 | 0.36 | 0.34 | 0.35 | 0.37 | 0.34 | 0.25 | 0.27 | 0.21 | 0.16 | 0.1 | 0.06
All Zones | Retail | Infiltration | T24 2022 - Appendix 5.4B, [Retail] | Weekday | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1
|  |  |  | Saturday | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1
|  |  |  | Sunday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1
All Zones | Retail | Refrigeration | T24 2022 - Appendix 5.4B, [Retail] | Weekday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Saturday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Sunday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
All Zones | Retail | HtgSetpt | T24 2022 - Appendix 5.4B, [Retail] | Weekday | 60 | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 60 | 60 | 60
|  |  |  | Saturday | 60 | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 60 | 60
|  |  |  | Sunday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 60 | 60 | 60 | 60 | 60
All Zones | Retail | ClgSetpt | T24 2022 - Appendix 5.4B, [Retail] | Weekday | 85 | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 85 | 85 | 85
|  |  |  | Saturday | 85 | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 85 | 85
|  |  |  | Sunday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 85 | 85 | 85 | 85 | 85
Other
| Building | ExtLightingNonMotionCtrl |  | Weekday | bar: Hour 1 to Hour 24
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
| Building | ExtLightingMotionCtrl |  | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Retails | Building | RetailSalePeopleActivityLevel | Based on Activity level schedules in CEC Prototypes | Weekday | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
|  |  |  | Saturday | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
|  |  |  | Sunday | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
Background Data [To be deleted prior to publication]
Background Data [To be deleted prior to publication] | bar: Hour 1

## Energy Usage
CalBEM Energy Consumption - RetailStripMall | [7 empty] | National Average (EnergyStar Portfolio Manager) |  |  |  | CEUS Energy Consumption : Retail | [8 empty] | PNNL RetailStripMall 2007 (with floor area of 22,500 ft2) for San Diego shows 62 KBTU/ft2 | PNNL results are close to RetailMedium
Prototype | CZ | CalBEM Electricity EUI (KBTU/ft²) | CalBEM Gas EUI (KBTU/ft²) | CalBEM Total EUI (KBTU/ft²) | New Construction Electricity EUI (KBTU/ft²) | New Construction Gas EUI (KBTU/ft²) | New Construction Total EUI (KBTU/ft²) | National Average | Acceptable Range (25% Higher) | Acceptable Range (25% Lower) | National Average Acceptable EUI Range | Prototype | CZ | Total Floorspace (Thousand of ft²) | CEUS 2023 Electricity EUI (kBtu/ft²) | CEUS 2023 Gas EUI (kBtu/ft²) | CEUS 2023 Total EUI (kBtu/ft²) | Acceptable Range (25% Higher) | Acceptable Range (25% Lower) | CEUS 2022 Acceptable EUI Range | PNNL RetailStripMall 2022 (with floor area of 22,500 ft2) for San Diego shows 29 KBTU/ft2
RetailStripMall | 1 | 43.6503 | 34.7795 | 78.4299 | 40.48 | 0 | 40.48 | 46.8 | 58.5 | 35.1 | 23.4 | Retail | 1 | 13814 | 37.9 | 10.4 | 48.3 | 60.375 | 36.225 | 24.15
| 2 | 48.0112 | 25.5682 | 73.5794 | 42.01 | 0 | 42.01 | 58.4 | 73 | 43.8 | 29.2 |  | 2 | 25239 | 26.6 | 14.8 | 41.4 | 51.75 | 31.05 | 20.7
| 3 | 42.6271 | 17.6309 | 60.258 | 39.54 | 0 | 39.54 | 52.3 | 65.375 | 39.225 | 26.15 |  | 3 | 88648 | 34.8 | 11.9 | 46.7 | 58.375 | 35.025 | 23.35
| 4 | 52.1671 | 21.8343 | 74.0014 | 42.67 | 0 | 42.67 | 60.9 | 76.125 | 45.675 | 30.45 |  | 4 | 44551 | 35.5 | 11.5 | 47 | 58.75 | 35.25 | 23.5
| 5 | 43.8578 | 15.8416 | 59.6995 | 39.43 | 0 | 39.43 | 50.4 | 63 | 37.8 | 25.2 |  | 5 | 9847 | 31.7 | 14.6 | 46.3 | 57.875 | 34.725 | 23.15
| 6 | 46.0886 | 5.2604 | 51.349 | 44.56 | 0 | 44.56 | 57.8 | 72.25 | 43.35 | 28.9 |  | 6 | 92562 | 29.3 | 4.6 | 33.9 | 42.375 | 25.425 | 16.95
| 7 | 45.7894 | 3.9679 | 49.7573 | 47.71 | 0 | 47.71 | 57.8 | 72.25 | 43.35 | 28.9 |  | 7 | 63471 | 35.1 | 3.2 | 38.3 | 47.875 | 28.725 | 19.15
| 8 | 53.3647 | 5.6488 | 59.0135 | 44.71 | 0 | 44.71 | 58.9 | 73.625 | 44.175 | 29.45 |  | 8 | 147354 | 29 | 4.5 | 33.5 | 41.875 | 25.125 | 16.75
| 9 | 53.4687 | 7.747 | 61.2157 | 44.81 | 0 | 44.81 | 59.6 | 74.5 | 44.7 | 29.8 |  | 9 | 212697 | 32.1 | 4.8 | 36.9 | 46.125 | 27.675 | 18.45
| 10 | 51.6691 | 7.5596 | 59.2288 | 45.53 | 0 | 45.53 | 60.2 | 75.25 | 45.15 | 30.1 |  | 10 | 149832 | 31.7 | 5.3 | 37 | 46.25 | 27.75 | 18.5
| 11 | 55.9096 | 24.1989 | 80.1085 | 46.55 | 0 | 46.55 | 62.3 | 77.875 | 46.725 | 31.15 |  | 11 | 45934 | 36.2 | 9.3 | 45.5 | 56.875 | 34.125 | 22.75
| 12 | 50.2497 | 21.9726 | 72.2223 | 44.39 | 0 | 44.39 | 61.3 | 76.625 | 45.975 | 30.65 |  | 12 | 195816 | 37.5 | 9.8 | 47.3 | 59.125 | 35.475 | 23.65
| 13 | 54.9117 | 17.104 | 72.0157 | 47.24 | 0 | 47.24 | 62.3 | 77.875 | 46.725 | 31.15 |  | 13 | 67122 | 42.3 | 8.9 | 51.2 | 64 | 38.4 | 25.6
| 14 | 56.8458 | 20.9867 | 77.8324 | 48 | 0 | 48 | 62.6 | 78.25 | 46.95 | 31.3 |  | 14 | 39049 | 29.3 | 4.4 | 33.7 | 42.125 | 25.275 | 16.85
| 15 | 67.1523 | 3.5693 | 70.7216 | 49.54 | 0 | 49.54 | 60.1 | 75.125 | 45.075 | 30.05 |  | 15 | 73160 | 34.1 | 8.3 | 42.4 | 53 | 31.8 | 21.2
| 16 | 47.8909 | 38.4677 | 86.3586 | 43.03 | 0 | 43.03 | 61.2 | 76.5 | 45.9 | 30.6 |  | 16 | 149464 | 32.8 | 5.3 | 38.1 | 47.625 | 28.575 | 19.05
Ref: CEUS 2022 Report
And converted FZ level data to CZ level
CEUS has only one category for Retail
Background Data [To be deleted prior to publication]

## Weights
% of Floor Area per CZ and Vintage Bin - Retail | [7 empty] | % of Floor Area per CZ and Vintage Bin - Retail
Prototype | CZ | Vintage Bin | [5 empty] | Prototype | Vintage Bin | CZ
|  | Pre-1978 | 1978-1997 | 1998-2007 | 2008-2018 | Not available |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
Retail | 1 | 31.2% | 28.3% | 16.2% | 8.6% | 15.7% | 100% | Retail | Pre-1978 | 1.032% | 2.937% | 8.47% | 4.478% | 0.5123% | 9.245% | 3.959% | 15.15% | 22.77% | 4.38% | 2.941% | 12.32% | 3.411% | 1.762% | 2.238% | 4.382% | 100%
| 2 | 48.6% | 29.2% | 6.8% | 2.6% | 12.8% | 100% |  | 1978-1997 | 0.9654% | 1.82% | 4.898% | 2.391% | 0.6523% | 6.121% | 6.717% | 8.877% | 13.6% | 12.82% | 2.873% | 13.56% | 4.426% | 2.92% | 5.583% | 11.78% | 100%
| 3 | 40% | 22.4% | 14.3% | 9.4% | 14% | 100.1% |  | 1998-2007 | 0.8936% | 0.6854% | 5.065% | 2.378% | 0.8837% | 5.233% | 3.57% | 8.596% | 13.11% | 10.33% | 3.788% | 18.44% | 7.631% | 2.796% | 5.919% | 10.69% | 100%
| 4 | 42% | 21.7% | 13.4% | 10.1% | 12.8% | 100% |  | 2008-2018 | 0.698% | 0.3836% | 4.893% | 2.637% | 0.261% | 2.686% | 1.16% | 4.394% | 4.996% | 21.7% | 2.94% | 10.57% | 3.94% | 5.328% | 9.302% | 24.11% | 100%
| 5 | 21.8% | 26.8% | 22.5% | 4.5% | 24.5% | 100.1% |  | Not available | 1.237% | 1.838% | 7.068% | 3.252% | 1.373% | 6.534% | 5.026% | 10.87% | 12.04% | 9.643% | 4.293% | 14.42% | 5.217% | 2.174% | 6.037% | 8.982% | 100%
| 6 | 41.8% | 26.8% | 14.2% | 4.9% | 12.4% | 100.1% |  | Total | 0.9739% | 1.779% | 6.248% | 3.14% | 0.6942% | 6.525% | 4.474% | 10.39% | 14.99% | 10.56% | 3.238% | 13.8% | 4.732% | 2.753% | 5.158% | 10.54% | 100%
| 7 | 26.1% | 42.8% | 14.1% | 3.1% | 13.9% | 100%
| 8 | 43% | 24.4% | 14.6% | 5.1% | 12.9% | 100%
| 9 | 44.8% | 25.9% | 15.4% | 4% | 9.9% | 100%
| 10 | 12.2% | 34.6% | 17.2% | 24.6% | 11.3% | 99.9%
| 11 | 26.8% | 25.3% | 20.6% | 10.9% | 16.4% | 100%
| 12 | 26.3% | 28% | 23.6% | 9.2% | 12.9% | 100%
| 13 | 21.2% | 26.7% | 28.5% | 10% | 13.6% | 100%
| 14 | 18.9% | 30.3% | 17.9% | 23.2% | 9.8% | 100.1%
| 15 | 12.8% | 30.9% | 20.2% | 21.6% | 14.5% | 100%
| 16 | 12.3% | 31.9% | 17.9% | 27.4% | 10.5% | 100%
| Statewide | 32.9% | 28% | 17.2% | 9.7% | 12.1% | 99.9%
Ref: CEUS 2022 dataset
And converted FZ level data to CZ level
CEUS has only one category for Retail
Background Data [To be deleted prior to publication] | [8 empty] | #DIV/0! | CZ 1: #DIV/0!; CZ 2: #DIV/0!; CZ 3: #DIV/0!

## PV (hidden)
PV - RetailStripMall
TBD

## EV Charger (hidden)
EV Charger - RetailStripMall
TBD
Background Data [To be deleted prior to publication]

## Data (hidden)
Space Function | Electric Equipment Load Intensity | Electric Equipment Load Intensity | LPD
Aging Eye/Low-vision (Corridor Area) |  |  | 2013 | 2016 | 2019 | 2025
Aging Eye/Low-vision (Dining)
Aging Eye/Low-vision (Lobby, Main Entry)
Aging Eye/Low-vision (Lounge/Waiting Area)
Aging Eye/Low-vision (Multipurpose Room)
Aging Eye/Low-vision (Religious Worship Area)
Aging Eye/Low-vision (Restroom)
Aging Eye/Low-vision (Stairwell)
Audience Seating Area
Auditorium Area
Auto Repair / Maintenance Area
Barber, Beauty Salon, Spa Area
Civic Meeting Place Area
Classroom, Lecture, Training, Vocational Areas
Concourse and Atria Area
Convention, Conference, Multipurpose and Meeting Area
Copy Room
Corridor Area
Dining Area (Bar/Lounge and Fine Dining)
Dining Area (Cafeteria/Fast Food)
Dining Area (Family and Leisure)
Electrical, Mechanical, Telephone Rooms
Exercise/Fitness Center and Gymnasium Areas
Financial Transaction Area
Healthcare Facility and Hospitals (Exam/Treatment Room)
Healthcare Facility and Hospitals (Imaging Room)
Healthcare Facility and Hospitals (Medical Supply Room)
Healthcare Facility and Hospitals (Nursery)
Healthcare Facility and Hospitals (Nurse's Station)
Healthcare Facility and Hospitals (Operating Room)
Healthcare Facility and Hospitals (Patient Room)
Healthcare Facility and Hospitals (Physical Therapy Room)
Healthcare Facility and Hospitals (Recovery Room)
Hotel Function Area
Kitchen/Food Preparation Area
Kitchenette or Residential Kitchen
Laboratory, Scientific
Laundry Area
Library (Reading Area)
Library (Stacks Area)
Lobby, Main Entry
Locker Room
Lounge, Breakroom, or Waiting Area
Manufacturing, Commercial & Industrial Work Area (Low Bay)
Manufacturing, Commercial & Industrial Work Area (High Bay)
Manufacturing, Commercial & Industrial Work Area (Precision)
Museum Area (Exhibition/Display)
Museum Area (Restoration Room)
Office Area (>250 square feet)
Office Area (<250 square feet)
Parking Garage Area (Parking Zone and Ramps)
Parking Garage Area (Daylight Adaptation Zones)
Pharmacy Area
Retail Sales Area (Grocery Sales)
Retail Sales Area (Retail Merchandise Sales)
Retail Sales Area (Fitting Room)
Religious Worship Area
Restrooms
Stairwell
Storage, Commercial/Industrial (Warehouse)
Storage, Commercial/Industrial (Refrigerated)
Storage, Commercial/Industrial (Shipping & Handling)
Storage (General)
Sports Arena - Playing Area (> 5,000 Spectators)
Sports Arena - Playing Area (2,000 - 5,000 Spectators)
Sports Arena - Playing Area (< 2,000 Spectators)
Sports Arena - Playing Area (Recreational)
Theater Area (Motion Picture)
Theater Area (Performance)
Transportation Function (Baggage Area)
Transportation Function (Ticketing Area)
Videoconferencing Studio
High-Rise Residential Living Spaces
Hotel/Motel Guest Room
All other
Attic
Reception Area
Elevator
Plenum
IT Room (EPD 12)
Computer Room (EPD 20)
Server Room (EPD 45)