## Notes
Data Sources
Dataset | Dodge 2023
CEUS 2022
ComStock 2023
Prototype | CEC 2028 School prototype | https://efiling.energy.ca.gov/GetDocument.aspx?tn=265691&DocumentContentId=102542
Codes | Title 24, part 6, referred to as T24 (1984, 2001, 2007, 2013, 2016, 2022, 2025)
ASHRAE 90.1 (2022)
CFR Title 10 (2008, 2010, 2025)
ACM 2022
| T24 2022 - Appendix 5.4A and Appendix 5.4B | https://www.energy.ca.gov/publications/2022/2022-nonresidential-and-multifamily-alternative-calculation-method-reference
Other | 2022 Reduced infiltration CASE report | https://title24stakeholders.com/wp-content/uploads/2020/10/2022-T24-Final-CASE-Report_Reduce-Infiltration.pdf
| 2019 Outdoor Lighting CASE Report | https://title24stakeholders.com/wp-content/uploads/2016/10/T24-2019-CASE-Study-Results-Report-Outdoor-Sources_Final_with-Attachments.pdf
| 2019 High Efficiency Fume Hoods in Laboratory Spaces CASE Report | https://title24stakeholders.com/wp-content/uploads/2017/09/2019-T24-CASE-Report_Fume-Hoods_Final_September-2017.pdf?
| PNNL 20405, 2011 | https://www.pnnl.gov/main/publications/external/technical_reports/PNNL-20405.pdf
| Air leakage Memo, NORESCO, 2025 | Infiltration_rate_report_14May2025-Short-Version.docx — internal NORESCO project memo (not a public URL). See Prototype basis / Source access below.
| ENERGY STAR certified commercial water heaters (electric heat pump; integrated commercial HPWH) | ENERGY STAR — electric (HPWH)
| ENERGY STAR commercial WH dataset (download) | ENERGY STAR dataset xmq6-bm79
| ENERGY STAR commercial WH eligibility (electric heat pump, min COPh 3) | ENERGY STAR key product criteria
Construction Rate
Dodge 2023 construction rates used in the SCE vintage-bin analysis. Legend labels STC 41 and STC 49 are Dodge structure-type series identifiers from that analysis (Prototype D6, NonRes-Vintage bins-Draft Report-30Nov2023). They are not Title 24 climate zones.
Notes
2025 T24 | School includes five buildings: north classroom, lab classroom, shop classroom, MPR/Admin, and gym/courts/locker.
Prototype basis
Geometry | Geometry is CEC SchoolHigh as implemented in CBECC (Prototype C7:C16; five buildings in B34: north classroom, lab classroom, shop classroom, MPR/Admin, gym/courts/locker). Floor area 174,819 ft². Prototype comparison columns (CalBEM SchoolLarge, DEER Education-Secondary, PNNL SchoolSecondary) are reference only.
Vintage bins | Existing vintages Pre-1978, 1978-1997, 1998-2007, 2008-2018 plus New Construction 2019+ follow the SCE Enhanced Prototypes vintage-bin analysis (Prototype D6). Dodge 2023 construction rates inform stock weighting; they are not a Title 24 prescriptive requirement.
Curriculum and stock | Comprehensive high school program (classrooms, labs, shops, gym/lockers, MPR, kitchen, library, administration). The prototype represents average California high-school stock. Funding/condition variation is carried in vintage envelope/HVAC/lighting assumptions (including Envelope H8 30-year roof replacement).
WWR, heights, energy | WWR 6.86%, no exterior shades (CEC). Floor-to-floor 14 ft except MPR/Admin 14–25 ft and Court 22–34 ft. Existing HVAC: PSZAC + gas furnace (MPR SZVAV). New construction: SZHP. Service water: existing electric resistance; NC heat-pump water heater (Water Heater B3:B4).
Abbreviations | T24 = California Title 24, Part 6. ACM = Nonresidential/Multifamily Alternative Calculation Method Reference Manual. CEC = California Energy Commission. CBECC = California Building Energy Code Compliance software. CEUS = California Commercial End-Use Survey. PSZAC = packaged single-zone air conditioner. SZHP = single-zone heat pump. SZVAV = single-zone VAV. HPWH = heat-pump water heater. SRR = skylight-to-roof ratio. WWR = window-to-wall ratio. IWA = initial wattage allowance.
Source access | Column C lists public links where they exist. Dodge 2023 is a licensed dataset with no public URL. The NORESCO air-leakage memo is an internal file (C19), not a webpage. ENERGY STAR water-heater rows use the commercial electric (heat pump) Product Finder and dataset xmq6-bm79. Schedule fractions that cite the Plug Loads and Schedules project with CEC (2025) do not have an external link yet; an ASHRAE paper has been submitted and the citation will be updated when that paper is published or when ACM 2028 is released.
Sources used | Used on this scorecard: CEC SchoolHigh (efiling tn=265691); T24 2022 App. 5.4A/5.4B; ACM 2025 §5.9.2 and fan tables; T24 Tables 140.3-B, 110.2-A/B, 140.6-C, 140.7-A/B, 120.1-A/B; 2022 Reduced Infiltration CASE; 2019 Outdoor Lighting CASE; 2019 Fume-hood CASE (labs present); PNNL 20405; ASHRAE 90.1-2022 Appendix A; ASHRAE Handbook of Fundamentals; ENERGY STAR commercial HPWH list. Reviewer-suggested references that do not support a retained assumption are not added.

## Prototype
NORESCO, Updated September 2026
SchoolHigh
Characteristic | Value | Data Sources
Building Type | High School
Building Category | Nonresidential
Version | v2-0
Vintages | 4 Vintages: Pre-1978, 1978-1997,1998-2007, 2008-2018 New Construction (2019+) | Based on the vintage bin analysis. A summary of the findings is presented in the following paper, with a link provided in the Notes tab: Yousefi, F., Athalye, R. (2025). “Determining Vintage Bins for Prototype Development: An Analysis of California Commercial Buildings.” ASHRAE Annual Conference.
Shape |  | The analysis uses prototype geometry originally developed by CEC approved 2028 SchoolK-8 prototype.
Total Floor Area (ft²) | 174818.98 | CEC SchoolKto8 / CBECC (same as Prototype comparison column C).
Aspect Ratio | It varies for different buildings. | Same as the CEC approved 2028 SchoolK-8 prototype
Number of Floors | It varies for different buildings. | Same as the CEC approved 2028 SchoolK-8 prototype
Roof type | Flat | Same as the CEC approved 2028 SchoolK-8 prototype
WWR | 6.86% | Same as the CEC approved 2028 SchoolK-8 prototype
Shading Geometry | No Shades | Same as the CEC approved 2028 SchoolK-8 prototype
Floor to floor height (feet) | It varies for different buildings: MPR/Admin: 14-25 Court: 22-34 Other buildings: 14 ft | Same as the CEC approved 2028 SchoolK-8 prototype
Floor to ceiling height (feet) | It varies for different buildings: MPR/Admin: 14-25 Court: 22-34 Other buildings: 14 ft | Same as the CEC approved 2028 SchoolK-8 prototype
Glazing sill height (feet) | It varies for different buildings. | Same as the CEC approved 2028 SchoolK-8 prototype
Above grade wall area (ft²) | 140514
Gross wall area (ft²) | 140514
Roof area (ft²) | 134334.45
Underground Gross Wall Area (ft²) | 0

## Zones
Proposed Layout - High School
Building | Space/Thermal Zone | Space Type [Primarily from: T24, 2022 Appendix 5.4A] - See Notes column | HVAC System Name/AHU Name | Schedule Category | Conditioned (Y/N) | Area Fraction | Area (ft²) | Volume (ft³) | Multipliers | Number of People | People (Persons/1,000 ft²) [T24, 2025,Table 120.1-A] | Notes | Total Floor area (multiper applied)
SchoolHigh Admin/MPR | ADMIN/MPR_BREAKROOM_ZN | Lounge, Breakroom, or Waiting Area | AHU-1 | MPR | Y | 0.329% | 575.2 | 8053.16 | 1 | 18.9816 | 33 |  | 575.2
SchoolHigh Admin/MPR | ADMIN/MPR_CAFETERIA ZNS 3_ZN | Dining Area (Cafeteria/Fast Food) | AHU-2 | MPR | Y | 3.153% | 5512.19 | 137811.47 | 1 | 181.9023 | 33 |  | 5512.19
SchoolHigh Admin/MPR | ADMIN/MPR_CONFERENCE ROOM ZNS 3_ZN | Convention, Conference, Multipurpose and Meeting Area | AHU-3 | MPR | Y | 0.958% | 1674.74 | 23447.5 | 1 | 55.2664 | 33 |  | 1674.74
SchoolHigh Admin/MPR | ADMIN/MPR_CORRIDOR_ZN | Corridor Area | AHU-4 | MPR | Y | 11.3% | 1161.52 | 16262.09 | 17 | 5.8076 | 5 |  | 19745.84
SchoolHigh Admin/MPR | ADMIN/MPR_EMT_ZN | Electrical, Mechanical, Telephone Rooms | AHU-5 | MPR | Y | 0.7957% | 278.21 | 3895.07 | 5 | 1.391 | 5 |  | 1391.05
SchoolHigh Admin/MPR | ADMIN/MPR_IDF ROOM_ZN | Electrical, Mechanical, Telephone Rooms | AHU-6 | MPR | Y | 0.9731% | 340.23 | 4763.43 | 5 | 1.7012 | 5 |  | 1701.15
SchoolHigh Admin/MPR | ADMIN/MPR_KITCHEN_ZN | Kitchen/Food Preparation Area | AHU-7 | Kitchen | Y | 0.8336% | 1457.25 | 20402.54 | 1 | 4.3717 | 3 |  | 1457.25
SchoolHigh Admin/MPR | ADMIN/MPR_LOBBY_ZN | Lobby, Main Entry | AHU-8 | MPR | Y | 2.841% | 1241.47 | 17381.45 | 4 | 40.9685 | 33 |  | 4965.88
SchoolHigh Admin/MPR | ADMIN/MPR_OFFICE - LT 250 SF ZNS 6_ZN | Office Area (<250 square feet) | AHU-9 | MPR | Y | 3.598% | 1048.35 | 14677.59 | 6 | 5.2417 | 5 |  | 6290.1
SchoolHigh Admin/MPR | ADMIN/MPR_RESTROOM ZNS 3_ZN | Restrooms | AHU-10 | MPR | Y | 1.031% | 901.17 | 12620.46 | 2 | 4.5058 | 5 |  | 1802.34
SchoolHigh Admin/MPR | ADMIN/MPR_STORAGE - GENERAL_ZN | Storage (General) | AHU-11 | MPR | Y | 2.855% | 1247.73 | 17469.08 | 4 | 6.2386 | 5 |  | 4990.92
SchoolHigh Admin/MPR | ADMIN/MPR_STORAGE - REFRIGERATED_ZN | Storage, Commercial/Industrial (Refrigerated) | AHU-12 | MPR | Y | 0.144% | 251.72 | 3524.26 | 1 | 0 | 0 |  | 251.72
SchoolHigh Admin/MPR | ADMIN/MPR_THEATER - PERFORMANCE_ZN | Theater Area (Performance) | AHU-13 | MPR | Y | 3.048% | 1065.56 | 26638.09 | 5 | 35.1635 | 33 |  | 5327.8
SchoolHigh Lab Classrooms | CLASSRM LAB_FLR 1_EMT-01_ZN | Electrical, Mechanical, Telephone Rooms | AHU-14 | Classroom | Y | 0.06922% | 121.01 | 1694.25 | 1 | 0.60505 | 5 |  | 121.01
SchoolHigh Lab Classrooms | CLASSRM LAB_FLR 1_EMT-02_ZN | Electrical, Mechanical, Telephone Rooms | AHU-15 | Classroom | Y | 0.05606% | 98.01 | 1372.2 | 1 | 0.49005 | 5 |  | 98.01
SchoolHigh Lab Classrooms | CLASSRM LAB_FLR 1_LAB ZNS 2_ZN | Laboratory, Scientific | AHU-16 | Classroom | Y | 1.175% | 2054.94 | 28770.52 | 1 | 51.3735 | 25 |  | 2054.94
SchoolHigh Lab Classrooms | CLASSRM LAB_FLR 1_LIBRARY - READING AREA_ZN | Library (Reading Area) | AHU-17 | Classroom | Y | 0.6848% | 1197.13 | 16760.6 | 1 | 11.9713 | 10 |  | 1197.13
SchoolHigh Lab Classrooms | CLASSRM LAB_FLR 1_RESTROOM_ZN | Restrooms | AHU-18 | Classroom | Y | 0.3221% | 563.05 | 7883.15 | 1 | 2.8152 | 5 |  | 563.05
SchoolHigh Lab Classrooms | CLASSRM LAB_FLR 1_STORAGE - GENERAL_ZN | Storage (General) | AHU-19 | Classroom | Y | 0.2178% | 380.84 | 5331.98 | 1 | 1.9042 | 5 |  | 380.84
SchoolHigh Lab Classrooms | CLASSRM LAB_FLR 2_CLASSROOM_ZN | Classroom, Lecture, Training, Vocational Areas | AHU-20 | Classroom | Y | 0.2178% | 380.84 | 5331.98 | 1 | 9.521 | 25 |  | 380.84
SchoolHigh Lab Classrooms | CLASSRM LAB_FLR 2_IDF ROOM_ZN | Electrical, Mechanical, Telephone Rooms | AHU-21 | Classroom | Y | 0.06922% | 121.01 | 1694.25 | 1 | 0.60505 | 5 |  | 121.01
SchoolHigh Lab Classrooms | CLASSRM LAB_FLR 2_LAB ZNS 3_ZN | Laboratory, Scientific | AHU-22 | Classroom | Y | 1.86% | 3252.06 | 45531.11 | 1 | 81.3015 | 25 |  | 3252.06
SchoolHigh Lab Classrooms | CLASSRM LAB_FLR 2_RESTROOM_ZN | Restrooms | AHU-23 | Classroom | Y | 0.3221% | 563.05 | 7883.15 | 1 | 2.8152 | 5 |  | 563.05
SchoolHigh Lab Classrooms | CLASSRM LAB_FLR 2_STORAGE - GENERAL_ZN | Storage (General) | AHU-24 | Classroom | Y | 0.05606% | 98.01 | 1372.2 | 1 | 0.49005 | 5 |  | 98.01
SchoolHigh North Classrooms | CLASSRM N_FLR 1_CLASSROOM-01_ZN | Classroom, Lecture, Training, Vocational Areas | AHU-25 | Classroom | Y | 1.719% | 1001.75 | 14025.15 | 3 | 25.0437 | 25 |  | 3005.25
SchoolHigh North Classrooms | CLASSRM N_FLR 1_CLASSROOM-02 ZNS 6_ZN | Classroom, Lecture, Training, Vocational Areas | AHU-26 | Classroom | Y | 17.32% | 6054.03 | 84760.52 | 5 | 151.3508 | 25 |  | 30270.15
SchoolHigh North Classrooms | CLASSRM N_FLR 1_OFFICE - LT 250 SF_ZN | Office Area (<250 square feet) | AHU-27 | Classroom | Y | 0.9889% | 288.13 | 4033.99 | 6 | 1.4406 | 5 |  | 1728.78
SchoolHigh North Classrooms | CLASSRM N_FLR 1_RESTROOM_ZN | Restrooms | AHU-28 | Classroom | Y | 0.6094% | 532.7 | 7458.19 | 2 | 2.6635 | 5 |  | 1065.4
SchoolHigh North Classrooms | CLASSRM N_FLR 2_CLASSROOM-01 ZNS 6_ZN | Classroom, Lecture, Training, Vocational Areas | AHU-29 | Classroom | Y | 17.32% | 6054.03 | 84760.52 | 5 | 151.3508 | 25 |  | 30270.15
SchoolHigh North Classrooms | CLASSRM N_FLR 2_CLASSROOM-02_ZN | Classroom, Lecture, Training, Vocational Areas | AHU-30 | Classroom | Y | 1.719% | 1001.75 | 14025.15 | 3 | 25.0437 | 25 |  | 3005.25
SchoolHigh North Classrooms | CLASSRM N_FLR 2_OFFICE - LT 250 SF_ZN | Office Area (<250 square feet) | AHU-31 | Classroom | Y | 0.9889% | 288.13 | 4033.99 | 6 | 1.4406 | 5 |  | 1728.78
SchoolHigh North Classrooms | CLASSRM N_FLR 2_RESTROOM_ZN | Restrooms | AHU-32 | Classroom | Y | 0.6094% | 532.7 | 7458.19 | 2 | 2.6635 | 5 |  | 1065.4
SchoolHigh Shop Classrooms | CLASSRM SHOP_EMT_ZN | Electrical, Mechanical, Telephone Rooms | AHU-33 | Classroom | Y | 0.09774% | 170.87 | 2392.3 | 1 | 0.85435 | 5 |  | 170.87
SchoolHigh Shop Classrooms | CLASSRM SHOP_IDF ROOM_ZN | Electrical, Mechanical, Telephone Rooms | AHU-34 | Classroom | Y | 0.0489% | 85.48 | 1196.71 | 1 | 0.4274 | 5 |  | 85.48
SchoolHigh Shop Classrooms | CLASSRM SHOP_RESTROOM_ZN | Restrooms | AHU-35 | Classroom | Y | 0.1522% | 266.03 | 3724.56 | 1 | 1.3301 | 5 |  | 266.03
SchoolHigh Shop Classrooms | CLASSRM SHOP_SHOP-01 ZNS 4_ZN | Wood/Metal Shop Classroom | AHU-36 | Classroom | Y | 3.143% | 5494.54 | 76927.37 | 1 | 54.9454 | 10 |  | 5494.54
SchoolHigh Shop Classrooms | CLASSRM SHOP_SHOP-02_ZN | Wood/Metal Shop Classroom | AHU-37 | Classroom | Y | 0.8238% | 1440.14 | 20162.95 | 1 | 14.4014 | 10 |  | 1440.14
SchoolHigh Shop Classrooms | CLASSRM SHOP_STORAGE - GENERAL_ZN | Storage (General) | AHU-38 | Classroom | Y | 0.6772% | 1183.8 | 16573.95 | 1 | 5.919 | 5 |  | 1183.8
SchoolHigh Sports | COURTS - AUX ZN | Exercise/Fitness Center and Gymnasium Areas | AHU-39 | Gym | Y | 2.966% | 5184.51 | 176281.81 | 1 | 51.8451 | 10 |  | 5184.51
SchoolHigh Sports | COURTS ZN | Exercise/Fitness Center and Gymnasium Areas | AHU-40 | Gym | Y | 6.92% | 12097.18 | 411324.21 | 1 | 120.9718 | 10 |  | 12097.18
SchoolHigh Sports | LOCKERS ZN | Locker Room | AHU-41 | Gym | Y | 4.366% | 7632.74 | 167928.58 | 1 | 38.1637 | 5 |  | 7632.74
SchoolHigh Sports | ROOMS & STUDIOS ZN | Exercise/Fitness Center and Gymnasium Areas | AHU-42 | Gym | Y | 2.636% | 4608.45 | 101390.84 | 1 | 46.0845 | 10 |  | 4608.45
Total (5 Buildings) | Total (42 spaces) | Total (18 Space types) | Total (42 HVAC Systems) | Total (4 Schedule categories) | Total (42 Conditioned zones) | 100% | 79502.25 | 1629030.56 |  | 1221.3724
Area Distribution By Space Type
[14 empty] | Space Type | Area (ft²) | % Area
[14 empty] | Lounge, Breakroom, or Waiting Area | 575.2 | 0.329%
[14 empty] | Dining Area (Cafeteria/Fast Food) | 5512.19 | 3.153%
[14 empty] | Convention, Conference, Multipurpose and Meeting Area | 1674.74 | 0.958%
[14 empty] | Corridor Area | 1161.52 | 11.3%
[14 empty] | Electrical, Mechanical, Telephone Rooms | 1214.82 | 2.11%
[14 empty] | Kitchen/Food Preparation Area | 1457.25 | 0.8336%
[14 empty] | Lobby, Main Entry | 1241.47 | 2.841%
[14 empty] | Office Area (<250 square feet) | 1624.61 | 5.576%
[14 empty] | Restrooms | 3358.7 | 3.046%
[14 empty] | Storage (General) | 2910.38 | 3.806%
[14 empty] | Storage, Commercial/Industrial (Refrigerated) | 251.72 | 0.144%
[14 empty] | Theater Area (Performance) | 1065.56 | 3.048%
[14 empty] | Laboratory, Scientific | 5307 | 3.036%
[14 empty] | Library (Reading Area) | 1197.13 | 0.6848%
[14 empty] | Classroom, Lecture, Training, Vocational Areas | 14492.4 | 38.29%
[14 empty] | Wood/Metal Shop Classroom | 6934.68 | 3.967%
[14 empty] | Exercise/Fitness Center and Gymnasium Areas | 21890.14 | 12.52%
[14 empty] | Locker Room | 7632.74 | 4.366%
[14 empty] | Total | 79502.25 | 100%
N

## Envelope
Envelope - SchoolHigh
Element | Prototype | Assembly Type | Construction | Thermal properties | Vintage | Selected T24 | Notes | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
External Wall | SchoolHigh | ExtWall_MetalFramed_NonRes | Metal frame + insulation + Gypsum board | U-value IP | Pre 1978 | N/A | ASHRAE 90.1-2022 Table A3.3.3.1 (metal-framed), 3.5 in., R-0, U-0.352 all CZ | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352
[5 empty] | 1978-1997 | 1992 | TABLE NO. 1-I | 0.182 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182
[5 empty] | 1998-2007 | 2001 | Table 1-H metal frame | 0.182 | 0.182 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182
[5 empty] | 2008-2018 | 2013 | Table 140.3-B metal-framed | 0.098 | 0.062 | 0.082 | 0.062 | 0.062 | 0.098 | 0.098 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062
[5 empty] | 2019+ | 2025 | Table 140.3-B (2025) Metal-framed walls | 0.06 | 0.055 | 0.071 | 0.055 | 0.055 | 0.06 | 0.06 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055
Roof | SchoolHigh | FlatRoof_WoodFramedAndOther_NonRes | Built-up Roof roof membrane+roof insulation+metal decking | U-value IP | Pre 1978 | N/A | Considering 30 years for roof/insulation replacement | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 1978-1997 | N/A |  | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 1998-2007 | 2001 | Table 1-H | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.049 | 0.039 | 0.039 | 0.039 | 0.049 | 0.075 | 0.067 | 0.067 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.047 | 0.047 | 0.047 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028
Windows | SchoolHigh | FixedWindow_NonRes | Single pane | U-value IP | Pre 1978 | N/A | ASHRAE Handbook of Fundamentals (Table 4-Ch15) for single pane & T24, 2013 for double pane (33%-67%)* | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108
[5 empty] | 1978-1997 | N/A |  | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108
|  |  | Double pane |  | 1998-2007 | 2001 | Table 1-H | 0.49 | 0.49 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.34 | 0.36 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.36
| SchoolHigh | FixedWindow_NonRes | Single pane | SHGC | Pre 1978 | N/A | ASHRAE Handbook of Fundamentals (Table 10-Ch15) for single pane & T24, 2013 for double pane (33%-67%)* | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282
[5 empty] | 1978-1997 | N/A |  | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282
|  |  | Double pane |  | 1998-2007 | 2001 | Table 1-H — WWR ≤10% (prototype 6.86%), SHGC non-north. | 0.43 | 0.31 | 0.41 | 0.41 | 0.41 | 0.34 | 0.34 | 0.34 | 0.34 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.43
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.22 | 0.25 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.25
Skylight | SchoolHigh | Skylight | Plastic curb-mounted | U-factor IP | Pre 1978 | 1992 | Table 1-I Translucent (1992 term for this plastic curb product). CalBEM skylight 1,825 ft² vs CEC 547 ft²; SRR ~0.4–1.4% (0–2% bin). | 0.85 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
[5 empty] | 1978-1997 | 1992 |  | 0.85 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
[5 empty] | 1998-2007 | 2001 | Table 1-H plastic w/curb U-factor (U does not vary by SRR). | 0.87 | 1.1 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 0.87
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88
|  |  |  | SHGC | Pre 1978 | 1992 | Table 1-I Translucent SHGC (1992 term; same plastic curb product). | 0.81 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81
[5 empty] | 1978-1997 | 1992 |  | 0.81 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81
[5 empty] | 1998-2007 | 2001 | Table 1-H plastic w/curb, SRR 0–2% (High ~0.4% CEC / ~1.4% CalBEM). Not 2.1–5%. | 0.77 | 0.77 | 0.79 | 0.79 | 0.79 | 0.77 | 0.77 | 0.77 | 0.77 | 0.77 | 0.77 | 0.77 | 0.77 | 0.71 | 0.71 | 0.77
[5 empty] | 2008-2018 | 2013 | Table 140.3-B plastic curb SHGC = NR; used 2001 Table 1-H 0–2% SRR. | 0.77 | 0.77 | 0.79 | 0.79 | 0.79 | 0.77 | 0.77 | 0.77 | 0.77 | 0.77 | 0.77 | 0.77 | 0.77 | 0.71 | 0.71 | 0.77
[5 empty] | 2019+ | 2025 | Table 140.3-B (2025) plastic curb SHGC = NR; same 2001 0–2% SRR values. | 0.77 | 0.77 | 0.79 | 0.79 | 0.79 | 0.77 | 0.77 | 0.77 | 0.77 | 0.77 | 0.77 | 0.77 | 0.77 | 0.71 | 0.71 | 0.77
Floor: SlabOnGrade_Unheated_NonRes is a 4 in. concrete slab-on-grade with no insulation. It is the same for every vintage (F-factor 0.73), so it is documented here instead of as a table row.
Infiltration
|  |  | Building | Zones | Vintage | I_75 6-Sided Inifltration rate @ 75 pa | Note | I-design (cfm/ft²) (4-sided Infiltration rate at normal presure) (Design flow rate approach and Flow/Exterior Wall Area calulation method)
|  | Infiltration | SchoolHigh Admin/MPR |  | Pre 1978 | 1.1 | 2022 CASE report (Table 38) | 1.0981 | [15 empty] | Floor or roof area (ft2) | 55686.18
[5 empty] | 1978-1997 | 1.1 | 2022 CASE report (Table 38) | 1.0981 | [15 empty] | Walls area (ft2) | 14075
[5 empty] | 1998-2007 | 1.1 | 2022 CASE report (Table 38) | 1.0981 | [15 empty] | Building 4 sided area (ft2)= | 14075
[5 empty] | 2008-2018 | 1 | 2022 CASE report (Table 38) & T24, 2008-2016 (Table 140.3-B)--Air barrier is required in CZ 10-16 | 0.99823 | [15 empty] | Building 6 sided area (ft2)= | 125447.36
[5 empty] | 2019+ | 0.6 | 2022 CASE report (Table 38) & T24, 2025 (Table 140.3-B)--Air barrier is required in all CZs | 0.59894 | [15 empty] | 6 sided /4 sided factor= | 8.9128
|  |  | SchoolHigh Lab Classrooms |  | Pre 1978 | 1.1 | 2022 CASE report (Table 38) | 0.36083 | [15 empty] | Floor or roof area (ft2) | 8829.95
[5 empty] | 1978-1997 | 1.1 | 2022 CASE report (Table 38) | 0.36083 | [15 empty] | Walls area (ft2) | 9156
[5 empty] | 1998-2007 | 1.1 | 2022 CASE report (Table 38) | 0.36083 | [15 empty] | Building 4 sided area (ft2)= | 9156
[5 empty] | 2008-2018 | 1 | 2022 CASE report (Table 38) & T24, 2008-2016 (Table 140.3-B)--Air barrier is required in CZ 10-16 | 0.32802 | [15 empty] | Building 6 sided area (ft2)= | 26815.9
[5 empty] | 2019+ | 0.6 | 2022 CASE report (Table 38) & T24, 2025 (Table 140.3-B)--Air barrier is required in all CZs | 0.19681 | [15 empty] | 6 sided /4 sided factor= | 2.9288
|  |  | SchoolHigh North Classrooms |  | Pre 1978 | 1.1 | 2022 CASE report (Table 38) | 1.3054 | [15 empty] | Floor or roof area (ft2) | 72139.16
[5 empty] | 1978-1997 | 1.1 | 2022 CASE report (Table 38) | 1.3054 | [15 empty] | Walls area (ft2) | 15036
[5 empty] | 1998-2007 | 1.1 | 2022 CASE report (Table 38) | 1.3054 | [15 empty] | Building 4 sided area (ft2)= | 15036
[5 empty] | 2008-2018 | 1 | 2022 CASE report (Table 38) & T24, 2008-2016 (Table 140.3-B)--Air barrier is required in CZ 10-16 | 1.1867 | [15 empty] | Building 6 sided area (ft2)= | 159314.32
[5 empty] | 2019+ | 0.6 | 2022 CASE report (Table 38) & T24, 2025 (Table 140.3-B)--Air barrier is required in all CZs | 0.71202 | [15 empty] | 6 sided /4 sided factor= | 10.5955
|  |  | SchoolHigh Shop Classrooms |  | Pre 1978 | 1.1 | 2022 CASE report (Table 38) | 0.44404 | [15 empty] | Floor or roof area (ft2) | 8640.86
[5 empty] | 1978-1997 | 1.1 | 2022 CASE report (Table 38) | 0.44404 | [15 empty] | Walls area (ft2) | 6636
[5 empty] | 1998-2007 | 1.1 | 2022 CASE report (Table 38) | 0.44404 | [15 empty] | Building 4 sided area (ft2)= | 6636
[5 empty] | 2008-2018 | 1 | 2022 CASE report (Table 38) & T24, 2008-2016 (Table 140.3-B)--Air barrier is required in CZ 10-16 | 0.40367 | [15 empty] | Building 6 sided area (ft2)= | 23917.72
[5 empty] | 2019+ | 0.6 | 2022 CASE report (Table 38) & T24, 2025 (Table 140.3-B)--Air barrier is required in all CZs | 0.2422 | [15 empty] | 6 sided /4 sided factor= | 3.6042
|  |  | SchoolHigh Sports |  | Pre 1978 | 1.1 | 2022 CASE report (Table 38) | 0.39064 | [15 empty] | Floor or roof area (ft2) | 29522.88
[5 empty] | 1978-1997 | 1.1 | 2022 CASE report (Table 38) | 0.39064 | [15 empty] | Walls area (ft2) | 27200
[5 empty] | 1998-2007 | 1.1 | 2022 CASE report (Table 38) | 0.39064 | [15 empty] | Building 4 sided area (ft2)= | 27200
[5 empty] | 2008-2018 | 1 | 2022 CASE report (Table 38) & T24, 2008-2016 (Table 140.3-B)--Air barrier is required in CZ 10-16 | 0.35513 | [15 empty] | Building 6 sided area (ft2)= | 86245.76
[5 empty] | 2019+ | 0.6 | 2022 CASE report (Table 38) & T24, 2025 (Table 140.3-B)--Air barrier is required in all CZs | 0.21308 | [15 empty] | 6 sided /4 sided factor= | 3.1708
Source: T24 air barrier requirements (all editions) and the standardized infiltration rate reported in the 2022 CASE report and Dodge 2023 data
|  |  |  | Air Lekage Memo: |  | Infiltration_rate_report_14May2025-Short-Version.docx

## HVAC System
HVAC system - SchoolHigh
Vintage | Zones | Heating | Cooling | Air Distribution | Other Systems | Source | Note
Exisiting | All Space Types except MPR/refrigerated storage | Gas Furnace | PSZAC (DX cooling) | CAV | OA mixing. Air-side economizer: not modeled (see Economizer / ERV). | Engineering Judgement | System 3a
| Admin/MPR Multipurpose Room / Cafeteria | SZHP (DX heating) | SZHP (DX cooling) | SZVAV (single-zone VAV) | OA mixing. Air-side economizer: not modeled (see Economizer / ERV). | Engineering Judgement | VAV:NoReheat terminal, Fan:VariableVolume for the tall MPR/cafeteria volume. Theater and other Admin zones remain CAV.
| Admin/MPR_Storage - Refrigerated | n/a (walk-in refrigeration) | Walk-in cooler (not PSZ DX) | n/a | n/a — walk-in refrigeration, not an air-side HVAC OA system. | Engineering Judgement | Refrigeration system; 35°F product; equipment W/ft² on Equipment tab.
New Construction | All Space Types except MPR and refrigerated storage | SZHP | SZHP | CAV | OA mixing. Air-side economizer: not modeled (see Economizer / ERV). | ACM 2025 | System 3b
| Admin/MPR Multipurpose Room / Cafeteria | SZHP (DX heating) | SZHP (DX cooling) | SZVAV (single-zone VAV) | OA mixing. Air-side economizer: not modeled (see Economizer / ERV). | Engineering Judgement | VAV:NoReheat terminal, Fan:VariableVolume for the tall MPR/cafeteria volume. Theater and other Admin zones remain CAV.
| Admin/MPR_Storage - Refrigerated | n/a (walk-in refrigeration) | Walk-in cooler (not PSZ DX) | n/a | n/a — walk-in refrigeration, not an air-side HVAC OA system. | Engineering Judgement | Refrigeration system; 35°F product; equipment W/ft² on Equipment tab.
Efficiency of HVAC System (Efficiency is capacity-dependent. The following table provides a general estimate of system efficiency based on preliminary simulations in one climate zone, or assuming cooling load based on rule of thumb)
Vintage | Upgrade/Installed year | Gas Furnace | Heating DX | Cooling DX | Sources | Note
Pre 1978 | 2008 | Thermal Efficiency of 80% | n/a | EER 11.2 for <65 kBtu/h EER 10.3 for 65-135 kBtu/h | 2005 Title 20 Appliance Efficiency Regulations, 2005 T24 Standards, Tables 112-A, 112-B
1978-1997
1998-2007
2008-2018 | 2013 | Thermal Efficiency of 80% | n/a | EER 11.2 for <65 kBtu/h EER 11.2 for 65–135 kBtu/h | 2013 Title 20 Appliance Efficiency Regulations, 2013 T24 Tables 110.2 | 2013 T24 Table 110.2-A (air-cooled packaged AC). Existing vintage is PSZAC + gas furnace, not HP.
New Construction | 2025 | n/a | Heating @ 47°F: <65 kBtu/h (AHRI 210/240): federal minimum HSPF2 / 10 CFR 430 65–135 kBtu/h: COP 3.40 (10 CFR 431 / T24 Table 110.2-B) Heating @ 17°F: COP 2.25 (Table 110.2-B) | <65 kBtu/h packaged HP (10 CFR 430.32): SEER2 13.4 (pair to HSPF2 6.7) 65–135 kBtu/h: EER 11.0 + federal min IEER (Table 110.2-B) 135–240 kBtu/h: EER 10.6 + federal min IEER (MPR bin) ≥240 kBtu/h: EER 9.5 + federal min IEER | T24 2025 Table 110.2-B; 10 CFR 431.97 (COP @ 47°F); 10 CFR 430.32 (HSPF2/SEER2 <65 kBtu/h); AHRI 340/360 (≥65) / AHRI 210/240 (<65)
|  | * Et = Combustion efficiency | * Et = Thermal efficiency
Fan power
Vintage | Approach | System | Total Static Pressure (TSP) (in w.c.) | Fan Efficiency [ACM 2025] | Motor Efficiency | Fan Power Index (W/cfm) | Data Source
Existing | PNNL 90.1-2011, TSP | CAV, PSZ classrooms/admin (except MPR/cafeteria), design airflow < 7,437 cfm | 2.5 | 0.65 | ASHRAE 90.1, 2004, Table 10.8 * |  | Fan power formula: PNNL 20405, 2010, section 5.2.2.5 TSP and fan efficiency: PNNL 20405, 2010, Table 5.11, 90.1-04ac values Motor and drive efficiency: ASHRAE 90.1, 2004, Table 10.8 | PNNL 20405, 2010, Table 5.11
|  | SZVAV, Admin/MPR Multipurpose Room / Cafeteria, VAV > 4,648 cfm | 5.58
Brake horsepower (bhp) = (Supply cfm × TSP in w.c.) / (6356 × fan efficiency)
Fan power (w/cfm) = (bhp × 746) / ( supply cfm × motor efficiency )
New Construction | ACM 2025 | SZHP (System 3b), CAV classrooms/admin, ≤5,000 cfm | TSP = fan power × motor efficiency × fan efficiency × 6356 / 746 | 0.65 | 2025 ACM Table 12 ** | 0.744 | Fan power index: [ACM 2025, Table 13] Motor efficiency: [ACM 2025, Table 12]
|  | SZVAVHP (System 7b), MPR/cafeteria, >10,000 cfm | TSP = fan power × motor efficiency × fan efficiency × 6356 / 746 |  |  | 0.676
* According to PNNL 20405 section 5.2.2.5, the full-load efficiency of the motor serving the fan is taken from ASHRAE 90.1, 2004, Table 10.8, based on motor nameplate and assuming enclosed motors operating at 1,800 rotations per minute (rpm) Motor nameplate size (bhp) = brake horsepower (bhp) × 1.1 ( using a 10% oversizing factor)
** The full‑load efficiency of the motor serving the fan is taken from ACM 2025 Table 12 based on the cfm of the fan. Brake horsepower (bhp) = (Supply cfm from sizing run × fan power in W/cfm) / 746. Note: Packaged SZHP. Same index as Hotel Small System 3b ≤5,000 cfm. Note: Single-zone VAV heat pump, not System 6. ACM System 7b >10,000 cfm = 0.676; >5,000–10,000 cfm = 0.720. PNNL row was VAV >4,648 cfm.
Economizer / ERV | Air-side economizer: not modeled. EnergyPlus Controller:OutdoorAir Economizer Control Type = NoEconomizer on existing PSZAC and NC SZHP units. ERV: not modeled. T24 §140.4(e) would require an air economizer when cooling capacity ≥ 54,000 Btu/h (with listed exceptions); CBECC Standard Design uses FixedDryBulb on units that meet that threshold. This prototype does not include economizers.
Background Data [To be deleted prior to publication]

## Thermostat
Thermostat Setpoints - SchoolHigh
Setpoint | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16 | Source
School Heating Setpoint (F) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | T24 2022 - Appendix 5.4B
School Heating Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
School Cooling Setpoint (F) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | T24 2022 - Appendix 5.4B
School Cooling Setback (F) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
Kitchen Heating Setpoint (F) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | T24 2022 - Appendix 5.4B (school kitchen occupied 70/75; not commercial restaurant 66–79)
Kitchen Heating Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Kitchen Cooling Setpoint (F) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
Kitchen Cooling Setback (F) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
Restrooms Heating Setpoint (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | PNNL 90.1 Primary School bathroom (HTGSETP_SCH_Setback / CLGSETP_SCH_Setup)
Restrooms Heating Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Restrooms Cooling Setpoint (F) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
Restrooms Cooling Setback (F) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
Storage and Electrical/Mechanical (non-refrigerated) Heating Setpoint (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | Engineering Judgment (semi-conditioned storage / electrical-mechanical)
Storage and Electrical/Mechanical (non-refrigerated) Heating Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Storage and Electrical/Mechanical (non-refrigerated) Cooling Setpoint (F) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
Storage and Electrical/Mechanical (non-refrigerated) Cooling Setback (F) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
Refrigerated storage setpoint (F) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | Engineering judgment, medium-temp cooler within T24 28–55°F
Refrigerated storage setback (F) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35

## Ventilation
Outdoor Airflow Rate - SchoolHigh
Space Type [Primarily from: T24, 2022 Appendix 5.4A] - See Notes column | Space/Thermal Zone | Number of People | Floor Area (ft²) | cfm/person [T24, 2025, Equation 120.1-F and Table 120.1-A] | cfm/ft² [T24, 2025, Equation 120.1-F and Table 120.1-A] | Required exhaust rate-CFM/ft²- [T24, 2025, Table 120.1-B – minimum exhaust rates] | Total cfm driven by people | Total cfm driven by area | Total cfm driven by exhaust | Total cfm | Notes
Lounge, Breakroom, or Waiting Area | ADMIN/MPR_BREAKROOM_ZN | 18.9816 | 575.2 | 15 | 0.15 |  | 284.724 | 86.28 | 0 | 284.724
Dining Area (Cafeteria/Fast Food) | ADMIN/MPR_CAFETERIA ZNS 3_ZN | 181.9023 | 5512.19 | 15 | 0.15 |  | 2728.534 | 826.8285 | 0 | 2728.534
Convention, Conference, Multipurpose and Meeting Area | ADMIN/MPR_CONFERENCE ROOM ZNS 3_ZN | 55.2664 | 1674.74 | 15 | 0.15 |  | 828.9963 | 251.211 | 0 | 828.9963
Corridor Area | ADMIN/MPR_CORRIDOR_ZN | 5.8076 | 1161.52 | 15 | 0.15 |  | 87.114 | 174.228 | 0 | 174.228
Electrical, Mechanical, Telephone Rooms | ADMIN/MPR_EMT_ZN | 1.391 | 278.21 | 15 | 0.15 |  | 20.8657 | 41.7315 | 0 | 41.7315
Electrical, Mechanical, Telephone Rooms | ADMIN/MPR_IDF ROOM_ZN | 1.7012 | 340.23 | 15 | 0.15 |  | 25.5173 | 51.0345 | 0 | 51.0345
Kitchen/Food Preparation Area | ADMIN/MPR_KITCHEN_ZN | 4.3717 | 1457.25 | 15 | 0.15 | 0.7 | 65.5762 | 218.5875 | 1020.075 | 1020.075 | Table 120.1-B commercial kitchen exhaust, 0.70 cfm/ft². This is the kitchen hood rate.
Lobby, Main Entry | ADMIN/MPR_LOBBY_ZN | 40.9685 | 1241.47 | 15 | 0.15 |  | 614.5276 | 186.2205 | 0 | 614.5276
Office Area (<250 square feet) | ADMIN/MPR_OFFICE - LT 250 SF ZNS 6_ZN | 5.2417 | 1048.35 | 15 | 0.15 |  | 78.6262 | 157.2525 | 0 | 157.2525
Restrooms | ADMIN/MPR_RESTROOM ZNS 3_ZN | 4.5058 | 901.17 | 0 | 0 | 0.5 | 0 | 0 | 450.585 | 450.585 | Exhaust 0.50 cfm/ft² on every restroom, same as School K-8.
Storage (General) | ADMIN/MPR_STORAGE - GENERAL_ZN | 6.2386 | 1247.73 | 15 | 0.15 |  | 93.5797 | 187.1595 | 0 | 187.1595
Storage, Commercial/Industrial (Refrigerated) | ADMIN/MPR_STORAGE - REFRIGERATED_ZN | 0 | 251.72 | 0 | 0 |  | 0 | 0 | 0 | 0
Theater Area (Performance) | ADMIN/MPR_THEATER - PERFORMANCE_ZN | 35.1635 | 1065.56 | 15 | 0.15 |  | 527.4522 | 159.834 | 0 | 527.4522
Electrical, Mechanical, Telephone Rooms | CLASSRM LAB_FLR 1_EMT-01_ZN | 0.60505 | 121.01 | 15 | 0.15 |  | 9.0758 | 18.1515 | 0 | 18.1515
Electrical, Mechanical, Telephone Rooms | CLASSRM LAB_FLR 1_EMT-02_ZN | 0.49005 | 98.01 | 15 | 0.15 |  | 7.3507 | 14.7015 | 0 | 14.7015
Laboratory, Scientific | CLASSRM LAB_FLR 1_LAB ZNS 2_ZN | 51.3735 | 2054.94 | 15 | 0.15 | 1 | 770.6025 | 308.241 | 2054.94 | 2054.94 | Table 120.1-B educational science laboratories, 1.00 cfm/ft².
Library (Reading Area) | CLASSRM LAB_FLR 1_LIBRARY - READING AREA_ZN | 11.9713 | 1197.13 | 15 | 0.15 |  | 179.5695 | 179.5695 | 0 | 179.5695
Restrooms | CLASSRM LAB_FLR 1_RESTROOM_ZN | 2.8152 | 563.05 | 0 | 0 | 0.5 | 0 | 0 | 281.525 | 281.525
Storage (General) | CLASSRM LAB_FLR 1_STORAGE - GENERAL_ZN | 1.9042 | 380.84 | 15 | 0.15 |  | 28.563 | 57.126 | 0 | 57.126
Classroom, Lecture, Training, Vocational Areas | CLASSRM LAB_FLR 2_CLASSROOM_ZN | 9.521 | 380.84 | 15 | 0.15 |  | 142.815 | 57.126 | 0 | 142.815
Electrical, Mechanical, Telephone Rooms | CLASSRM LAB_FLR 2_IDF ROOM_ZN | 0.60505 | 121.01 | 15 | 0.15 |  | 9.0758 | 18.1515 | 0 | 18.1515
Laboratory, Scientific | CLASSRM LAB_FLR 2_LAB ZNS 3_ZN | 81.3015 | 3252.06 | 15 | 0.15 | 1 | 1219.5225 | 487.809 | 3252.06 | 3252.06
Restrooms | CLASSRM LAB_FLR 2_RESTROOM_ZN | 2.8152 | 563.05 | 0 | 0 | 0.5 | 0 | 0 | 281.525 | 281.525
Storage (General) | CLASSRM LAB_FLR 2_STORAGE - GENERAL_ZN | 0.49005 | 98.01 | 15 | 0.15 |  | 7.3507 | 14.7015 | 0 | 14.7015
Classroom, Lecture, Training, Vocational Areas | CLASSRM N_FLR 1_CLASSROOM-01_ZN | 25.0437 | 1001.75 | 15 | 0.15 |  | 375.6562 | 150.2625 | 0 | 375.6562
Classroom, Lecture, Training, Vocational Areas | CLASSRM N_FLR 1_CLASSROOM-02 ZNS 6_ZN | 151.3508 | 6054.03 | 15 | 0.15 |  | 2270.2613 | 908.1045 | 0 | 2270.2613
Office Area (<250 square feet) | CLASSRM N_FLR 1_OFFICE - LT 250 SF_ZN | 1.4406 | 288.13 | 15 | 0.15 |  | 21.6097 | 43.2195 | 0 | 43.2195
Restrooms | CLASSRM N_FLR 1_RESTROOM_ZN | 2.6635 | 532.7 | 0 | 0 | 0.5 | 0 | 0 | 266.35 | 266.35
Classroom, Lecture, Training, Vocational Areas | CLASSRM N_FLR 2_CLASSROOM-01 ZNS 6_ZN | 151.3508 | 6054.03 | 15 | 0.15 |  | 2270.2613 | 908.1045 | 0 | 2270.2613
Classroom, Lecture, Training, Vocational Areas | CLASSRM N_FLR 2_CLASSROOM-02_ZN | 25.0437 | 1001.75 | 15 | 0.15 |  | 375.6562 | 150.2625 | 0 | 375.6562
Office Area (<250 square feet) | CLASSRM N_FLR 2_OFFICE - LT 250 SF_ZN | 1.4406 | 288.13 | 15 | 0.15 |  | 21.6097 | 43.2195 | 0 | 43.2195
Restrooms | CLASSRM N_FLR 2_RESTROOM_ZN | 2.6635 | 532.7 | 0 | 0 | 0.5 | 0 | 0 | 266.35 | 266.35
Electrical, Mechanical, Telephone Rooms | CLASSRM SHOP_EMT_ZN | 0.85435 | 170.87 | 15 | 0.15 |  | 12.8153 | 25.6305 | 0 | 25.6305
Electrical, Mechanical, Telephone Rooms | CLASSRM SHOP_IDF ROOM_ZN | 0.4274 | 85.48 | 15 | 0.15 |  | 6.411 | 12.822 | 0 | 12.822
Restrooms | CLASSRM SHOP_RESTROOM_ZN | 1.3301 | 266.03 | 0 | 0 | 0.5 | 0 | 0 | 133.015 | 133.015
Wood/Metal Shop Classroom | CLASSRM SHOP_SHOP-01 ZNS 4_ZN | 54.9454 | 5494.54 | 15 | 0.15 | 0.5 | 824.181 | 824.181 | 2747.27 | 2747.27 | Table 120.1-B woodwork shop/classrooms, 0.50 cfm/ft².
Wood/Metal Shop Classroom | CLASSRM SHOP_SHOP-02_ZN | 14.4014 | 1440.14 | 15 | 0.15 | 0.5 | 216.021 | 216.021 | 720.07 | 720.07
Storage (General) | CLASSRM SHOP_STORAGE - GENERAL_ZN | 5.919 | 1183.8 | 15 | 0.15 |  | 88.785 | 177.57 | 0 | 177.57
Exercise/Fitness Center and Gymnasium Areas | COURTS - AUX ZN | 51.8451 | 5184.51 | 15 | 0.15 |  | 777.6765 | 777.6765 | 0 | 777.6765
Exercise/Fitness Center and Gymnasium Areas | COURTS ZN | 120.9718 | 12097.18 | 15 | 0.15 |  | 1814.577 | 1814.577 | 0 | 1814.577
Locker Room | LOCKERS ZN | 38.1637 | 7632.74 | 15 | 0.15 | 0.5 | 572.4555 | 1144.911 | 3816.37 | 3816.37 | Table 120.1-B locker rooms for athletic facilities, 0.50 cfm/ft².
Exercise/Fitness Center and Gymnasium Areas | ROOMS & STUDIOS ZN | 46.0845 | 4608.45 | 15 | 0.15 |  | 691.2675 | 691.2675 | 0 | 691.2675
| Total (42 spaces) | 1221.3724 | 79502.25 |  |  |  | 18068.6832 | 11383.7745 | 15290.135 | 30208.8092

## Water Heater
Water Heater -SchoolHigh
Vintage | WH Type | Efficiency | Number of WH | Tank Volume (gal) | Tank Loss |  | Note
Existing | Electric | 0.98 | 5 | See plant climate-zone tables, Storage Volume (col F) | See plant climate-zone tables, Standby Loss (col G) | See climate-zone HPWH tables | five various WH
New Construction | HPWH | 4.3 | 5 | See plant climate-zone tables, Storage Volume (col F) | See plant climate-zone tables, Standby Loss (col G) | See climate-zone HPWH tables | five various WH
Peak Hot Water Consumption
Space Name | Baseline WH Type [T24, 2022, Appendix 5.4A , sheet: "2022 SpaceFuncData-Input"] | Total Area (ft²) | Number of People | Hot Water Usage Specification (gal/hr per person) [T24, 2022, Appendix 5.4A , sheet: "2022 SpaceFuncData-Input"] | Peak Hot Water Usage (gal/hr) | Peak Hot Water Usage (gal/min)
ADMIN/MPR_BREAKROOM_ZN | HPWH | 575.2 | 18.9816 | 0.09 | 1.7083 | 0.028472
ADMIN/MPR_CAFETERIA ZNS 3_ZN | HPWH | 5512.19 | 181.9023 | 0.578 | 105.1395 | 1.7523
ADMIN/MPR_CONFERENCE ROOM ZNS 3_ZN | HPWH | 1674.74 | 55.2664 | 0.09 | 4.974 | 0.0829
ADMIN/MPR_CORRIDOR_ZN | HPWH | 1161.52 | 5.8076 | 0 | 0 | 0
ADMIN/MPR_EMT_ZN | HPWH | 278.21 | 1.391 | 0.18 | 0.25039 | 0.0041731
ADMIN/MPR_IDF ROOM_ZN | HPWH | 340.23 | 1.7012 | 0.18 | 0.30621 | 0.0051034
ADMIN/MPR_KITCHEN_ZN | HPWH | 1457.25 | 4.3717 | 0.578 | 2.5269 | 0.042115
ADMIN/MPR_LOBBY_ZN | HPWH | 1241.47 | 40.9685 | 0.09 | 3.6872 | 0.061453
ADMIN/MPR_OFFICE - LT 250 SF ZNS 6_ZN | HPWH | 1048.35 | 5.2417 | 0.18 | 0.94351 | 0.015725
ADMIN/MPR_RESTROOM ZNS 3_ZN | HPWH | 901.17 | 4.5058 | 0 | 0 | 0
ADMIN/MPR_STORAGE - GENERAL_ZN | HPWH | 1247.73 | 6.2386 | 0 | 0 | 0
ADMIN/MPR_STORAGE - REFRIGERATED_ZN | HPWH | 251.72 | 0 | 0.18 | 0 | 0
ADMIN/MPR_THEATER - PERFORMANCE_ZN | HPWH | 1065.56 | 35.1635 | 0.09 | 3.1647 | 0.052745
CLASSRM LAB_FLR 1_EMT-01_ZN | HPWH | 121.01 | 0.60505 | 0.18 | 0.10891 | 0.0018152
CLASSRM LAB_FLR 1_EMT-02_ZN | HPWH | 98.01 | 0.49005 | 0.18 | 0.088209 | 0.0014701
CLASSRM LAB_FLR 1_LAB ZNS 2_ZN | HPWH | 2054.94 | 51.3735 | 0.18 | 9.2472 | 0.15412
CLASSRM LAB_FLR 1_LIBRARY - READING AREA_ZN | HPWH | 1197.13 | 11.9713 | 0.18 | 2.1548 | 0.035914
CLASSRM LAB_FLR 1_RESTROOM_ZN | HPWH | 563.05 | 2.8152 | 0 | 0 | 0
CLASSRM LAB_FLR 1_STORAGE - GENERAL_ZN | HPWH | 380.84 | 1.9042 | 0 | 0 | 0
CLASSRM LAB_FLR 2_CLASSROOM_ZN | HPWH | 380.84 | 9.521 | 0.18 | 1.7138 | 0.028563
CLASSRM LAB_FLR 2_IDF ROOM_ZN | HPWH | 121.01 | 0.60505 | 0.18 | 0.10891 | 0.0018152
CLASSRM LAB_FLR 2_LAB ZNS 3_ZN | HPWH | 3252.06 | 81.3015 | 0.18 | 14.6343 | 0.2439
CLASSRM LAB_FLR 2_RESTROOM_ZN | HPWH | 563.05 | 2.8152 | 0 | 0 | 0
CLASSRM LAB_FLR 2_STORAGE - GENERAL_ZN | HPWH | 98.01 | 0.49005 | 0 | 0 | 0
CLASSRM N_FLR 1_CLASSROOM-01_ZN | HPWH | 1001.75 | 25.0437 | 0.18 | 4.5079 | 0.075131
CLASSRM N_FLR 1_CLASSROOM-02 ZNS 6_ZN | HPWH | 6054.03 | 151.3508 | 0.18 | 27.2431 | 0.45405
CLASSRM N_FLR 1_OFFICE - LT 250 SF_ZN | HPWH | 288.13 | 1.4406 | 0.18 | 0.25932 | 0.0043219
CLASSRM N_FLR 1_RESTROOM_ZN | HPWH | 532.7 | 2.6635 | 0 | 0 | 0
CLASSRM N_FLR 2_CLASSROOM-01 ZNS 6_ZN | HPWH | 6054.03 | 151.3508 | 0.18 | 27.2431 | 0.45405
CLASSRM N_FLR 2_CLASSROOM-02_ZN | HPWH | 1001.75 | 25.0437 | 0.18 | 4.5079 | 0.075131
CLASSRM N_FLR 2_OFFICE - LT 250 SF_ZN | HPWH | 288.13 | 1.4406 | 0.18 | 0.25932 | 0.0043219
CLASSRM N_FLR 2_RESTROOM_ZN | HPWH | 532.7 | 2.6635 | 0 | 0 | 0
CLASSRM SHOP_EMT_ZN | HPWH | 170.87 | 0.85435 | 0.18 | 0.15378 | 0.002563
CLASSRM SHOP_IDF ROOM_ZN | HPWH | 85.48 | 0.4274 | 0.18 | 0.076932 | 0.0012822
CLASSRM SHOP_RESTROOM_ZN | HPWH | 266.03 | 1.3301 | 0 | 0 | 0
CLASSRM SHOP_SHOP-01 ZNS 4_ZN | HPWH | 5494.54 | 54.9454 | 0.18 | 9.8902 | 0.16484
CLASSRM SHOP_SHOP-02_ZN | HPWH | 1440.14 | 14.4014 | 0.18 | 2.5923 | 0.043204
CLASSRM SHOP_STORAGE - GENERAL_ZN | HPWH | 1183.8 | 5.919 | 0 | 0 | 0
COURTS - AUX ZN | HPWH | 5184.51 | 51.8451 | 0.18 | 9.3321 | 0.15554
COURTS ZN | HPWH | 12097.18 | 120.9718 | 0.18 | 21.7749 | 0.36292
LOCKERS ZN | HPWH | 7632.74 | 38.1637 | 0.578 | 22.0586 | 0.36764
ROOMS & STUDIOS ZN | HPWH | 4608.45 | 46.0845 | 0.18 | 8.2952 | 0.13825
Plant peak hot water (gal/hr)
Water Heater Name | WH type | Peak Hot Water Usage (gal/hr) | Notes
HPWH - Admin | HPWH | 122.7007 | Minimum peak hot water usage is 75 gal/hr according to ACM 2025
HPWH - North Classroom | HPWH | 75
HPWH - Lab Classroom | HPWH | 75
HPWH - Shop Classroom | HPWH | 75
HPWH - Sports | HPWH | 75
Design supply temperature (°F) | 135 | Title 24 2022 Reference Appendices, Appendix 5.4B
Design supply temperature used in CZ tables (°F) | 135 | Title 24 2022 Reference Appendices, Appendix 5.4B
WH system factor | 0.6 | 2025 ACM §5.9.2 Rated Capacity
Water mass conversion (lb/gal) | 8.2877 | 2025 ACM §5.9.2 Rated Capacity
Reheat multiplier | 0.4 | 2025 ACM §5.9.2 Storage Volume
Commercial HPWH configuration | Unitary storage HPWH (integrated) | Distributed unitary storage HPWH; retain the High School prototype's 5 water heaters / 5 service-water loops.
Selected commercial COPh | 4.3 | ENERGY STAR Certified Commercial Water Heaters, integrated commercial 119-gal CHP family COPh = 4.3.
ENERGY STAR minimum commercial COPh | 3 | ENERGY STAR commercial electric heat pump water-heater criterion.
Design COPh | 4.3 | Use commercial COPh directly. Residential UEF-to-EF-to-COP conversion removed.
Climate Zone Water Heater Sizing and Loss Coefficients
Water Heater name | Climate Zone | Minimum Monthly Mains Temp (°F) [T24 2022 - Appendix 5.4B] | Heat Output (Btu/hr) [ACM, 2025, 5.9.2: Rated capacity section] | WH Capacity (Btu/hr) [ACM, 2025, 5.9.2: Rated capacity section] | Required Electric Input (Btu/hr) [WH Capacity ÷ commercial COPh] | Storage Volume (gal) [prototype unitary-storage sizing bin] | Standby Loss (%/hr) [derived from DEER HPWH UA = 4.37 Btu/h·°F] |  | Off/On Cycle Loss Coefficient to Ambient Temp [DEER HPWH UA] |  | Source / Method Note
HPWH - Admin | CZ01 | 47.9 | 88572.5608 | 53143.5365 | 12358.962 | 50 | 1.048 | %/hr | 4.37 | Btu/h·°F | Approach: distributed unitary storage HPWH. Retain one plant per existing service-water loop on this prototype (5 plants). Efficiency: commercial COPh = 4.3 from ENERGY STAR certified integrated commercial HPWH. Electric input = WH Capacity / COPh. Tank UA = 4.37 Btu/h·°F (DEER commercial HPWH). Standby Loss (%/hr) = UA / (0.0834 × Storage Volume).
HPWH - Admin | CZ02 | 50.8 | 85623.5318 | 51374.1191 | 11947.4696 | 50 | 1.048 | %/hr | 4.37 | Btu/h·°F
HPWH - Admin | CZ03 | 52.2 | 84199.8627 | 50519.9176 | 11748.818 | 50 | 1.048 | %/hr | 4.37 | Btu/h·°F
HPWH - Admin | CZ04 | 52.7 | 83691.4094 | 50214.8456 | 11677.8711 | 50 | 1.048 | %/hr | 4.37 | Btu/h·°F
HPWH - Admin | CZ05 | 51.6 | 84810.0066 | 50886.004 | 11833.9544 | 50 | 1.048 | %/hr | 4.37 | Btu/h·°F
HPWH - Admin | CZ06 | 56.8 | 79522.0925 | 47713.2555 | 11096.1059 | 50 | 1.048 | %/hr | 4.37 | Btu/h·°F
HPWH - Admin | CZ07 | 58.4 | 77895.042 | 46737.0252 | 10869.0756 | 50 | 1.048 | %/hr | 4.37 | Btu/h·°F
HPWH - Admin | CZ08 | 58.4 | 77895.042 | 46737.0252 | 10869.0756 | 50 | 1.048 | %/hr | 4.37 | Btu/h·°F
HPWH - Admin | CZ09 | 57.6 | 78708.5673 | 47225.1404 | 10982.5908 | 50 | 1.048 | %/hr | 4.37 | Btu/h·°F
HPWH - Admin | CZ10 | 57.1 | 79217.0205 | 47530.2123 | 11053.5377 | 50 | 1.048 | %/hr | 4.37 | Btu/h·°F
HPWH - Admin | CZ11 | 50.5 | 85928.6038 | 51557.1623 | 11990.0377 | 50 | 1.048 | %/hr | 4.37 | Btu/h·°F
HPWH - Admin | CZ12 | 51.4 | 85013.3879 | 51008.0327 | 11862.3332 | 50 | 1.048 | %/hr | 4.37 | Btu/h·°F
HPWH - Admin | CZ13 | 51.7 | 84708.3159 | 50824.9896 | 11819.765 | 50 | 1.048 | %/hr | 4.37 | Btu/h·°F
HPWH - Admin | CZ14 | 50.1 | 86335.3664 | 51801.2198 | 12046.7953 | 50 | 1.048 | %/hr | 4.37 | Btu/h·°F
HPWH - Admin | CZ15 | 63.2 | 73013.8906 | 43808.3343 | 10187.9847 | 50 | 1.048 | %/hr | 4.37 | Btu/h·°F
HPWH - Admin | CZ16 | 41.4 | 95182.4534 | 57109.4721 | 13281.2726 | 50 | 1.048 | %/hr | 4.37 | Btu/h·°F
HPWH - North Classrooms | CZ01 | 47.9 | 54139.4002 | 32483.6401 | 7554.3349 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F | Same DEER HPWH UA method as the Admin plant table. Peak cell $F$57.
HPWH - North Classrooms | CZ02 | 50.8 | 52336.8255 | 31402.0953 | 7302.8129 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F
HPWH - North Classrooms | CZ03 | 52.2 | 51466.617 | 30879.9702 | 7181.3884 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F
HPWH - North Classrooms | CZ04 | 52.7 | 51155.8282 | 30693.4969 | 7138.0225 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F
HPWH - North Classrooms | CZ05 | 51.6 | 51839.5635 | 31103.7381 | 7233.4275 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F
HPWH - North Classrooms | CZ06 | 56.8 | 48607.3605 | 29164.4163 | 6782.4224 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F
HPWH - North Classrooms | CZ07 | 58.4 | 47612.8365 | 28567.7019 | 6643.6516 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F
HPWH - North Classrooms | CZ08 | 58.4 | 47612.8365 | 28567.7019 | 6643.6516 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F
HPWH - North Classrooms | CZ09 | 57.6 | 48110.0985 | 28866.0591 | 6713.037 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F
HPWH - North Classrooms | CZ10 | 57.1 | 48420.8872 | 29052.5323 | 6756.4029 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F
HPWH - North Classrooms | CZ11 | 50.5 | 52523.2987 | 31513.9792 | 7328.8324 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F
HPWH - North Classrooms | CZ12 | 51.4 | 51963.879 | 31178.3274 | 7250.7738 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F
HPWH - North Classrooms | CZ13 | 51.7 | 51777.4057 | 31066.4434 | 7224.7543 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F
HPWH - North Classrooms | CZ14 | 50.1 | 52771.9297 | 31663.1578 | 7363.5251 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F
HPWH - North Classrooms | CZ15 | 63.2 | 44629.2645 | 26777.5587 | 6227.3392 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F
HPWH - North Classrooms | CZ16 | 41.4 | 58179.654 | 34907.7924 | 8118.0913 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F
HPWH - Lab Classrooms | CZ01 | 47.9 | 54139.4002 | 32483.6401 | 7554.3349 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F | Same DEER HPWH UA method as the Admin plant table. Peak cell $F$58.
HPWH - Lab Classrooms | CZ02 | 50.8 | 52336.8255 | 31402.0953 | 7302.8129 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F
HPWH - Lab Classrooms | CZ03 | 52.2 | 51466.617 | 30879.9702 | 7181.3884 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F
HPWH - Lab Classrooms | CZ04 | 52.7 | 51155.8282 | 30693.4969 | 7138.0225 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F
HPWH - Lab Classrooms | CZ05 | 51.6 | 51839.5635 | 31103.7381 | 7233.4275 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F
HPWH - Lab Classrooms | CZ06 | 56.8 | 48607.3605 | 29164.4163 | 6782.4224 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F
HPWH - Lab Classrooms | CZ07 | 58.4 | 47612.8365 | 28567.7019 | 6643.6516 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F
HPWH - Lab Classrooms | CZ08 | 58.4 | 47612.8365 | 28567.7019 | 6643.6516 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F
HPWH - Lab Classrooms | CZ09 | 57.6 | 48110.0985 | 28866.0591 | 6713.037 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F
HPWH - Lab Classrooms | CZ10 | 57.1 | 48420.8872 | 29052.5323 | 6756.4029 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F
HPWH - Lab Classrooms | CZ11 | 50.5 | 52523.2987 | 31513.9792 | 7328.8324 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F
HPWH - Lab Classrooms | CZ12 | 51.4 | 51963.879 | 31178.3274 | 7250.7738 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F
HPWH - Lab Classrooms | CZ13 | 51.7 | 51777.4057 | 31066.4434 | 7224.7543 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F
HPWH - Lab Classrooms | CZ14 | 50.1 | 52771.9297 | 31663.1578 | 7363.5251 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F
HPWH - Lab Classrooms | CZ15 | 63.2 | 44629.2645 | 26777.5587 | 6227.3392 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F
HPWH - Lab Classrooms | CZ16 | 41.4 | 58179.654 | 34907.7924 | 8118.0913 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F
HPWH - Shop Classrooms | CZ01 | 47.9 | 54139.4002 | 32483.6401 | 7554.3349 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F | Same DEER HPWH UA method as the Admin plant table. Peak cell $F$59.
HPWH - Shop Classrooms | CZ02 | 50.8 | 52336.8255 | 31402.0953 | 7302.8129 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F
HPWH - Shop Classrooms | CZ03 | 52.2 | 51466.617 | 30879.9702 | 7181.3884 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F
HPWH - Shop Classrooms | CZ04 | 52.7 | 51155.8282 | 30693.4969 | 7138.0225 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F
HPWH - Shop Classrooms | CZ05 | 51.6 | 51839.5635 | 31103.7381 | 7233.4275 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F
HPWH - Shop Classrooms | CZ06 | 56.8 | 48607.3605 | 29164.4163 | 6782.4224 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F
HPWH - Shop Classrooms | CZ07 | 58.4 | 47612.8365 | 28567.7019 | 6643.6516 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F
HPWH - Shop Classrooms | CZ08 | 58.4 | 47612.8365 | 28567.7019 | 6643.6516 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F
HPWH - Shop Classrooms | CZ09 | 57.6 | 48110.0985 | 28866.0591 | 6713.037 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F
HPWH - Shop Classrooms | CZ10 | 57.1 | 48420.8872 | 29052.5323 | 6756.4029 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F
HPWH - Shop Classrooms | CZ11 | 50.5 | 52523.2987 | 31513.9792 | 7328.8324 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F
HPWH - Shop Classrooms | CZ12 | 51.4 | 51963.879 | 31178.3274 | 7250.7738 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F
HPWH - Shop Classrooms | CZ13 | 51.7 | 51777.4057 | 31066.4434 | 7224.7543 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F
HPWH - Shop Classrooms | CZ14 | 50.1 | 52771.9297 | 31663.1578 | 7363.5251 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F
HPWH - Shop Classrooms | CZ15 | 63.2 | 44629.2645 | 26777.5587 | 6227.3392 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F
HPWH - Shop Classrooms | CZ16 | 41.4 | 58179.654 | 34907.7924 | 8118.0913 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F
HPWH - Sports | CZ01 | 47.9 | 54139.4002 | 32483.6401 | 7554.3349 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F | Same DEER HPWH UA method as the Admin plant table. Peak cell $F$60.
HPWH - Sports | CZ02 | 50.8 | 52336.8255 | 31402.0953 | 7302.8129 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F
HPWH - Sports | CZ03 | 52.2 | 51466.617 | 30879.9702 | 7181.3884 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F
HPWH - Sports | CZ04 | 52.7 | 51155.8282 | 30693.4969 | 7138.0225 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F
HPWH - Sports | CZ05 | 51.6 | 51839.5635 | 31103.7381 | 7233.4275 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F
HPWH - Sports | CZ06 | 56.8 | 48607.3605 | 29164.4163 | 6782.4224 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F
HPWH - Sports | CZ07 | 58.4 | 47612.8365 | 28567.7019 | 6643.6516 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F
HPWH - Sports | CZ08 | 58.4 | 47612.8365 | 28567.7019 | 6643.6516 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F
HPWH - Sports | CZ09 | 57.6 | 48110.0985 | 28866.0591 | 6713.037 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F
HPWH - Sports | CZ10 | 57.1 | 48420.8872 | 29052.5323 | 6756.4029 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F
HPWH - Sports | CZ11 | 50.5 | 52523.2987 | 31513.9792 | 7328.8324 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F
HPWH - Sports | CZ12 | 51.4 | 51963.879 | 31178.3274 | 7250.7738 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F
HPWH - Sports | CZ13 | 51.7 | 51777.4057 | 31066.4434 | 7224.7543 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F
HPWH - Sports | CZ14 | 50.1 | 52771.9297 | 31663.1578 | 7363.5251 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F
HPWH - Sports | CZ15 | 63.2 | 44629.2645 | 26777.5587 | 6227.3392 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F
HPWH - Sports | CZ16 | 41.4 | 58179.654 | 34907.7924 | 8118.0913 | 40 | 1.31 | %/hr | 4.37 | Btu/h·°F
Market data — integrated HPWH
Catalog tank (gal) | Tank source | Heating output (Btu/h) | Output source
40 | ENERGY STAR | 14000 | ENERGY STAR integrated HPWH
50 | ENERGY STAR | 16000 | ENERGY STAR integrated HPWH
66 | ENERGY STAR | 18000 | ENERGY STAR integrated HPWH
80 | ENERGY STAR | 20000 | ENERGY STAR integrated HPWH
120 | ENERGY STAR | 25000 | ENERGY STAR integrated HPWH

## Interior Lights
Interior Lighting - SchoolHigh
Space Type | New Construction |  |  | Existing
| Lighting density (W/ft²) | Additional lighting power for porTable lighting (W/ft²) | Source | LPD (W/ft²) | Additional LPD for PorTable Lighting (W/ft²) | Source
Lounge, Breakroom, or Waiting Area | 0.55 | 0.25 | T24, 2025, Table 140.6 C (Area category method) | 0.9 | 0.25 | T24, 2016, Table 140.6 C (Area category method)
Dining Area (Cafeteria/Fast Food) | 0.45 |  |  | 1
Convention, Conference, Multipurpose and Meeting Area | 0.75 | 0.25 |  | 1.2 | 0.2
Corridor Area | 0.4 |  |  | 0.6
Electrical, Mechanical, Telephone Rooms | 0.4 |  |  | 0.55
Kitchen/Food Preparation Area | 0.95 |  |  | 1.2
Restrooms | 0.65 |  |  | 0.6
Lobby, Main Entry | 0.7 | 0.25 |  | 0.95 | 0.2
Office Area (<250 square feet) | 0.65 | 0.2 |  | 1 | 0.2
Storage (General) | 0.4 |  |  | 0.6
Storage, Commercial/Industrial (Refrigerated) | 0.4 |  |  | 0.7
Theater Area (Performance) | 0.8 |  |  | 1.4
Laboratory, Scientific | 0.9 | 0.35 |  | 1.4 | 0.2
Library (Reading Area) | 0.8 |  |  | 1.1
Classroom, Lecture, Training, Vocational Areas | 0.6 |  |  | 1.2
Wood/Metal Shop Classroom | 0.6 |  |  | 1.2
Locker Room | 0.45 |  |  | 0.8
Exercise/Fitness Center and Gymnasium Areas | 0.5 |  |  | 1
Exercise/Fitness Center and Gymnasium Areas | 0.5 |  |  | 1

## Ext Lighting
Exterior Lighting - SchoolHigh
Motion Controlled Luminaires (W) | Non-motion Controlled Luminaires (W) | Total (W) | Source
4040.6229 | 7440.8933 | 11481.5162 | T24, 2022 & 2025 2019 Outdoor Lighting CASE report PNNL 90.1-2010 TSD
Exterior Lighting
Items (Assume LZ2) | Assumptions [2019 Outdoor Lighting CASE Report & PNNL 90.1-2010 TS] |  | Unit | Lighting Power Allowance [T24, 2025, Table 140.7-A & 140.7-B] | Unit | Exterior Lighting Power (W)
IWA (Initial Wattage Allowance) |  |  |  | 200 | (W) | 200
Parking area | 400 ft² for every parking space 1 parking space per 360 ft² of gross building area | 194243.3111 | (ft²) | 0.019 | (W/ft²) | 3690.6229
Building Entrance | Two required exits per building (5 buildings). Exterior classroom access | 10 | (count) | 15 | (W/ea) | 150
Hardscape Ornamental Light | Hardscape ornamental: 0.1 ft² per 1 ft² GFA, then 25% of that area | 4370.4745 | (ft²) | 0.007 | (W/ft²) | 30.5933
Building façade | 0.1 W per 1 ft² of facade area Façade Area = Perimeter × 0.25 × max ( height and 34) (34 ft is the max height that is lit) * The 0.25 factor assumes that only half of the perimeter walls are lit. -Formula ia developed based on the 2019 Outdoor Lighting CASE report | 72103 | (ft²) | 0.1 | (W/ft²) | 7210.3
Student pickup / drop-off (walkway) | Allowance: walkway LPD on assumed 4,000 ft² loading loop (site program does not list a separate canopy). T24 2025 Table 140.7-B walkways. |  |  |  |  | 200
Motion Controlled Luminaires (W) | [5 empty] | 4040.6229
Non-motion-controlled Luminaires | [5 empty] | 7440.8933
Total | [5 empty] | 11481.5162
| North Classroom | Lab Classroom | Shop Classroom | MPR/Admin | Gym / Courts / Locker
Perimeter of each buildings (ft) | 537 | 327 | 474 | 563 | 800
Max Height that is lit for each buildings (ft) | 28 | 28 | 14 | 25 | 34
Each building footprint | 7876 | 4415 | 8640 | 16754 | 29523
Floors | 2 | 2 | 1 | 1 | 1
Floor area of each building (ft²) | 72139.16 | 8829.95 | 0 | 55686.18 | 29522.88
Wall area of each building (ft²) | 15036 | 9156 | 6636 | 14075 | 27200
Total Perimeter (ft) | 2701
Total floor area (ft²) | 174818.98

## Equipment
Equipment - SchoolHigh
Space Type | Plug load Power Density (W/ft²) | Gas Power Density (Btu/hr-ft²) | Refrigeration Power Density (W/ft²) | Source
Lounge, Breakroom, or Waiting Area | 1 | 0 | 0 | T24 2022 / current NRMFACM Appendix 5.4A
Dining Area (Cafeteria/Fast Food) | 0.5 | 0 | 0.25
Convention, Conference, Multipurpose and Meeting Area | 1 | 0 | 0
Corridor Area | 0 | 0 | 0
Electrical, Mechanical, Telephone Rooms | 3 | 0 | 0 | Plug 3.0 W/ft² — T24 2022 Appendix 5.4A. Gas 0 and refrigeration 0 per Appendix 5.4A.
Kitchen/Food Preparation Area | 1.5 | 17.5377 | 1.12 | Plug 1.5 W/ft²; gas 17.54 Btu/h-ft²; refrigeration 1.12 W/ft² — all T24 2022 Appendix 5.4A (ACM 2025 table unchanged). Not from the Plug Loads and Schedules project.
Restrooms | 0.5 | 0 | 0 | Plug load and schedules project with CEC, 2025
Lobby, Main Entry | 0.7 | 0 | 0 | T24 2022 / current NRMFACM Appendix 5.4A
Office Area (<250 square feet) | 0.7 | 0 | 0 | Plug 0.7 W/ft² — Plug Loads and Schedules project with CEC, 2025 (Appendix 5.4A office ≤250 ft² is 1.5 W/ft²). Gas 0 and refrigeration 0 — Appendix 5.4A has no process gas or commercial refrigeration for this space.
Storage (General) | 0.2 | 0 | 0 | T24 2022 / current NRMFACM Appendix 5.4A
Storage, Commercial/Industrial (Refrigerated) | 0.2 | 0 | 10
Theater Area (Performance) | 0.5 | 0 | 0
Laboratory, Scientific | 1.5 | 0 | 0
Library (Reading Area) | 1.5 | 0 | 0
Classroom, Lecture, Training, Vocational Areas | 0.8 | 0 | 0
Wood/Metal Shop Classroom | 1 | 0 | 0
Locker Room | 0.5
Exercise/Fitness Center and Gymnasium Areas | 0.5 | 0 | 0
Exercise/Fitness Center and Gymnasium Areas | 0.5 | 0 | 0
Elevator
Vintage | Class | Number of elevators (ne) | Cab Lighting Power Limit (W/ft2) | Fan Power Limit (W/CFM) | Cab Ventilation Fan & Lighting Shutoff | Design Motor Load (W) | Fan Load (W) | Lighting Load (W) | Total (W) | Note
Existing | F/G | 2 | 1.14 | 0.33 | When stopped and unoccupied with doors closed for over 15 minutes, cab interior lighting and ventilation shall be de-energized until required for operation. | 6379.25 | 165 | 68.17 | 6612.42 | Design load is calculated according to ISO 25745-2 method using Class F/G. Cab lighting and fan requirements are based on ASHRAE 90.1 2013.
New Construction | E | 2 | 0.6 | 0.33 | When the elevator cab is stopped and unoccupied with doors closed for over 15 minutes, the cab interior lighting and ventilation fans shall be switched off until elevator cab operation resumes. | 3329.02 | 165 | 35.88 | 3529.9 | Design load is calculated according to ISO 25745-2 method using Class E. Cab lighting and fan requirements are based on T24 2025 §120.6 (f).
Elevator count (C25:C26 = 2) is one elevator per two-story classroom building (North Classroom and Lab) from the CEC SchoolHigh layout. F24 is the cab lighting/ventilation shutoff requirement, not a count source.
School High Elevator Calculations
Symbol | Definition | Value | Units | Source
E | Annual energy consumption of the elevator - Existing | 31634.71 | kWh/year | Calculated
| Annual energy consumption of the elevator - New Construction | 16508.63 | kWh/year | Calculated
C1 | Running-energy coefficient | 3.65 for Class E; 5.47 for Class F | Coefficient | ISO 25745-2 Table 7
C2 | Idle/standby coefficient | 800 for Class E; 1,600 for Class F | Coefficient | ISO 25745-2 Table 7
Q | Rated load of elevator | 1361 | kg | Assumed for all prototypes
Elevator Size | Cab floor area | 29.9 | ft^2 | W=6.781 ft, L=4.406 ft; assumed based on representative manufacturer
CFM | Cab fan airflow | 250 | cfm | Assumed for multifamily and commercial prototypes
cat | Usage category | 2 | - | ISO 25745-2 Table A.1
d | Operating days per year | 260 | days/year | ISO 25745-2 Table A.1
nf | Number of floors | 2 | floors | Prototype assumptions
h | Floor-to-floor height | 4.27 | m | Prototype assumptions
v | Elevator lift speed | 1 | m/s | ISO 25745-2 Table A.1
nd | Number of trips per day | 125 | trips/day | ISO 25745-2 Table A.1
S_pct | Percent of average travel distance | 1 | % | ISO 25745-2 Table 2
a | Acceleration | 1 | m/s^2 | Annex B of ISO 25745-2
j | Jerk | 1.25 | m/s^3 | Annex B of ISO 25745-2
td | Door time | 8 | seconds | Annex B of ISO 25745-2
S_av | Average distance traveled per trip | 8.54 | m/trip | Calculated (nf * h * S_pct)
t_av | Average trip time | 18.34 | seconds/trip | Calculated (S_av/v + v/a + a/j + td)
t_nr | Time not running per day | 23.36 | hours/day | Calculated (24 - nd * t_av)
Standby Hours | Annual standby hours | 8594.43 | hours/year | Calculated (24*(365-d)+t_nr*d)
Total light level | Total light level | 40 | lm/ft2 | PNNL Prototypes
EFLH | Equivalent full load hours | 4959 | hours | Calculated using the elevator schedule

## Schedules
Schedules - SchoolHigh
Zone | Schedule Category | Schedule | Source | Type | Hour
[5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
School Zones | Classroom | Occupancy | T24 2022 - Appendix 5.4B [School] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.75 | 0.9 | 0.9 | 0.8 | 0.8 | 0.8 | 0.8 | 0.45 | 0.15 | 0.05 | 0.15 | 0.2 | 0.2 | 0.1 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School Zones | Classroom | Lights | T24 2022 - Appendix 5.4B [School] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.6 | 0.65 | 0.65 | 0.65 | 0.55 | 0.55 | 0.55 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.3 | 0.05 | 0.05
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
School Zones | Classroom | ElecEquipment | T24 2022 - Appendix 5.4B [School] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.85 | 0.95 | 0.95 | 0.95 | 0.8 | 0.8 | 0.8 | 0.7 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.3 | 0.05 | 0.05
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
School Zones | Classroom | ServiceHotWater | T24 2022 - Appendix 5.4B [School] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09
|  |  |  | Saturday | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
|  |  |  | Sunday | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
School Zones | Classroom | GasEquipment | T24 2022 - Appendix 5.4B [School] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.75 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School Zones | Classroom | Refrigeration | T24 2022 - Appendix 5.4B [School] | Weekday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Saturday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Sunday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
School Zones | Classroom | HVACAvail | T24 2022 - Appendix 5.4B [School] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School Zones | Classroom | HtgSetpt | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 60 | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 60 | 60
|  |  |  | Saturday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  |  | Sunday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
School Zones | Classroom | ClgSetpt | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 85 | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 85 | 85
|  |  |  | Saturday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
|  |  |  | Sunday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
School Zones | Classroom | Infiltration | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
Kitchen |  | Other
Kitchen Zone | Kitchen | Occupancy | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitchen Zone | Kitchen | HVACAvail | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitchen Zone | Kitchen | Lights | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitchen Zone | Kitchen | ElecEquipment | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.3 | 0.9 | 0.9 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.7 | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitchen Zone | Kitchen | HtgSetpt | T24 2022 - Appendix 5.4B (school kitchen occupied 70/75; not commercial restaurant 66–79) | Weekday | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  |  | Saturday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  |  | Sunday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Kitchen Zone | Kitchen | ClgSetpt | T24 2022 - Appendix 5.4B (school kitchen occupied 70/75; not commercial restaurant 66–79) | Weekday | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
|  |  |  | Saturday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
|  |  |  | Sunday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
Kitchen Zone | Kitchen | OAControl | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitchen Zone | Kitchen | Che | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
Kitchen Zone | Kitchen | Refrigeration | T24 2022 - Appendix 5.4B [School] | Weekday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Saturday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Sunday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
Kitchen Zone | Kitchen | GasEquipment | T24 2022 - Appendix 5.4B [School] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.75 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitchen Zone | Kitchen | ServiceHotWater | T24 2022 - Appendix 5.4B [School] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09
|  |  |  | Saturday | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
|  |  |  | Sunday | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
MPR |  | Other
MPR Zone | MPR | Occupancy | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.5 | 0.25 | 0.25 | 0.05 | 0.25 | 0.95 | 0.95 | 0.25 | 0.2 | 0.2 | 0.2 | 0.15 | 0.15 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MPR Zone | MPR | HVACAvail | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MPR Zone | MPR | Lights | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MPR Zone | MPR | ElecEquipment | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.3 | 0.9 | 0.9 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.7 | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MPR Zone | MPR | HtgSetpt | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 60 | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 60 | 60 | 60 | 60
|  |  |  | Saturday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 60 | 60 | 60 | 60 | 60 | 60
|  |  |  | Sunday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
MPR Zone | MPR | ClgSetpt | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 85 | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 85 | 85 | 85 | 85
|  |  |  | Saturday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 85 | 85 | 85 | 85 | 85 | 85
|  |  |  | Sunday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
MPR Zone | MPR | OAControl | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MPR Zone | MPR | Infiltration | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
MPR Zone | MPR | Refrigeration | T24 2022 - Appendix 5.4B [School] | Weekday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Saturday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Sunday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
MPR Zone | MPR | ServiceHotWater | T24 2022 - Appendix 5.4B [School] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09
|  |  |  | Saturday | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
|  |  |  | Sunday | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
Gym |  | Other
Gym Zone | Gym | Occupancy | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Unoccupied | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Practice WD - Winter | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.02 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.01 | 0 | 0 | 0
|  |  |  | Practice WD - Fall & Spring | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.125 | 0.125 | 0.125 | 0.125 | 0.125 | 0.02 | 0.125 | 0.125 | 0.125 | 0.125 | 0.125 | 0.125 | 0.125 | 0.01 | 0 | 0 | 0
|  |  |  | Game day WD - Winter | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0375 | 0.25 | 0.25 | 0.25 | 0.25 | 0.02 | 0.25 | 0.25 | 0.01 | 0.01 | 0.05 | 0.5 | 0.5 | 0.95 | 0.95 | 0.05 | 0
|  |  |  | Game day WD - Fall & Spring | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01875 | 0.125 | 0.125 | 0.125 | 0.125 | 0.02 | 0.125 | 0.125 | 0.01 | 0.01 | 0.025 | 0.25 | 0.25 | 0.5 | 0.5 | 0.025 | 0
|  |  |  | All WE - Winter | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | All WE - Fall & Spring | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.025 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Summer Camp | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
Gym Zone | Gym | HVACAvail | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Unoccupied | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Practice WD - Winter | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
|  |  |  | Practice WD - Fall & Spring | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
|  |  |  | Game day WD - Winter | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0
|  |  |  | Game day WD - Fall & Spring | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0
|  |  |  | All WE - Winter | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | All WE - Fall & Spring | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Summer Camp | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Gym Zone | Gym | Lights | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Unoccupied | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Practice WD - Winter | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
|  |  |  | Practice WD - Fall & Spring | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
|  |  |  | Game day WD - Winter | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0
|  |  |  | Game day WD - Fall & Spring | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0
|  |  |  | All WE - Winter | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | All WE - Fall & Spring | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Summer Camp | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Gym Zone | Gym | ElecEquipment | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Unoccupied | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
|  |  |  | Practice WD - Winter | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.2 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.2 | 0.15 | 0.15 | 0.15
|  |  |  | Practice WD - Fall & Spring | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.2 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.2 | 0.15 | 0.15 | 0.15
|  |  |  | Game day WD - Winter | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.75 | 0.75 | 0.75 | 0.75 | 0.2 | 0.75 | 0.75 | 0.15 | 0.15 | 0.2 | 0.75 | 0.75 | 0.95 | 0.95 | 0.2 | 0.15
|  |  |  | Game day WD - Fall & Spring | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.75 | 0.75 | 0.75 | 0.75 | 0.2 | 0.75 | 0.75 | 0.15 | 0.15 | 0.2 | 0.75 | 0.75 | 0.75 | 0.75 | 0.2 | 0.15
|  |  |  | All WE - Winter | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
|  |  |  | All WE - Fall & Spring | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
|  |  |  | Summer Camp | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
Gym Zone | Gym | HtgSetpt | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  |  | Saturday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  |  | Sunday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 60 | 60 | 60 | 60 | 60 | 60
Gym Zone | Gym | ClgSetpt | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
|  |  |  | Saturday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
|  |  |  | Sunday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 85 | 85 | 85 | 85 | 85 | 85
Gym Zone | Gym | OAControl | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gym Zone | Gym | Infiltration | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
Gym Zone | Gym | Refrigeration | T24 2022 - Appendix 5.4B [School] | Weekday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Saturday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Sunday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
Gym Zone | Gym | ServiceHotWater | T24 2022 - Appendix 5.4B [School] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09
|  |  |  | Saturday | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
|  |  |  | Sunday | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
Other |  | Other | [26 empty] | EFLH
| Building | Elevator | T24 2022 Appendix 5.4B [School]. Updated based on Plug load and schedules project with CEC, 2025 (no public link yet; ASHRAE paper submitted — update when published or when ACM 2028 is released). | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 4959
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Building | ExtLightingNonMotionCtrl |  | Weekday | bar: Hour 1 to Hour 24
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
| Building | ExtLightingMotionCtrl |  | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Auditorium | Building | PerformanceSpcPeopleActivityLevel | Based on Activilty level schedules in CEC Prototypes | Weekday | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6
|  |  |  | Saturday | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6
|  |  |  | Sunday | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6
Gym | Building | GymPeopleActivityLevel | Based on Activilty level schedules in CEC Prototypes Updated based on the Plug Loads project | Unoccupied | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Practice WD - Winter | 0 | 0 | 0 | 0 | 0 | 0 | 331.1703 | 331.1703 | 331.1703 | 331.1703 | 331.1703 | 331.1703 | 331.1703 | 331.1703 | 331.1703 | 331.1703 | 331.1703 | 331.1703 | 331.1703 | 331.1703 | 331.1703 | 0 | 0 | 0
|  |  |  | Practice WD - Fall & Spring | 0 | 0 | 0 | 0 | 0 | 0 | 331.1703 | 331.1703 | 331.1703 | 331.1703 | 331.1703 | 331.1703 | 331.1703 | 331.1703 | 331.1703 | 331.1703 | 331.1703 | 331.1703 | 331.1703 | 331.1703 | 331.1703 | 0 | 0 | 0
|  |  |  | Game day WD - Winter | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 331.1703 | 331.1703 | 331.1703 | 331.1703 | 331.1703 | 331.1703 | 331.1703 | 331.1703 | 0 | 0 | 331.1703 | 331.1703 | 331.1703 | 331.1703 | 331.1703 | 331.1703 | 0
|  |  |  | Game day WD - Fall & Spring | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 331.1703 | 331.1703 | 331.1703 | 331.1703 | 331.1703 | 331.1703 | 331.1703 | 331.1703 | 0 | 0 | 331.1703 | 331.1703 | 331.1703 | 331.1703 | 331.1703 | 331.1703 | 0
|  |  |  | All WE - Winter | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 331.1703 | 331.1703 | 331.1703 | 331.1703 | 331.1703 | 331.1703 | 331.1703 | 331.1703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | All WE - Fall & Spring | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 331.1703 | 331.1703 | 331.1703 | 331.1703 | 331.1703 | 331.1703 | 331.1703 | 331.1703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Summer Camp | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 331.1703 | 331.1703 | 331.1703 | 331.1703 | 331.1703 | 331.1703 | 331.1703 | 331.1703 | 331.1703 | 331.1703 | 331.1703 | 0 | 0 | 0 | 0 | 0 | 0
Restroom, Coridor, Lobby, Mechanical RM, Lounge, Storage, Theater | Building | CommonAreaPeopleActivityLevel | Based on Activilty level schedules in CEC Prototypes | Weekday | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5
|  |  |  | Saturday | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5
|  |  |  | Sunday | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5
Classroom | Building | MeetingPeopleActivityLevel | Based on Activilty level schedules in CEC Prototypes | Weekday | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2
|  |  |  | Saturday | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2
|  |  |  | Sunday | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2
DiningArea | Building | DiningAreaPeopleActivityLevel | Based on Activilty level schedules in CEC Prototypes | Weekday | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2
|  |  |  | Saturday | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2
|  |  |  | Sunday | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2
Library, office, MultiMeetingRm | Building | FunctionalAreaPeopleActivityLevel | Based on Activilty level schedules in CEC Prototypes and assumed spaces for Basement | Weekday | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
|  |  |  | Saturday | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
|  |  |  | Sunday | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
RefStorage | Building | RefStoragePeopleActivityLevel | Based on Activilty level schedules in CEC Prototypes | Weekday | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8
|  |  |  | Saturday | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8
|  |  |  | Sunday | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8
Refrigerated storage (walk-in) |  | Other
Refrigerated storage zone | Admin/MPR_Storage - Refrigerated | HVACAvail | T24 2025 §100.1 cooler: ≥28°F and <55°F. Engineering judgment, medium-temp. Compressor available every hour | Weekday | bar: Hour 1 to Hour 24
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
Refrigerated storage zone | Admin/MPR_Storage - Refrigerated | HtgSetpt | T24 2025 §100.1 cooler: ≥28°F and <55°F. Engineering judgment, medium-temp. Compressor available every hour | Weekday | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
|  |  |  | Saturday | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
|  |  |  | Sunday | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Refrigerated storage zone | Admin/MPR_Storage - Refrigerated | ClgSetpt | T24 2025 §100.1 cooler: ≥28°F and <55°F. Engineering judgment, medium-temp. Compressor available every hour | Weekday | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
|  |  |  | Saturday | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
|  |  |  | Sunday | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35

## Energy Usage (hidden)
CalBEM Energy Consumption - High School | [11 empty] | Energy Consumption - SchoolHigh
Prototype | CZ | CalBEM Electricity EUI (KBTU/ft²) | CalBEM Gas EUI (KBTU/ft²) | CalBEM Total EUI (KBTU/ft²) | New Construction Electricity EUI (KBTU/ft²) | New Construction Gas EUI (KBTU/ft²) | New Construction Total EUI (KBTU/ft²) | National Average | Acceptable Range (25% Higher) | Acceptable Range (25% Lower) | National Average Acceptable EUI Range | Prototype | CZ | Total Floorspace (Thousand of ft²) | CEUS 2023 Electricity EUI (kBtu/ft²) | CEUS 2023 Gas EUI (kBtu/ft²) | CEUS 2023 Total EUI (kBtu/ft²) | Acceptable Range (25% Higher) | Acceptable Range (25% Lower) | CEUS 2022 Acceptable EUI Range
High School | 1 | [6 empty] | 38.7 | 48.375 | 29.025 | 19.35 | High School | 1 | 7618.5337 | 32.3492 | 12.8481 | 55.3648 | 69.206 | 41.5236 | 27.6824
| 2 | [6 empty] | 34.3 | 42.875 | 25.725 | 17.15 |  | 2 | 11477.6706 | 15.4216 | 12.914 | 47.8933 | 59.8666 | 35.92 | 23.9466
| 3 | [6 empty] | 30.8 | 38.5 | 23.1 | 15.4 |  | 3 | 46411.8605 | 20.4796 | 12.7992 | 100.095 | 125.1187 | 75.0712 | 50.0475
| 4 | [6 empty] | 39.5 | 49.375 | 29.625 | 19.75 |  | 4 | 23032.968 | 21.4937 | 13.0198 | 106.6213 | 133.2767 | 79.966 | 53.3107
| 5 | [6 empty] | 29.7 | 37.125 | 22.275 | 14.85 |  | 5 | 5978.4428 | 11.9981 | 11.5852 | 59.1493 | 73.9366 | 44.362 | 29.5746
| 6 | [6 empty] | 31.8 | 39.75 | 23.85 | 15.9 |  | 6 | 57755.9589 | 22.6073 | 9.9467 | 82.3475 | 102.9344 | 61.7606 | 41.1737
| 7 | [6 empty] | 32.8 | 41 | 24.6 | 16.4 |  | 7 | 35149.9926 | 24.8484 | 6.97 | 88.5535 | 110.6918 | 66.4151 | 44.2767
| 8 | [6 empty] | 38.6 | 48.25 | 28.95 | 19.3 |  | 8 | 92353.4113 | 22.9353 | 8.8422 | 103.4418 | 129.3023 | 77.5814 | 51.7209
| 9 | [6 empty] | 38.5 | 48.125 | 28.875 | 19.25 |  | 9 | 141795.4506 | 26.7973 | 10.0891 | 119.1513 | 148.9391 | 89.3635 | 59.5757
| 10 | [6 empty] | 42.2 | 52.75 | 31.65 | 21.1 |  | 10 | 92589.8669 | 22.4904 | 10.109 | 67.4191 | 84.2739 | 50.5643 | 33.7096
| 11 | [6 empty] | 47.7 | 59.625 | 35.775 | 23.85 |  | 11 | 33810.4884 | 26.9287 | 8.7604 | 68.8393 | 86.0491 | 51.6294 | 34.4196
| 12 | [6 empty] | 41.6 | 52 | 31.2 | 20.8 |  | 12 | 108342.4341 | 31.7996 | 12.2303 | 85.5874 | 106.9842 | 64.1905 | 42.7937
| 13 | [6 empty] | 49.6 | 62 | 37.2 | 24.8 |  | 13 | 46676.8078 | 32.656 | 15.4735 | 57.7357 | 72.1696 | 43.3018 | 28.8678
| 14 | [6 empty] | 48.8 | 61 | 36.6 | 24.4 |  | 14 | 22787.7389 | 21.8072 | 11.4332 | 68.5025 | 85.6282 | 51.3769 | 34.2513
| 15 | [6 empty] | 65.8 | 82.25 | 49.35 | 32.9 |  | 15 | 54746.0029 | 21.9543 | 10.4391 | 47.7153 | 59.6441 | 35.7864 | 23.8576
| 16 | [6 empty] | 44 | 55 | 33 | 22 |  | 16 | 85267.8904 | 27.0269 | 11.6529 | 67.5765 | 84.4706 | 50.6824 | 33.7882
Ref: CEUS 2022 Report
And by applying FZ-CZ multipliers for converting FZ data to CZ data

## PV (hidden)
PV - SchoolHigh
TBD

## EV Charger (hidden)
EV Charger - SchoolHigh
TBD
Background Data [To be deleted prior to publication]

## Data (hidden)
Space Function | Electric Equipment Load Intensity | Electric Equipment Load Intensity | LPD
Aging Eye/Low-vision (Corridor Area) |  |  | 2013 | 2016 | 2019 | 2025
Aging Eye/Low-vision (Dining)
Aging Eye/Low-vision (Lobby, Main Entry)
Aging Eye/Low-vision (Lounge/Waiting Area)
Aging Eye/Low-vision (Multipurpose Room)
Aging Eye/Low-vision (Religious Worship Area)
Aging Eye/Low-vision (Restroom)
Aging Eye/Low-vision (Stairwell)
Audience Seating Area
Auditorium Area
Auto Repair / Maintenance Area
Barber, Beauty Salon, Spa Area
Civic Meeting Place Area
Classroom, Lecture, Training, Vocational Areas
Concourse and Atria Area
Convention, Conference, Multipurpose and Meeting Area
Copy Room
Corridor Area
Dining Area (Bar/Lounge and Fine Dining)
Dining Area (Cafeteria/Fast Food)
Dining Area (Family and Leisure)
Electrical, Mechanical, Telephone Rooms
Exercise/Fitness Center and Gymnasium Areas
Financial Transaction Area
Healthcare Facility and Hospitals (Exam/Treatment Room)
Healthcare Facility and Hospitals (Imaging Room)
Healthcare Facility and Hospitals (Medical Supply Room)
Healthcare Facility and Hospitals (Nursery)
Healthcare Facility and Hospitals (Nurse's Station)
Healthcare Facility and Hospitals (Operating Room)
Healthcare Facility and Hospitals (Patient Room)
Healthcare Facility and Hospitals (Physical Therapy Room)
Healthcare Facility and Hospitals (Recovery Room)
Hotel Function Area
Kitchen/Food Preparation Area
Kitchenette or Residential Kitchen
Laboratory, Scientific
Laundry Area
Library (Reading Area)
Library (Stacks Area)
Lobby, Main Entry
Locker Room
Lounge, Breakroom, or Waiting Area
Manufacturing, Commercial & Industrial Work Area (Low Bay)
Manufacturing, Commercial & Industrial Work Area (High Bay)
Manufacturing, Commercial & Industrial Work Area (Precision)
Museum Area (Exhibition/Display)
Museum Area (Restoration Room)
Office Area (>250 square feet)
Office Area (<250 square feet)
Parking Garage Area (Parking Zone and Ramps)
Parking Garage Area (Daylight Adaptation Zones)
Pharmacy Area
Retail Sales Area (Grocery Sales)
Retail Sales Area (Retail Merchandise Sales)
Retail Sales Area (Fitting Room)
Religious Worship Area
Restrooms
Stairwell
Storage, Commercial/Industrial (Warehouse)
Storage, Commercial/Industrial (Refrigerated)
Storage, Commercial/Industrial (Shipping & Handling)
Storage (General)
Sports Arena - Playing Area (> 5,000 Spectators)
Sports Arena - Playing Area (2,000 - 5,000 Spectators)
Sports Arena - Playing Area (< 2,000 Spectators)
Sports Arena - Playing Area (Recreational)
Theater Area (Motion Picture)
Theater Area (Performance)
Transportation Function (Baggage Area)
Transportation Function (Ticketing Area)
Videoconferencing Studio
High-Rise Residential Living Spaces
Hotel/Motel Guest Room
All other
Attic
Reception Area
Elevator
Plenum
Computer Room
Server Room
Wood/Metal Shop Classroom

## Weights (hidden)
% of Floor Area per CZ and Vintage Bin - Schools
Prototype | CZ | Vintage Bin
|  | Pre-1978 | 1978-1997 | 1998-2007 | 2008-2018 | Not available
High School | 1 | [5 empty] | 0%
| 2 | [5 empty] | 0%
| 3 | [5 empty] | 0%
| 4 | [5 empty] | 0%
| 5 | [5 empty] | 0%
| 6 | [5 empty] | 0%
| 7 | [5 empty] | 0%
| 8 | [5 empty] | 0%
| 9 | [5 empty] | 0%
| 10 | [5 empty] | 0%
| 11 | [5 empty] | 0%
| 12 | [5 empty] | 0%
| 13 | [5 empty] | 0%
| 14 | [5 empty] | 0%
| 15 | [5 empty] | 0%
| 16 | [5 empty] | 0%
Statewide
Ref: CEUS 2022 dataset