## Notes
Data Sources
Dataset | Dodge 2023
CEUS 2022
ComStock 2023
Prototype | CalBEM SchoolLarge / PNNL Secondary School prototype | https://www.energycodes.gov/prototype-building-models
Codes | Title 24, part 6, referred to as T24 (1984, 2001, 2007, 2013, 2016, 2022, 2025)
ASHRAE 90.1 (2022)
CFR Title 10 (2008, 2010, 2025)
ACM 2022
| T24 2022 - Appendix 5.4A and Appendix 5.4B | https://www.energy.ca.gov/publications/2022/2022-nonresidential-and-multifamily-alternative-calculation-method-reference
Other | 2022 Reduced infiltration CASE report | https://title24stakeholders.com/wp-content/uploads/2020/10/2022-T24-Final-CASE-Report_Reduce-Infiltration.pdf
| 2019 Outdoor Lighting CASE Report | https://title24stakeholders.com/wp-content/uploads/2016/10/T24-2019-CASE-Study-Results-Report-Outdoor-Sources_Final_with-Attachments.pdf
| 2019 High Efficiency Fume Hoods in Laboratory Spaces CASE Report | https://title24stakeholders.com/wp-content/uploads/2017/09/2019-T24-CASE-Report_Fume-Hoods_Final_September-2017.pdf?
| PNNL 20405, 2011 | https://www.pnnl.gov/main/publications/external/technical_reports/PNNL-20405.pdf
| Air leakage Memo, NORESCO, 2025 | Infiltration_rate_report_14May2025-Short-Version.docx — internal NORESCO project memo (not a public URL). See Prototype basis / Source access below.
Water Heater | ENERGY STAR certified commercial water heaters (gas storage input ≥76 kBtu/h; ES tank sizes) | ENERGY STAR product finder — gas
| ENERGY STAR commercial WH dataset (download) | ENERGY STAR dataset xmq6-bm79
| ENERGY STAR commercial WH eligibility (gas storage >75 kBtu/h) | ENERGY STAR key product criteria
| Grainger gas tank water heaters (sizes below ES commercial, e.g. 30–75 kBtu/h) | Grainger — gas tank WH
| Grainger electric tank water heaters (kW ladder, tank gallons) | Grainger — electric tank WH
| ES commercial electric = heat pumps only; not used for resistance tank list | ENERGY STAR — electric (HPWH)
Construction Rate
Notes
Prototype basis
Geometry | Geometry is CalBEM SchoolLarge, based on the DOE/PNNL Secondary School prototype (Prototype comparison column B): one 2-story building, 210,907 ft², WWR 34.5%, steel-framed walls, built-up roof, plastic curb-mounted skylights over gymnasium. CEC SchoolHigh (column C) and DEER education columns are comparison only — they are not this prototype's geometry.
Vintage bins | Existing vintages Pre-1978, 1978-1997, 1998-2007, 2008-2018 plus New Construction 2019+ follow the SCE Enhanced Prototypes vintage-bin analysis (Prototype D6). Dodge 2023 construction rates inform stock weighting; they are not a Title 24 prescriptive requirement.
Curriculum and stock | Conventional secondary-school program (classrooms, cafeteria, kitchen, library, gym/aux gym, auditorium, offices, corridors). The prototype represents average California large-school stock. Funding/condition variation is carried in vintage envelope/HVAC/lighting assumptions (including Envelope H8 30-year roof replacement).
WWR, heights, energy | WWR 34.5%, no exterior shades (CalBEM/PNNL). Floor-to-floor ~13.1 ft except gymnasium and auditorium ~26.2 ft (double-height; Zones H/G). HVAC: central VAV with hydronic reheat, gas boiler, air-cooled chiller (2 air loops). Service water: gas storage (Water Heater B3:B4). 1998–2007 window SHGC uses Table 1-H 31–40% WWR (prototype 34.5%), not the ≤10% row used on CEC campus schools.
Abbreviations | T24 = California Title 24, Part 6. ACM = Nonresidential/Multifamily Alternative Calculation Method Reference Manual. CEC = California Energy Commission. CalBEM = California Building Energy Modeling. PNNL = Pacific Northwest National Laboratory. VAV = variable air volume. WWR = window-to-wall ratio. SRR = skylight-to-roof ratio. IWA = initial wattage allowance.
Source access | Column C lists public links where they exist. Dodge 2023 is a licensed dataset with no public URL. The NORESCO air-leakage memo is an internal file (C19), not a webpage. ENERGY STAR water-heater rows use Product Finder and dataset xmq6-bm79. Schedule fractions that cite the Plug Loads and Schedules project with CEC (2025) do not have an external link yet; an ASHRAE paper has been submitted and the citation will be updated when that paper is published or when ACM 2028 is released.
Sources used | Used on this scorecard: DOE/PNNL Secondary School / CalBEM SchoolLarge; T24 2022 App. 5.4A/5.4B; ACM 2025 §5.9.2 and fan tables; T24 Tables 140.3-B, 110.2-D/J, 140.6-C, 140.7-A/B, 120.1-A/B; 2022 Reduced Infiltration CASE; 2019 Outdoor Lighting CASE; PNNL 20405; ASHRAE 90.1-2022 Appendix A; ASHRAE Handbook of Fundamentals; ENERGY STAR commercial gas storage WH. CEC SchoolHigh efiling tn=265691 is not this prototype's geometry source.

## Prototype
NORESCO, Updated September 2026
SchoolLarge
Characteristic | Value | Data Sources
Building Type | Large School
Building Category | Nonresidential
Version | v2-0
Vintages | 4 Vintages: Pre-1978, 1978-1997,1998-2007, 2008-2018 New Construction (2019+) | Based on the vintage bin analysis. A summary of the findings is presented in the following paper, with a link provided in the Notes tab: Yousefi, F., Athalye, R. (2025). “Determining Vintage Bins for Prototype Development: An Analysis of California Commercial Buildings.” ASHRAE Annual Conference.
Shape |  | The analysis uses CalBEM SchoolLarge geometry (DOE/PNNL Secondary School). CEC SchoolHigh in the comparison table is a different prototype.
Total Floor Area (ft²) | 210906.62 | CalBEM SchoolLarge / PNNL Secondary School (same as Prototype comparison column B).
Aspect Ratio | 1.3558 | CalBEM SchoolLarge / PNNL Secondary School (comparison column B).
Number of Floors | 2 | CalBEM SchoolLarge / PNNL Secondary School (comparison column B).
Roof type | Flat | CalBEM SchoolLarge / PNNL Secondary School (comparison column B).
WWR | 34.5% | CalBEM SchoolLarge / PNNL Secondary School (comparison column B).
Shading Geometry | No Shades | CalBEM SchoolLarge / PNNL Secondary School (comparison column B).
Floor to floor height (feet) | 13.1 ft typical (Zones volume/area). Gymnasium and auditorium ~26.2 ft (double-height). | CalBEM SchoolLarge / PNNL Secondary School (comparison column B).
Floor to ceiling height (feet) | 13.1 ft typical. Gymnasium and auditorium ~26.2 ft (double-height). | CalBEM SchoolLarge / PNNL Secondary School (comparison column B).
Glazing sill height (feet) | 3.6 ft | CalBEM SchoolLarge / PNNL Secondary School (comparison column B).
Above grade wall area (ft²) | 64245.23
Gross wall area (ft²) | 64245.23
Roof area (ft²) | 128124.28
Underground Gross Wall Area (ft²) | 0

## Zones
Proposed Layout - SchoolLarge
Building | Space/Thermal Zone | Space Type [Primarily from: T24, 2022 Appendix 5.4A] - See Notes column | HVAC System Name/AHU Name | Schedule Category | Conditioned (Y/N) | Area Fraction | Area (ft²) | Volume (ft³) | Multipliers | Number of People | People (Persons/1,000 ft²) [T24, 2025,Table 120.1-A] | Notes
SchoolLarge | Auditorium_FF_Zn | Auditorium Area | BaseAirSys5 | Classroom | Y | 5.043% | 10635.81 | 279168.51 | 1 | 755.1425 | 71
SchoolLarge | Aux_Gym_FF_Zn | Exercise/Fitness Center and Gymnasium Areas | BaseAirSys5 | Classroom | Y | 6.37% | 13434.61 | 352631.31 | 1 | 134.3461 | 10 |  | Space Type | Area (ft²) | Fraction | % of total
SchoolLarge | Bathrooms_FF_Zn | Restrooms | BaseAirSys5 | AnhillaryRestroom | Y | 1.072% | 2260.58 | 29667.9 | 1 | 11.3029 | 5 |  | Auditorium Area | 10635.81 | 0.050429 | 0.050429
SchoolLarge | Bathrooms_SF_Zn | Restrooms | BaseAirSys5-2 | AncillaryRestroom | Y | 1.072% | 2260.58 | 29667.68 | 1 | 11.3029 | 5 |  | Exercise/Fitness Center and Gymnasium Areas | 34706.13 | 0.16456 | 0.16456
SchoolLarge | Cafeteria_FF_Zn | Dining Area (Cafeteria/Fast Food) | BaseAirSys5 | Classroom | Y | 3.185% | 6717.34 | 88158.58 | 1 | 221.6722 | 33 |  | Restrooms | 4521.16 | 0.021437 | 0.021437
SchoolLarge | Corner_Class_1_Pod_1_FF_Zn | Classroom, Lecture, Training, Vocational Areas | BaseAirSys5 | Classroom | Y | 0.5053% | 1065.73 | 13986.7 | 1 | 26.6432 | 25 |  | Dining Area (Cafeteria/Fast Food) | 6717.34 | 0.03185 | 0.03185
SchoolLarge | Corner_Class_1_Pod_1_SF_Zn | Classroom, Lecture, Training, Vocational Areas | BaseAirSys5-2 | Classroom | Y | 0.5053% | 1065.73 | 13986.6 | 1 | 26.6432 | 25 |  | Classroom, Lecture, Training, Vocational Areas | 74407.4 | 0.3528 | 0.3528
SchoolLarge | Corner_Class_1_Pod_2_FF_Zn | Classroom, Lecture, Training, Vocational Areas | BaseAirSys5 | Classroom | Y | 0.5053% | 1065.71 | 13986.42 | 1 | 26.6427 | 25 |  | Corridor Area | 45212.42 | 0.21437 | 0.21437
SchoolLarge | Corner_Class_1_Pod_2_SF_Zn | Classroom, Lecture, Training, Vocational Areas | BaseAirSys5-2 | Classroom | Y | 0.5053% | 1065.71 | 13986.31 | 1 | 26.6427 | 25 |  | Kitchen/Food Preparation Area | 2325.26 | 0.011025 | 0.011025
SchoolLarge | Corner_Class_1_Pod_3_FF_Zn | Classroom, Lecture, Training, Vocational Areas | BaseAirSys5 | Classroom | Y | 0.5053% | 1065.75 | 13986.89 | 1 | 26.6438 | 25 |  | Library (Reading Area) | 9042.6 | 0.042875 | 0.042875
SchoolLarge | Corner_Class_1_Pod_3_SF_Zn | Classroom, Lecture, Training, Vocational Areas | BaseAirSys5-2 | Classroom | Y | 0.5053% | 1065.75 | 13986.79 | 1 | 26.6438 | 25 |  | Lobby, Main Entry | 4521.24 | 0.021437 | 0.021437
SchoolLarge | Corner_Class_2_Pod_1_FF_Zn | Classroom, Lecture, Training, Vocational Areas | BaseAirSys5 | Classroom | Y | 0.5053% | 1065.73 | 13986.66 | 1 | 26.6432 | 25 |  | Electrical, Mechanical, Telephone Rooms | 7363.34 | 0.034913 | 0.034913
SchoolLarge | Corner_Class_2_Pod_1_SF_Zn | Classroom, Lecture, Training, Vocational Areas | BaseAirSys5-2 | Classroom | Y | 0.5053% | 1065.73 | 13986.55 | 1 | 26.6432 | 25 |  | Office Area (>250 square feet) | 11453.94 | 0.054308 | 0.054308
SchoolLarge | Corner_Class_2_Pod_2_FF_Zn | Classroom, Lecture, Training, Vocational Areas | BaseAirSys5 | Classroom | Y | 0.5053% | 1065.75 | 13986.89 | 1 | 26.6438 | 25 |  | Total | 210906.64 | 1
SchoolLarge | Corner_Class_2_Pod_2_SF_Zn | Classroom, Lecture, Training, Vocational Areas | BaseAirSys5-2 | Classroom | Y | 0.5053% | 1065.75 | 13986.79 | 1 | 26.6438 | 25
SchoolLarge | Corner_Class_2_Pod_3_FF_Zn | Classroom, Lecture, Training, Vocational Areas | BaseAirSys5 | Classroom | Y | 0.5053% | 1065.71 | 13986.42 | 1 | 26.6427 | 25
SchoolLarge | Corner_Class_2_Pod_3_SF_Zn | Classroom, Lecture, Training, Vocational Areas | BaseAirSys5-2 | Classroom | Y | 0.5053% | 1065.71 | 13986.31 | 1 | 26.6427 | 25
SchoolLarge | Corridor_Pod_1_FF_Zn | Corridor Area | BaseAirSys5 | Classroom | Y | 1.633% | 3444.79 | 45209.59 | 1 | 17.224 | 5
SchoolLarge | Corridor_Pod_1_SF_Zn | Corridor Area | BaseAirSys5-2 | Classroom | Y | 1.633% | 3444.79 | 45209.24 | 1 | 17.224 | 5
SchoolLarge | Corridor_Pod_2_FF_Zn | Corridor Area | BaseAirSys5 | Classroom | Y | 1.633% | 3444.75 | 45209.03 | 1 | 17.2237 | 5
SchoolLarge | Corridor_Pod_2_SF_Zn | Corridor Area | BaseAirSys5-2 | Classroom | Y | 1.633% | 3444.75 | 45208.69 | 1 | 17.2237 | 5
SchoolLarge | Corridor_Pod_3_FF_Zn | Corridor Area | BaseAirSys5 | Classroom | Y | 1.633% | 3444.75 | 45209.03 | 1 | 17.2237 | 5
SchoolLarge | Corridor_Pod_3_SF_Zn | Corridor Area | BaseAirSys5-2 | Classroom | Y | 1.633% | 3444.75 | 45208.69 | 1 | 17.2237 | 5
SchoolLarge | Gym_FF_Zn | Exercise/Fitness Center and Gymnasium Areas | BaseAirSys5 | Gym | Y | 10.09% | 21271.52 | 558334.4 | 1 | 212.7152 | 10
SchoolLarge | Kitchen_FF_Zn | Kitchen/Food Preparation Area | BaseAirSys5 | Kitchen | Y | 1.103% | 2325.26 | 30516.83 | 1 | 6.9758 | 3
SchoolLarge | Library_Media_Center_SF_Zn | Library (Reading Area) | BaseAirSys5-2 | Classroom | Y | 4.287% | 9042.6 | 118674.5 | 1 | 90.426 | 10
SchoolLarge | Lobby_FF_Zn | Lobby, Main Entry | BaseAirSys5 | Classroom | Y | 1.072% | 2260.62 | 29668.42 | 1 | 74.6005 | 33
SchoolLarge | Lobby_SF_Zn | Lobby, Main Entry | BaseAirSys5-2 | Classroom | Y | 1.072% | 2260.62 | 29668.19 | 1 | 74.6005 | 33
SchoolLarge | Main_Corridor_FF_Zn | Corridor Area | BaseAirSys5 | Classroom | Y | 5.819% | 12271.92 | 161057.23 | 1 | 61.3596 | 5
SchoolLarge | Main_Corridor_SF_Zn | Corridor Area | BaseAirSys5-2 | Classroom | Y | 5.819% | 12271.92 | 161056 | 1 | 61.3596 | 5
SchoolLarge | Mech_FF_Zn | Electrical, Mechanical, Telephone Rooms | BaseAirSys5 | Ancillary | Y | 1.746% | 3681.67 | 48318.44 | 1 | 18.4083 | 5
SchoolLarge | Mech_SF_Zn | Electrical, Mechanical, Telephone Rooms | BaseAirSys5-2 | Ancillary | Y | 1.746% | 3681.67 | 48318.07 | 1 | 18.4083 | 5
SchoolLarge | Mult_Class_1_Pod_1_FF_Zn | Classroom, Lecture, Training, Vocational Areas | BaseAirSys5 | Classroom | Y | 2.435% | 5134.9 | 67390.66 | 1 | 128.3725 | 25
SchoolLarge | Mult_Class_1_Pod_1_SF_Zn | Classroom, Lecture, Training, Vocational Areas | BaseAirSys5-2 | Classroom | Y | 2.435% | 5134.9 | 67390.15 | 1 | 128.3725 | 25
SchoolLarge | Mult_Class_1_Pod_2_FF_Zn | Classroom, Lecture, Training, Vocational Areas | BaseAirSys5 | Classroom | Y | 2.435% | 5134.8 | 67389.29 | 1 | 128.37 | 25
SchoolLarge | Mult_Class_1_Pod_2_SF_Zn | Classroom, Lecture, Training, Vocational Areas | BaseAirSys5-2 | Classroom | Y | 2.435% | 5134.8 | 67388.78 | 1 | 128.37 | 25
SchoolLarge | Mult_Class_1_Pod_3_FF_Zn | Classroom, Lecture, Training, Vocational Areas | BaseAirSys5 | Classroom | Y | 2.435% | 5134.97 | 67391.57 | 1 | 128.3742 | 25
SchoolLarge | Mult_Class_1_Pod_3_SF_Zn | Classroom, Lecture, Training, Vocational Areas | BaseAirSys5-2 | Classroom | Y | 2.435% | 5134.97 | 67391.06 | 1 | 128.3742 | 25
SchoolLarge | Mult_Class_2_Pod_1_FF_Zn | Classroom, Lecture, Training, Vocational Areas | BaseAirSys5 | Classroom | Y | 2.435% | 5134.88 | 67390.43 | 1 | 128.372 | 25
SchoolLarge | Mult_Class_2_Pod_1_SF_Zn | Classroom, Lecture, Training, Vocational Areas | BaseAirSys5-2 | Classroom | Y | 2.435% | 5134.88 | 67389.92 | 1 | 128.372 | 25
SchoolLarge | Mult_Class_2_Pod_2_FF_Zn | Classroom, Lecture, Training, Vocational Areas | BaseAirSys5 | Classroom | Y | 2.435% | 5134.97 | 67391.57 | 1 | 128.3742 | 25
SchoolLarge | Mult_Class_2_Pod_2_SF_Zn | Classroom, Lecture, Training, Vocational Areas | BaseAirSys5-2 | Classroom | Y | 2.435% | 5134.97 | 67391.06 | 1 | 128.3742 | 25
SchoolLarge | Mult_Class_2_Pod_3_FF_Zn | Classroom, Lecture, Training, Vocational Areas | BaseAirSys5 | Classroom | Y | 2.435% | 5134.8 | 67389.29 | 1 | 128.37 | 25
SchoolLarge | Mult_Class_2_Pod_3_SF_Zn | Classroom, Lecture, Training, Vocational Areas | BaseAirSys5-2 | Classroom | Y | 2.435% | 5134.8 | 67388.78 | 1 | 128.37 | 25
SchoolLarge | Offices_FF_Zn | Office Area (>250 square feet) | BaseAirSys5 | Classroom | Y | 2.715% | 5726.97 | 75160.96 | 1 | 28.6349 | 5
SchoolLarge | Offices_SF_Zn | Office Area (>250 square feet) | BaseAirSys5-2 | Classroom | Y | 2.715% | 5726.97 | 75160.39 | 1 | 28.6349 | 5
Total (1 Building) | Total (46 spaces) | Total (11 Space types) | Total (2 air loops) | Total (3 Schedule categories) | Total (46 Conditioned zones) | 100% | 210906.64 | 3363003.57 |  | 3773.418
N

## Envelope
Envelope - SchoolLarge
Element | Prototype | Assembly Type | Construction | Thermal properties | Vintage | Selected T24 | Notes | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
External Wall | SchoolLarge | ExtWall_MetalFramed_NonRes | Metal frame + insulation + Gypsum board | U-value IP | Pre 1978 | N/A | ASHRAE 90.1-2022 Table A3.3.3.1 (metal-framed), 3.5 in., R-0, U-0.352 all CZ. Was A3.4.3.1 mass-wall U-0.292; construction C3 is ExtWall_MetalFramed_NonRes (DOE/PNNL Secondary School steel frame). | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352
[5 empty] | 1978-1997 | 1992 | TABLE NO. 1-I metal-framed | 0.182 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182
[5 empty] | 1998-2007 | 2001 | Table 1-H metal frame | 0.182 | 0.182 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182
[5 empty] | 2008-2018 | 2013 | Table 140.3-B metal-framed (2013) | 0.098 | 0.062 | 0.082 | 0.062 | 0.062 | 0.098 | 0.098 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062
[5 empty] | 2019+ | 2025 | Table 140.3-B (2025) Metal-framed walls | 0.06 | 0.055 | 0.071 | 0.055 | 0.055 | 0.06 | 0.06 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055
Roof | SchoolLarge | FlatRoof_WoodFramedAndOther_NonRes | Built-up Roof roof membrane+roof insulation+metal decking | U-value IP | Pre 1978 | N/A | Considering 30 years for roof/insulation replacement | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 1978-1997 | N/A |  | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 1998-2007 | 2001 | Table 1-H | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.049 | 0.039 | 0.039 | 0.039 | 0.049 | 0.075 | 0.067 | 0.067 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.047 | 0.047 | 0.047 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028
Windows | SchoolLarge | FixedWindow_NonRes | Single pane | U-value IP | Pre 1978 | N/A | ASHRAE Handbook of Fundamentals (Table 4-Ch15) for single pane & T24, 2013 for double pane (33%-67%)* | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108
[5 empty] | 1978-1997 | N/A |  | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108
|  |  | Double pane |  | 1998-2007 | 2001 | Table 1-H | 0.49 | 0.49 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.34 | 0.36 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.36
| SchoolLarge | FixedWindow_NonRes | Single pane | SHGC | Pre 1978 | N/A | ASHRAE Handbook of Fundamentals (Table 10-Ch15) for single pane & T24, 2013 for double pane (33%-67%)* | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282
[5 empty] | 1978-1997 | N/A |  | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282
|  |  | Double pane |  | 1998-2007 | 2001 | Table 1-H — WWR 31–40% (prototype 34.5%), SHGC non-north. Not the ≤10% / SHGC 0.31 row used on CEC campus schools. | 0.43 | 0.36 | 0.41 | 0.41 | 0.41 | 0.34 | 0.34 | 0.34 | 0.34 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.43
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.22 | 0.25 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.25
Skylight | SchoolLarge | Skylight | Plastic curb-mounted | U-factor IP | Pre 1978 | 1992 | Table 1-I Translucent (1992 term for plastic curb-mounted). Prototype comparison B35 = 1,825 ft²; SRR = 1,825 / 128,124 = 1.42% (0–2% bin). PNNL secondary-school gym skylights are plastic with curbs. | 0.85 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
[5 empty] | 1978-1997 | 1992 |  | 0.85 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
[5 empty] | 1998-2007 | 2001 | Table 1-H plastic w/curb U-factor (U does not vary by SRR). | 0.87 | 1.1 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 0.87
[5 empty] | 2008-2018 | 2013 | Table 140.3-B plastic curb-mounted U-factor | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88
[5 empty] | 2019+ | 2025 | Table 140.3-B (2025) plastic curb-mounted U-factor | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88
|  |  |  | SHGC | Pre 1978 | 1992 | Table 1-I Translucent SHGC (same plastic curb product). | 0.81 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81
[5 empty] | 1978-1997 | 1992 |  | 0.81 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81
[5 empty] | 1998-2007 | 2001 | Table 1-H plastic w/curb, SRR 0–2% (whole-roof SRR 1.42%). Not 2.1–5%. | 0.77 | 0.77 | 0.79 | 0.79 | 0.79 | 0.77 | 0.77 | 0.77 | 0.77 | 0.77 | 0.77 | 0.77 | 0.77 | 0.71 | 0.71 | 0.77
[5 empty] | 2008-2018 | 2013 | Table 140.3-B plastic curb SHGC = NR; used 2001 Table 1-H 0–2% SRR. | 0.77 | 0.77 | 0.79 | 0.79 | 0.79 | 0.77 | 0.77 | 0.77 | 0.77 | 0.77 | 0.77 | 0.77 | 0.77 | 0.71 | 0.71 | 0.77
[5 empty] | 2019+ | 2025 | Table 140.3-B (2025) plastic curb SHGC = NR; same 2001 0–2% SRR values. | 0.77 | 0.77 | 0.79 | 0.79 | 0.79 | 0.77 | 0.77 | 0.77 | 0.77 | 0.77 | 0.77 | 0.77 | 0.77 | 0.71 | 0.71 | 0.77
Floor: SlabOnGrade_Unheated_NonRes is a 4 in. concrete slab-on-grade with no insulation. It is the same for every vintage (F-factor 0.73), so it is documented here instead of as a table row.
Infiltration
|  |  | Building | Zones | Vintage | I_75 6-Sided Inifltration rate @ 75 pa | Note | I-design (cfm/ft²) (4-sided Infiltration rate at normal presure) (Design flow rate approach and Flow/Exterior Wall Area calulation method)
|  | Infiltration | SchoolRelocatable |  | Pre 1978 | 1.1 | 2022 CASE report (Table 38) | 0.6146
[5 empty] | 1978-1997 | 1.1 | 2022 CASE report (Table 38) | 0.6146
[5 empty] | 1998-2007 | 1.1 | 2022 CASE report (Table 38) | 0.6146
[5 empty] | 2008-2018 | 1 | 2022 CASE report (Table 38) & T24, 2008-2016 (Table 140.3-B)--Air barrier is required in CZ 10-16 | 0.5624
[5 empty] | 2019+ | 0.6 | 2022 CASE report (Table 38) & T24, 2025 (Table 140.3-B)--Air barrier is required in all CZs | 0.3352
Source: T24 air barrier requirements (all editions) and the standardized infiltration rate reported in the 2022 CASE report and Dodge 2023 data
|  |  |  | Air Lekage Memo: |  | Infiltration_rate_report_14May2025-Short-Version.docx

## HVAC System
HVAC system - SchoolLarge
Vintage | Zones | Heating | Cooling | Air Distribution | Other Systems | Source | Note
Exisiting | All Space Types | Gas Boiler | Air-cooled Chiller | VAV + Hydronic reheat | OA mixing through air handler. | Engineering Judgement | System 6
New Construction | All Space Types | Gas Boiler | Air-cooled Chiller | VAV + Hydronic reheat | OA mixing through air handler. | Engineering Judgement | System 6
Efficiency of HVAC System (Efficiency is capacity-dependent. The following table provides a general estimate of system efficiency based on preliminary simulations in one climate zone, or assuming cooling load based on rule of thumb)
Vintage | Upgrade/Installed year | Gas-Fired Boiler | Heating DX | Air-Cooled Chiller | Heat Rejection | Source | Note
Pre 1978 | 2008 | If 300,000 Btu/h ≤ input < 2.5 MMBtu/h: Et ≥ 75% | n/a | Air-cooled, with condenser, >150 tons: ≥ 2.80 COP (≥ 9.562 EER) / 3.05 IPLV (ARI 550/590) | n/a (air-cooled; no cooling tower) | T24 2008 Table 112-D (air-cooled with condenser). Was water-cooled centrifugal ≥300 tons + cooling tower; HVAC D3 is air-cooled chiller.
1978-1997
1998-2007
2008-2018 | 2013 | 300k–2.5 MMBtu/h: Et ≥ 80% > 2.5 MMBtu/h: Ec ≥ 82% | n/a | Air-cooled, with condenser, ≥150 tons: Path A ≥ 9.562 EER / ≥ 12.750 IPLV Path B = N.A. (2013 Table 110.2-D) | n/a (air-cooled; no cooling tower) | T24 2013 Table 110.2-D (air-cooled chiller) ¦ T24 2013 Table 110.2-K (boiler). Air-cooled Path B is N.A. in 2013.
New Construction | 2025 | Boiler (hot-water, gas, > 2.5 MMBtu/h): Ec ≥ 85% | n/a | Air-cooled, with condenser, ≥150 tons: Path B (T24 §140.4(i)) ≥ 9.700 EER / ≥ 16.100 IPLV | n/a (air-cooled; no cooling tower) | T24 2025 Table 110.2-D Path B (air-cooled ≥150 tons) ¦ Table 110.2-J (boiler). Size bin is the air-cooled table breakpoint (≥150 tons), not the old water-cooled 300–600 ton screw row.
|  | * Et = Combustion efficiency | * Et = Thermal efficiency
Fan power
Vintage | Approach | System | Total Static Pressure (TSP) (in w.c.) | Fan Efficiency [ACM 2025] | Motor Efficiency | Fan Power Index (W/cfm) | Data Source
Existing | PNNL 90.1-2011, TSP | VAV + hydronic reheat, design airflow ≥ 20,000 cfm | 5.58 | 0.65 | ASHRAE 90.1, 2004, Table 10.8 * |  | Fan power formula: PNNL 20405, 2010, section 5.2.2.5 TSP and fan efficiency: PNNL 20405, 2010, Table 5.11, 90.1-04ac values Motor and drive efficiency: ASHRAE 90.1, 2004, Table 10.8 | PNNL 20405, 2010, Table 5.11
Brake horsepower (bhp) = (Supply cfm × TSP in w.c.) / (6356 × fan efficiency)
Fan power (w/cfm) = (bhp × 746) / ( supply cfm × motor efficiency )
New Construction | ACM 2025 | VAV + hydronic reheat (System 6), ≥20,000 cfm | TSP = fan power × motor efficiency × fan efficiency × 6356 / 746 | 0.65 | 2025 ACM Table 12 ** | 0.947 | Fan power index: [ACM 2025, Table 13] Motor efficiency: [ACM 2025, Table 12]
* According to PNNL 20405 section 5.2.2.5, the full-load efficiency of the motor serving the fan is taken from ASHRAE 90.1, 2004, Table 10.8, based on motor nameplate and assuming enclosed motors operating at 1,800 rotations per minute (rpm) Motor nameplate size (bhp) = brake horsepower (bhp) × 1.1 ( using a 10% oversizing factor)
** The full‑load efficiency of the motor serving the fan is taken from ACM 2025 Table 12 based on the cfm of the fan. Brake horsepower (bhp) = (Supply cfm from sizing run × fan power in W/cfm) / 746. Note: ACM System 6 VAV >10,000 cfm.
Background Data [To be deleted prior to publication]

## Thermostat
Thermostat Setpoints - SchoolLarge
Setpoint | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16 | Source
School Heating Setpoint (F) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | T24 2022 - Appendix 5.4B
School Heating Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
School Cooling Setpoint (F) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
School Cooling Setback (F) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
Kitchen Heating Setpoint (F) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | T24 2022 - Appendix 5.4B (school kitchen occupied 70/75; not commercial restaurant 66–79)
Kitchen Heating Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Kitchen Cooling Setpoint (F) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
Kitchen Cooling Setback (F) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
Restrooms Heating Setpoint (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | PNNL 90.1 Primary School bathroom (HTGSETP_SCH_Setback / CLGSETP_SCH_Setup)
Restrooms Heating Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Restrooms Cooling Setpoint (F) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
Restrooms Cooling Setback (F) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
Electrical/Mechanical (non-refrigerated) Heating Setpoint (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | Engineering Judgment (semi-conditioned storage / electrical-mechanical)
Electrical/Mechanical (non-refrigerated) Heating Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Electrical/Mechanical (non-refrigerated) Cooling Setpoint (F) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
Electrical/Mechanical (non-refrigerated) Cooling Setback (F) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85

## Ventilation
Outdoor Airflow Rate - SchoolLarge
Space Type | Space/Thermal Zone | Number of People | Floor Area (ft²) | cfm/person [T24, 2025, Equation 120.1-F and Table 120.1-A] | cfm/ft² [T24, 2025, Equation 120.1-F and Table 120.1-A] | Required exhaust rate-CFM/ft²- [T24, 2025, Table 120.1-B – minimum exhaust rates] | Total cfm driven by people | Total cfm driven by area | Total cfm driven by exhaust | Total cfm | Notes
Auditorium Area | Auditorium_FF_Zn | 755.1425 | 10635.81 | 15 | 0.15 |  | 11327.1377 | 1595.3715 | 0 | 11327.1377
Exercise/Fitness Center and Gymnasium Areas | Aux_Gym_FF_Zn | 134.3461 | 13434.61 | 15 | 0.15 |  | 2015.1915 | 2015.1915 | 0 | 2015.1915
Restrooms | Bathrooms_FF_Zn | 11.3029 | 2260.58 | 0 | 0 | 0.5 | 0 | 0 | 1130.29 | 1130.29 | OA set to 0; exhaust 0.50 cfm/ft² is the same SchoolK8/SchoolHigh stand-in. T24 2025 Table 120.1-B toilets are 50/70 cfm per fixture and this prototype has no fixture count.
Restrooms | Bathrooms_SF_Zn | 11.3029 | 2260.58 | 0 | 0 | 0.5 | 0 | 0 | 1130.29 | 1130.29 | OA set to 0; exhaust 0.50 cfm/ft² is the same SchoolK8/SchoolHigh stand-in. T24 2025 Table 120.1-B toilets are 50/70 cfm per fixture and this prototype has no fixture count.
Dining Area (Cafeteria/Fast Food) | Cafeteria_FF_Zn | 221.6722 | 6717.34 | 15 | 0.15 |  | 3325.0833 | 1007.601 | 0 | 3325.0833
Classroom, Lecture, Training, Vocational Areas | Corner_Class_1_Pod_1_FF_Zn | 26.6432 | 1065.73 | 15 | 0.15 |  | 399.6487 | 159.8595 | 0 | 399.6487
Classroom, Lecture, Training, Vocational Areas | Corner_Class_1_Pod_1_SF_Zn | 26.6432 | 1065.73 | 15 | 0.15 |  | 399.6487 | 159.8595 | 0 | 399.6487
Classroom, Lecture, Training, Vocational Areas | Corner_Class_1_Pod_2_FF_Zn | 26.6427 | 1065.71 | 15 | 0.15 |  | 399.6413 | 159.8565 | 0 | 399.6413
Classroom, Lecture, Training, Vocational Areas | Corner_Class_1_Pod_2_SF_Zn | 26.6427 | 1065.71 | 15 | 0.15 |  | 399.6413 | 159.8565 | 0 | 399.6413
Classroom, Lecture, Training, Vocational Areas | Corner_Class_1_Pod_3_FF_Zn | 26.6438 | 1065.75 | 15 | 0.15 |  | 399.6562 | 159.8625 | 0 | 399.6562
Classroom, Lecture, Training, Vocational Areas | Corner_Class_1_Pod_3_SF_Zn | 26.6438 | 1065.75 | 15 | 0.15 |  | 399.6562 | 159.8625 | 0 | 399.6562
Classroom, Lecture, Training, Vocational Areas | Corner_Class_2_Pod_1_FF_Zn | 26.6432 | 1065.73 | 15 | 0.15 |  | 399.6487 | 159.8595 | 0 | 399.6487
Classroom, Lecture, Training, Vocational Areas | Corner_Class_2_Pod_1_SF_Zn | 26.6432 | 1065.73 | 15 | 0.15 |  | 399.6487 | 159.8595 | 0 | 399.6487
Classroom, Lecture, Training, Vocational Areas | Corner_Class_2_Pod_2_FF_Zn | 26.6438 | 1065.75 | 15 | 0.15 |  | 399.6562 | 159.8625 | 0 | 399.6562
Classroom, Lecture, Training, Vocational Areas | Corner_Class_2_Pod_2_SF_Zn | 26.6438 | 1065.75 | 15 | 0.15 |  | 399.6562 | 159.8625 | 0 | 399.6562
Classroom, Lecture, Training, Vocational Areas | Corner_Class_2_Pod_3_FF_Zn | 26.6427 | 1065.71 | 15 | 0.15 |  | 399.6413 | 159.8565 | 0 | 399.6413
Classroom, Lecture, Training, Vocational Areas | Corner_Class_2_Pod_3_SF_Zn | 26.6427 | 1065.71 | 15 | 0.15 |  | 399.6413 | 159.8565 | 0 | 399.6413
Corridor Area | Corridor_Pod_1_FF_Zn | 17.224 | 3444.79 | 15 | 0.15 |  | 258.3593 | 516.7185 | 0 | 516.7185
Corridor Area | Corridor_Pod_1_SF_Zn | 17.224 | 3444.79 | 15 | 0.15 |  | 258.3593 | 516.7185 | 0 | 516.7185
Corridor Area | Corridor_Pod_2_FF_Zn | 17.2237 | 3444.75 | 15 | 0.15 |  | 258.3562 | 516.7125 | 0 | 516.7125
Corridor Area | Corridor_Pod_2_SF_Zn | 17.2237 | 3444.75 | 15 | 0.15 |  | 258.3562 | 516.7125 | 0 | 516.7125
Corridor Area | Corridor_Pod_3_FF_Zn | 17.2237 | 3444.75 | 15 | 0.15 |  | 258.3562 | 516.7125 | 0 | 516.7125
Corridor Area | Corridor_Pod_3_SF_Zn | 17.2237 | 3444.75 | 15 | 0.15 |  | 258.3562 | 516.7125 | 0 | 516.7125
Exercise/Fitness Center and Gymnasium Areas | Gym_FF_Zn | 128.3742 | 5134.97 | 15 | 0.15 |  | 1925.6137 | 770.2455 | 0 | 1925.6137
Kitchen/Food Preparation Area | Kitchen_FF_Zn | 128.3742 | 5134.97 | 15 | 0.15 | 0.7 | 1925.6137 | 770.2455 | 3594.479 | 3594.479 | 15 cfm/person and Ra 0.15 from Table 120.1-A Kitchen (cooking); exhaust 0.70 cfm/ft² from Table 120.1-B Kitchens – commercial.
Library (Reading Area) | Library_Media_Center_SF_Zn | 128.372 | 5134.88 | 15 | 0.15 |  | 1925.58 | 770.232 | 0 | 1925.58
Lobby, Main Entry | Lobby_FF_Zn | 128.372 | 5134.88 | 15 | 0.15 |  | 1925.58 | 770.232 | 0 | 1925.58
Lobby, Main Entry | Lobby_SF_Zn | 74.6005 | 2260.62 | 15 | 0.15 |  | 1119.0069 | 339.093 | 0 | 1119.0069
Corridor Area | Main_Corridor_FF_Zn | 61.3596 | 12271.92 | 15 | 0.15 |  | 920.394 | 1840.788 | 0 | 1840.788
Corridor Area | Main_Corridor_SF_Zn | 61.3596 | 12271.92 | 15 | 0.15 |  | 920.394 | 1840.788 | 0 | 1840.788
Electrical, Mechanical, Telephone Rooms | Mech_FF_Zn | 18.4083 | 3681.67 | 15 | 0.15 |  | 276.1252 | 552.2505 | 0 | 552.2505
Electrical, Mechanical, Telephone Rooms | Mech_SF_Zn | 18.4083 | 3681.67 | 15 | 0.15 |  | 276.1252 | 552.2505 | 0 | 552.2505
Classroom, Lecture, Training, Vocational Areas | Mult_Class_1_Pod_1_FF_Zn | 128.3725 | 5134.9 | 15 | 0.15 |  | 1925.5875 | 770.235 | 0 | 1925.5875
Classroom, Lecture, Training, Vocational Areas | Mult_Class_1_Pod_1_SF_Zn | 128.3725 | 5134.9 | 15 | 0.15 |  | 1925.5875 | 770.235 | 0 | 1925.5875
Classroom, Lecture, Training, Vocational Areas | Mult_Class_1_Pod_2_FF_Zn | 128.37 | 5134.8 | 15 | 0.15 |  | 1925.55 | 770.22 | 0 | 1925.55
Classroom, Lecture, Training, Vocational Areas | Mult_Class_1_Pod_2_SF_Zn | 0 | 0 | 15 | 0.15 |  | 0 | 0 | 0 | 0
Classroom, Lecture, Training, Vocational Areas | Mult_Class_1_Pod_3_FF_Zn | 0 | 0 | 15 | 0.15 |  | 0 | 0 | 0 | 0
Classroom, Lecture, Training, Vocational Areas | Mult_Class_1_Pod_3_SF_Zn | 0 | 0 | 15 | 0.15 |  | 0 | 0 | 0 | 0
Classroom, Lecture, Training, Vocational Areas | Mult_Class_2_Pod_1_FF_Zn | 0 | 0 | 15 | 0.15 |  | 0 | 0 | 0 | 0
Classroom, Lecture, Training, Vocational Areas | Mult_Class_2_Pod_1_SF_Zn | 74.6005 | 2260.62 | 15 | 0.15 |  | 1119.0069 | 339.093 | 0 | 1119.0069
Classroom, Lecture, Training, Vocational Areas | Mult_Class_2_Pod_2_FF_Zn | 61.3596 | 12271.92 | 15 | 0.15 |  | 920.394 | 1840.788 | 0 | 1840.788
Classroom, Lecture, Training, Vocational Areas | Mult_Class_2_Pod_2_SF_Zn | 61.3596 | 12271.92 | 15 | 0.15 |  | 920.394 | 1840.788 | 0 | 1840.788
Classroom, Lecture, Training, Vocational Areas | Mult_Class_2_Pod_3_FF_Zn | 18.4083 | 3681.67 | 15 | 0.15 |  | 276.1252 | 552.2505 | 0 | 552.2505
Classroom, Lecture, Training, Vocational Areas | Mult_Class_2_Pod_3_SF_Zn | 18.4083 | 3681.67 | 15 | 0.15 |  | 276.1252 | 552.2505 | 0 | 552.2505
Office Area (>250 square feet) | Offices_FF_Zn | 128.3725 | 5134.9 | 15 | 0.15 |  | 1925.5875 | 770.235 | 0 | 1925.5875
Office Area (>250 square feet) | Offices_SF_Zn | 128.3725 | 5134.9 | 15 | 0.15 |  | 1925.5875 | 770.235 | 0 | 1925.5875
| Total (46 spaces) | 3773.418 | 210906.64 |  |  |  | 47367.7193 | 26819.22 | 5855.059 | 57633.385

## Water Heater
Water Heater -SchoolLarge
Vintage | WH Type | Efficiency | Number of WH | Tank Volume (gal) | Tank Loss | Source
Existing | Gas | 0.8 | 3 | See table below for CZ-specific values: Climate Zone Water Heater Sizing and Loss Coefficients, Storage Volume column (col F) | See table below: Climate Zone Water Heater Sizing and Loss Coefficients, Standby Loss column (col G) | See table below for sources: Climate Zone Water Heater Sizing and Loss Coefficients
New Construction | Gas | 0.8 | 3 | See table below for CZ-specific values: Climate Zone Water Heater Sizing and Loss Coefficients, Storage Volume column (col F) | See table below: Climate Zone Water Heater Sizing and Loss Coefficients, Standby Loss column (col G) | See table below for sources: Climate Zone Water Heater Sizing and Loss Coefficients
Peak Hot Water Consumption
Space Name | Baseline WH Type [T24, 2022, Appendix 5.4A , sheet: "2022 SpaceFuncData-Input"] | New Construction: Baseline WH Type ACM 2025 | Total Area (ft²) | Number of People | Hot Water Usage Specification (gal/hr per person) [T24, 2022, Appendix 5.4A , sheet: "2022 SpaceFuncData-Input"] | Peak Hot Water Usage (gal/hr) | Peak Hot Water Usage (gal/min)
Auditorium_FF_Zn | Gas |  | 10635.81 | 755.1425 | 0.09 | 67.9628 | 1.1327
Aux_Gym_FF_Zn | Gas |  | 13434.61 | 134.3461 | 0.18 | 24.1823 | 0.40304
Bathrooms_FF_Zn | Gas |  | 2260.58 | 11.3029 | 0 | 0 | 0
Bathrooms_SF_Zn | Gas |  | 2260.58 | 11.3029 | 0 | 0 | 0
Cafeteria_FF_Zn | Gas |  | 6717.34 | 221.6722 | 0.578 | 128.1265 | 2.1354
Corner_Class_1_Pod_1_FF_Zn | Gas |  | 1065.73 | 26.6432 | 0.18 | 4.7958 | 0.07993
Corner_Class_1_Pod_1_SF_Zn | Gas |  | 1065.73 | 26.6432 | 0.18 | 4.7958 | 0.07993
Corner_Class_1_Pod_2_FF_Zn | Gas |  | 1065.71 | 26.6427 | 0.18 | 4.7957 | 0.079928
Corner_Class_1_Pod_2_SF_Zn | Gas |  | 1065.71 | 26.6427 | 0.18 | 4.7957 | 0.079928
Corner_Class_1_Pod_3_FF_Zn | Gas |  | 1065.75 | 26.6438 | 0.18 | 4.7959 | 0.079931
Corner_Class_1_Pod_3_SF_Zn | Gas |  | 1065.75 | 26.6438 | 0.18 | 4.7959 | 0.079931
Corner_Class_2_Pod_1_FF_Zn | Gas |  | 1065.73 | 26.6432 | 0.18 | 4.7958 | 0.07993
Corner_Class_2_Pod_1_SF_Zn | Gas |  | 1065.73 | 26.6432 | 0.18 | 4.7958 | 0.07993
Corner_Class_2_Pod_2_FF_Zn | Gas |  | 1065.75 | 26.6438 | 0.18 | 4.7959 | 0.079931
Corner_Class_2_Pod_2_SF_Zn | Gas |  | 1065.75 | 26.6438 | 0.18 | 4.7959 | 0.079931
Corner_Class_2_Pod_3_FF_Zn | Gas |  | 1065.71 | 26.6427 | 0.18 | 4.7957 | 0.079928
Corner_Class_2_Pod_3_SF_Zn | Gas |  | 1065.71 | 26.6427 | 0.18 | 4.7957 | 0.079928
Corridor_Pod_1_FF_Zn | Gas |  | 3444.79 | 17.224 | 0 | 0 | 0
Corridor_Pod_1_SF_Zn | Gas |  | 3444.79 | 17.224 | 0 | 0 | 0
Corridor_Pod_2_FF_Zn | Gas |  | 3444.75 | 17.2237 | 0 | 0 | 0
Corridor_Pod_2_SF_Zn | Gas |  | 3444.75 | 17.2237 | 0 | 0 | 0
Corridor_Pod_3_FF_Zn | Gas |  | 3444.75 | 17.2237 | 0 | 0 | 0
Corridor_Pod_3_SF_Zn | Gas |  | 3444.75 | 17.2237 | 0 | 0 | 0
Gym_FF_Zn | Gas |  | 21271.52 | 212.7152 | 0.18 | 38.2887 | 0.63815
Kitchen_FF_Zn | Gas |  | 2325.26 | 6.9758 | 0.578 | 4.032 | 0.0672
Library_Media_Center_SF_Zn | Gas |  | 9042.6 | 90.426 | 0.18 | 16.2767 | 0.27128
Lobby_FF_Zn | Gas |  | 2260.62 | 74.6005 | 0.09 | 6.714 | 0.1119
Lobby_SF_Zn | Gas |  | 2260.62 | 74.6005 | 0.09 | 6.714 | 0.1119
Main_Corridor_FF_Zn | Gas |  | 12271.92 | 61.3596 | 0 | 0 | 0
Main_Corridor_SF_Zn | Gas |  | 12271.92 | 61.3596 | 0 | 0 | 0
Mech_FF_Zn | Gas |  | 3681.67 | 18.4083 | 0.18 | 3.3135 | 0.055225
Mech_SF_Zn | Gas |  | 3681.67 | 18.4083 | 0.18 | 3.3135 | 0.055225
Mult_Class_1_Pod_1_FF_Zn | Gas |  | 5134.9 | 128.3725 | 0.18 | 23.107 | 0.38512
Mult_Class_1_Pod_1_SF_Zn | Gas |  | 5134.9 | 128.3725 | 0.18 | 23.107 | 0.38512
Mult_Class_1_Pod_2_FF_Zn | Gas |  | 5134.8 | 128.37 | 0.18 | 23.1066 | 0.38511
Mult_Class_1_Pod_2_SF_Zn | Gas |  | 5134.8 | 128.37 | 0.18 | 23.1066 | 0.38511
Mult_Class_1_Pod_3_FF_Zn | Gas |  | 5134.97 | 128.3742 | 0.18 | 23.1074 | 0.38512
Mult_Class_1_Pod_3_SF_Zn | Gas |  | 5134.97 | 128.3742 | 0.18 | 23.1074 | 0.38512
Mult_Class_2_Pod_1_FF_Zn | Gas |  | 5134.88 | 128.372 | 0.18 | 23.107 | 0.38512
Mult_Class_2_Pod_1_SF_Zn | Gas |  | 5134.88 | 128.372 | 0.18 | 23.107 | 0.38512
Mult_Class_2_Pod_2_FF_Zn | Gas |  | 5134.97 | 128.3742 | 0.18 | 23.1074 | 0.38512
Mult_Class_2_Pod_2_SF_Zn | Gas |  | 5134.97 | 128.3742 | 0.18 | 23.1074 | 0.38512
Mult_Class_2_Pod_3_FF_Zn | Gas |  | 5134.8 | 128.37 | 0.18 | 23.1066 | 0.38511
Mult_Class_2_Pod_3_SF_Zn | Gas |  | 5134.8 | 128.37 | 0.18 | 23.1066 | 0.38511
Offices_FF_Zn | Gas |  | 5726.97 | 28.6349 | 0.18 | 5.1543 | 0.085905
Offices_SF_Zn | Gas |  | 5726.97 | 28.6349 | 0.18 | 5.1543 | 0.085905
Total | Gas storage |  |  |  |  | 644.066 | Minimum peak hot water usage is 75 gal according to ACM 2025
Total | Electric resistance |  |  |  |  | 0
Number of identical water heaters | 3
Design supply temperature (°F) | 135 | CEC-400-2022-009-CMF-REV2-AP5.4B
WH system factor | 0.6 | 2025 ACM §5.9.2 Rated Capacity
Water mass conversion (lb/gal) | 8.2877 | 2025 ACM §5.9.2 Rated Capacity
Reheat multiplier | 0.4 | 2025 ACM §5.9.2 Storage Volume
Climate Zone Water Heater Sizing and Loss Coefficients
Climate Zone | Minimum Monthly Mains Temp (°F) [T24 2022 - Appendix 5.4B] | Heat Output (Btu/hr) [ACM, 2025, 5.9.2: Rated capacity section] | WH Capacity (Btu/hr) [ACM, 2025, 5.9.2: Rated capacity section] | Required Energy Input (Btu/hr) | Storage Volume (gal) | Standby Loss [Title 20, §1605.1 Table F-4; Appendix B: Water Heating Calculation Method] |  | Off/On Cycle Loss Coefficient to Ambient Temp |  | Source/Note
CZ01 | 47.9 | 154974.8799 | 92984.9279 | 120000 | 90 | 1193.5516 | Btu/hr | 17.0507 | Btu/h·°F | Required Energy Input: vendor/available catalog size (Market data table). Storage Volume: standard/available catalog tank size (Market data table).
CZ02 | 50.8 | 149814.9815 | 89888.9889 | 120000 | 90 | 1193.5516 | Btu/hr | 17.0507 | Btu/h·°F
CZ03 | 52.2 | 147323.996 | 88394.3976 | 120000 | 90 | 1193.5516 | Btu/hr | 17.0507 | Btu/h·°F
CZ04 | 52.7 | 146434.3584 | 87860.615 | 120000 | 90 | 1193.5516 | Btu/hr | 17.0507 | Btu/h·°F
CZ05 | 51.6 | 148391.5612 | 89034.9367 | 120000 | 90 | 1193.5516 | Btu/hr | 17.0507 | Btu/h·°F
CZ06 | 56.8 | 139139.3296 | 83483.5978 | 120000 | 90 | 1193.5516 | Btu/hr | 17.0507 | Btu/h·°F
CZ07 | 58.4 | 136292.4891 | 81775.4934 | 120000 | 90 | 1193.5516 | Btu/hr | 17.0507 | Btu/h·°F
CZ08 | 58.4 | 136292.4891 | 81775.4934 | 120000 | 90 | 1193.5516 | Btu/hr | 17.0507 | Btu/h·°F
CZ09 | 57.6 | 137715.9093 | 82629.5456 | 120000 | 90 | 1193.5516 | Btu/hr | 17.0507 | Btu/h·°F
CZ10 | 57.1 | 138605.547 | 83163.3282 | 120000 | 90 | 1193.5516 | Btu/hr | 17.0507 | Btu/h·°F
CZ11 | 50.5 | 150348.7641 | 90209.2584 | 120000 | 90 | 1193.5516 | Btu/hr | 17.0507 | Btu/h·°F
CZ12 | 51.4 | 148747.4163 | 89248.4498 | 120000 | 90 | 1193.5516 | Btu/hr | 17.0507 | Btu/h·°F
CZ13 | 51.7 | 148213.6337 | 88928.1802 | 120000 | 90 | 1193.5516 | Btu/hr | 17.0507 | Btu/h·°F
CZ14 | 50.1 | 151060.4742 | 90636.2845 | 120000 | 90 | 1193.5516 | Btu/hr | 17.0507 | Btu/h·°F
CZ15 | 63.2 | 127751.9676 | 76651.1805 | 99900 | 90 | 1168.4266 | Btu/hr | 16.6918 | Btu/h·°F
CZ16 | 41.4 | 166540.1694 | 99924.1017 | 125000 | 90 | 1199.8016 | Btu/hr | 17.14 | Btu/h·°F
Market data
Catalog gas input (kBtu/h) | Input source | Elec resistance tank (kW) | Elec resistance (Btu/h) | Catalog gas tank (gal) | Tank source | Elec tank (gal) | Elec tank source | Sources and links → Note tab
30000 | Grainger | 6 | 20472 | 30 | Grainger | 6 | Grainger
32000 | Grainger | 9 | 30708 | 40 | Grainger | 12 | Grainger
34000 | Grainger | 12 | 40944 | 50 | Both | 20 | Grainger
36000 | Grainger | 13.5 | 46062 | 55 | ENERGY STAR | 30 | Grainger
38000 | Grainger | 15 | 51180 | 60 | Both | 40 | Grainger
40000 | Grainger | 18 | 61416 | 65 | Both | 50 | Grainger
42000 | Grainger | 24 | 81888 | 75 | Both | 80 | Grainger
50000 | Grainger | 27 | 92124 | 80 | Both | 120 | Grainger
60000 | Grainger | 30 | 102360 | 90 | ENERGY STAR
65000 | Grainger | 36 | 122832 | 100 | Both
75000 | Grainger | 40.5 | 138186 | 110 | ENERGY STAR
75100 | Grainger | 45 | 153540 | 119 | Both
76000 | Both | 54 | 184248 | 120 | Grainger
80000 | Grainger |  |  | 125 | ENERGY STAR
99900 | ENERGY STAR
100000 | Both
120000 | Both
125000 | ENERGY STAR
130000 | Both
145000 | ENERGY STAR
150000 | Both
154000 | Grainger
160000 | ENERGY STAR
175000 | ENERGY STAR
180000 | Grainger
199000 | Both
199900 | Both
200000 | ENERGY STAR
250000 | Both
251000 | Both
275000 | Grainger
285000 | ENERGY STAR
300000 | Both
305000 | Grainger
320000 | ENERGY STAR
365000 | Grainger
390000 | Grainger
398000 | ENERGY STAR
399000 | ENERGY STAR
399900 | Both
500000 | Grainger

## Interior Lights
Interior Lighting - SchoolLarge
Space Type | New Construction |  |  | Existing
| Lighting density (W/ft²) | Additional lighting power for porTable lighting (W/ft²) | Source | LPD (W/ft²) | Additional LPD for PorTable Lighting (W/ft²) | Source
Auditorium Area | 0.7 |  | T24, 2025, Table 140.6 C (Area category method) | 1.4 |  | T24, 2016, Table 140.6 C (Area category method)
Exercise/Fitness Center and Gymnasium Areas | 0.5 |  |  | 1
Restrooms | 0.65 |  |  | 0.6
Dining Area (Cafeteria/Fast Food) | 0.45 | 0.25 |  | 1
Classroom, Lecture, Training, Vocational Areas | 0.6 |  |  | 1.2
Corridor Area | 0.4 |  |  | 0.6
Kitchen/Food Preparation Area | 0.95 |  |  | 1.2
Library (Reading Area) | 0.8 |  |  | 1.1
Lobby, Main Entry | 0.7 | 0.125 |  | 0.95 | 0.25
Electrical, Mechanical, Telephone Rooms | 0.4 |  |  | 0.55
Office Area (>250 square feet) | 0.6 | 0.1 |  | 0.75 | 0.2

## Ext Lighting
Exterior Lighting - SchoolLarge
Motion Controlled Luminaires (W) | Non-motion Controlled Luminaires (W) | Total (W) | Source
2296.1931 | 2495.0716 | 4791.2648 | T24, 2022 & 2025 2019 Outdoor Lighting CASE report PNNL 90.1-2010 TSD
Exterior Lighting
Items (Assume LZ2) | Assumptions [2019 Outdoor Lighting CASE Report & PNNL 90.1-2010 TS] |  | Unit | Lighting Power Allowance [T24, 2025, Table 140.7-A & 140.7-B] | Unit | Exterior Lighting Power (W)
IWA (Initial Wattage Allowance) |  |  |  | 200 | (W) | 200
Parking area | 400 ft² for every parking space 1 parking space per 830 ft² of gross building area | 101641.7446 | (ft²) | 0.019 | (W/ft²) | 1931.1931
Building Entrance | 5 building entrance per PNNL Model (1 per 10,000 ft² footprint) | 11 | (count) | 15 | (W/ea) | 165
Hardscape Ornamental Light | 0.1 ft² per 1 ft² of gross building area for hardscape ornamental light | 21090.662 | (ft²) | 0.007 | (W/ft²) | 147.6346
Building façade | 0.1 W per 1 ft² of facade area Façade Area = Perimeter × 0.5 × max(height, 30) per this sheet's CASE note. Was 0.5×4×(P×H) = 2× wall area. | 23474.37 | (ft²) | 0.1 | (W/ft²) | 2347.437
Motion Controlled Luminaires (W) | [5 empty] | 2296.1931
Non-motion-controlled Luminaires | [5 empty] | 2495.0716
Total | [5 empty] | 4791.2648
Max Height (ft) | 28
Building footprint | 105453.31
Floors | 2
Perimeter(ft) | 1564.958
Total floor area (ft²) | 210906.62

## Equipment
Equipment - SchoolLarge
Space Type | Plug load Power Density (W/ft²) | Gas Power Density (Btu/hr-ft²) | Refrigeration Power Density (W/ft²) | Source
Auditorium Area | 1 | 0 | 0 | T24 2022 - Appendix 5.4A
Exercise/Fitness Center and Gymnasium Areas | 0.5 | 0 | 0
Restrooms | 0 | 0 | 0
Dining Area (Cafeteria/Fast Food) | 0.5 | 0 | 0.25
Corridor Area | 0 | 0 | 0 | T24 2022 - Appendix 5.4A
Kitchen/Food Preparation Area | 1.5 | 17.5377 | 1.12 | Plug 1.5 W/ft²; gas 17.54 Btu/h-ft²; refrigeration 1.12 W/ft² — all T24 2022 Appendix 5.4A (ACM 2025 table unchanged). Not from the Plug Loads and Schedules project.
Library (Reading Area) | 1.5 | 0 | 0 | T24 2022 - Appendix 5.4A
Lobby, Main Entry | 0.5 | 0 | 0
Electrical, Mechanical, Telephone Rooms | 3 | 0 | 0
Classroom, Lecture, Training, Vocational Areas | 0.8 | 0 | 0 | Plug 0.8 W/ft² — Plug Loads and Schedules project with CEC, 2025 (Appendix 5.4A classroom is 1.0 W/ft²). Gas 0 and refrigeration 0 — Appendix 5.4A has no process gas or commercial refrigeration for this space.
Office Area (>250 square feet) | 0.7 | 0 | 0
Elevator
Vintage | Class | Number of elevators (ne) | Cab Lighting Power Limit (W/ft2) | Fan Power Limit (W/CFM) | Cab Ventilation Fan & Lighting Shutoff | Design Motor Load (W) | Fan Load (W) | Lighting Load (W) | Total (W) | Note
Existing | F/G | 2 | 1.14 | 0.33 | When stopped and unoccupied with doors closed for over 15 minutes, cab interior lighting and ventilation shall be de-energized until required for operation. | 53481.84 | 165 | 68.17 | 53715.01 | Design load is calculated according to ISO 25745-2 method using Class F/G. Cab lighting and fan requirements are based on ASHRAE 90.1 2013.
New Construction | E | 2 | 0.6 | 0.33 | When the elevator cab is stopped and unoccupied with doors closed for over 15 minutes, the cab interior lighting and ventilation fans shall be switched off until elevator cab operation resumes. | 27849.14 | 165 | 35.88 | 28050.02 | Design load is calculated according to ISO 25745-2 method using Class E. Cab lighting and fan requirements are based on T24 2025 §120.6 (f).
Secondary School Elevator Calculations
Symbol | Definition | Value | Units | Source
E | Annual energy consumption of the elevator - Existing | 31407.21 | kWh/year | Calculated
| Annual energy consumption of the elevator - New Construction | 16354.41 | kWh/year | Calculated
C1 | Running-energy coefficient | 3.65 for Class E; 5.47 for Class F | Coefficient | ISO 25745-2 Table 7
C2 | Idle/standby coefficient | 800 for Class E; 1,600 for Class F | Coefficient | ISO 25745-2 Table 7
Q | Rated load of elevator | 1361 | kg | Assumed for all prototypes
Elevator Size | Cab floor area | 29.9 | ft^2 | W=6.781 ft, L=4.406 ft; assumed based on representative manufacturer
CFM | Cab fan airflow | 250 | cfm | Assumed for multifamily and commercial prototypes
cat | Usage category | 2 | - | ISO 25745-2 Table A.1
d | Operating days per year | 260 | days/year | ISO 25745-2 Table A.1
nf | Number of floors | 2 | floors | Prototype assumptions
h | Floor-to-floor height | 4.02 | m | Prototype assumptions
v | Elevator lift speed | 1 | m/s | ISO 25745-2 Table A.1
nd | Number of trips per day | 125 | trips/day | ISO 25745-2 Table A.1
S_pct | Percent of average travel distance | 1 | % | ISO 25745-2 Table 2
a | Acceleration | 1 | m/s^2 | Annex B of ISO 25745-2
j | Jerk | 1.25 | m/s^3 | Annex B of ISO 25745-2
td | Door time | 8 | seconds | Annex B of ISO 25745-2
S_av | Average distance traveled per trip | 8.04 | m/trip | Calculated (nf * h * S_pct)
t_av | Average trip time | 17.84 | seconds/trip | Calculated (S_av/v + v/a + a/j + td)
t_nr | Time not running per day | 23.38 | hours/day | Calculated (24 - nd * t_av)
Standby Hours | Annual standby hours | 8598.94 | hours/year | Calculated (24*(365-d)+t_nr*d)
Total light level | Total light level | 40 | lm/ft2 | PNNL Prototypes
EFLH | Equivalent full load hours | 587.25 | hours | Calculated using the elevator schedule

## Schedules
Schedules - SchoolLarge
Zone | Schedule Category | Schedule | Source | Type | Hour
[5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
School Zones | Classroom | Occupancy | T24 2022 - Appendix 5.4B [School] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.75 | 0.9 | 0.9 | 0.8 | 0.8 | 0.8 | 0.8 | 0.45 | 0.15 | 0.05 | 0.15 | 0.2 | 0.2 | 0.1 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School Zones | Classroom | Lights | T24 2022 - Appendix 5.4B [School] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.6 | 0.65 | 0.65 | 0.65 | 0.55 | 0.55 | 0.55 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.3 | 0.05 | 0.05
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
School Zones | Classroom | ElecEquipment | T24 2022 - Appendix 5.4B [School] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.85 | 0.95 | 0.95 | 0.95 | 0.8 | 0.8 | 0.8 | 0.7 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.3 | 0.05 | 0.05
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
School Zones | Classroom | ServiceHotWater | T24 2022 - Appendix 5.4B [School] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09
|  |  |  | Saturday | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
|  |  |  | Sunday | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
School Zones | Classroom | GasEquipment | T24 2022 - Appendix 5.4B [School] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.75 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School Zones | Classroom | Refrigeration | T24 2022 - Appendix 5.4B [School] | Weekday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Saturday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Sunday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
School Zones | Classroom | HVACAvail | T24 2022 - Appendix 5.4B [School] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School Zones | Classroom | Infiltration | T24 2022 - Appendix 5.4B [School] | Weekday | 0 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1
|  |  |  | Saturday | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Sunday | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
School Zones | Classroom | HtgSetpt | T24 2022 - Appendix 5.4B [School] | Weekday | 60 | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 60 | 60
|  |  |  | Saturday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  |  | Sunday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
School Zones | Classroom | ClgSetpt | T24 2022 - Appendix 5.4B [School] | Weekday | 85 | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 85 | 85
|  |  |  | Saturday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
|  |  |  | Sunday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
School Zones | Classroom | Infiltration | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
Kitchen |  | Other
Kitchen Zone | Kitchen | Occupancy | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitchen Zone | Kitchen | HVACAvail | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitchen Zone | Kitchen | Lights | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitchen Zone | Kitchen | ElecEquipment | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.3 | 0.9 | 0.9 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.7 | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitchen Zone | Kitchen | HtgSetpt | T24 2022 - Appendix 5.4B (school kitchen occupied 70/75; not commercial restaurant 66–79) | Weekday | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  |  | Saturday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  |  | Sunday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Kitchen Zone | Kitchen | ClgSetpt | T24 2022 - Appendix 5.4B (school kitchen occupied 70/75; not commercial restaurant 66–79) | Weekday | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
|  |  |  | Saturday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
|  |  |  | Sunday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
Kitchen Zone | Kitchen | OAControl | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitchen Zone | Kitchen | Infiltration | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
Kitchen Zone | Kitchen | Refrigeration | T24 2022 - Appendix 5.4B [School] | Weekday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Saturday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Sunday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
Kitchen Zone | Kitchen | GasEquipment | T24 2022 - Appendix 5.4B [School] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.75 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitchen Zone | Kitchen | ServiceHotWater | T24 2022 - Appendix 5.4B [School] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09
|  |  |  | Saturday | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
|  |  |  | Sunday | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
Gym |  | Other
Gym Zone | Gym | Occupancy | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.5 | 0.25 | 0.25 | 0.05 | 0.25 | 0.95 | 0.95 | 0.25 | 0.2 | 0.2 | 0.2 | 0.15 | 0.15 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gym Zone | Gym | HVACAvail | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gym Zone | Gym | Lights | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gym Zone | Gym | ElecEquipment | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.3 | 0.9 | 0.9 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.7 | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gym Zone | Gym | HtgSetpt | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 60 | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 60 | 60 | 60 | 60
|  |  |  | Saturday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  |  | Sunday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Gym Zone | Gym | ClgSetpt | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 85 | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 85 | 85 | 85 | 85
|  |  |  | Saturday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
|  |  |  | Sunday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
Gym Zone | Gym | OAControl | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gym Zone | Gym | Infiltration | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
Gym Zone | Gym | ServiceHotWater | T24 2022 - Appendix 5.4B [School] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09
|  |  |  | Saturday | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
|  |  |  | Sunday | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
Other |  | Other | [26 empty] | EFLH
| Building | Elevator | T24 2022 - Appendix 5.4B, [School] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 587.25
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Building | ExtLightingNonMotionCtrl |  | Weekday | bar: Hour 1 to Hour 24
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
| Building | ExtLightingMotionCtrl |  | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Auditorium | Building | PerformanceSpcPeopleActivityLevel | Based on Activity level schedules in CEC Prototypes | Weekday | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6
|  |  |  | Saturday | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6
|  |  |  | Sunday | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6
Gym | Building | GymPeopleActivityLevel | Based on Activity level schedules in CEC Prototypes | Weekday | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2
|  |  |  | Saturday | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2
|  |  |  | Sunday | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2
Classroom | Building | MeetingPeopleActivityLevel | Based on Activity level schedules in CEC Prototypes | Weekday | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2
|  |  |  | Saturday | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2
|  |  |  | Sunday | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2
DiningArea | Building | DiningAreaPeopleActivityLevel | Based on Activity level schedules in CEC Prototypes | Weekday | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2
|  |  |  | Saturday | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2
|  |  |  | Sunday | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2
Library, Office | Building | FunctionalAreaPeopleActivityLevel | Based on Activity level schedules in CEC Prototypes | Weekday | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
|  |  |  | Saturday | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
|  |  |  | Sunday | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
Lobby, Mech, Corridor, Restroom | Building | CommonAreaPeopleActivityLevel | Based on Activity level schedules in CEC Prototypes | Weekday | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5
|  |  |  | Saturday | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5
|  |  |  | Sunday | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5
Kitchen | Building | KitchenPeopleActivityLevel | Based on Activity level schedules in CEC Prototypes | Weekday | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033
|  |  |  | Saturday | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033
|  |  |  | Sunday | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033
Ancillary |  | Other
Mechanical Room | Ancillary | Occupancy | T24 2022 - Appendix 5.4B [School] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.75 | 0.9 | 0.9 | 0.8 | 0.8 | 0.8 | 0.8 | 0.45 | 0.15 | 0.05 | 0.15 | 0.2 | 0.2 | 0.1 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mechanical Room | Ancillary | Lights | T24 2022 - Appendix 5.4B [School] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.6 | 0.65 | 0.65 | 0.65 | 0.55 | 0.55 | 0.55 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.3 | 0.05 | 0.05
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Mechanical Room | Ancillary | ElecEquipment | T24 2022 - Appendix 5.4B [School] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.85 | 0.95 | 0.95 | 0.95 | 0.8 | 0.8 | 0.8 | 0.7 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.3 | 0.05 | 0.05
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Mechanical Room | Ancillary | ServiceHotWater | T24 2022 - Appendix 5.4B [School] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09
|  |  |  | Saturday | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
|  |  |  | Sunday | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
Mechanical Room | Ancillary | HVACAvail | T24 2022 - Appendix 5.4B [School] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mechanical Room | Ancillary | Infiltration | T24 2022 - Appendix 5.4B [School] | Weekday | 0 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1
|  |  |  | Saturday | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Sunday | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
#REF! | Ancillary | ClgSetpt |  | Weekday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  |  | Saturday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  |  | Sunday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
#REF! | Ancillary | HtgSetpt |  | Weekday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
|  |  |  | Saturday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
|  |  |  | Sunday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
AncillaryREstroom |  | Other
Restroom | AncillaryRestroom | Occupancy | T24 2022 - Appendix 5.4B [School] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.75 | 0.9 | 0.9 | 0.8 | 0.8 | 0.8 | 0.8 | 0.45 | 0.15 | 0.05 | 0.15 | 0.2 | 0.2 | 0.1 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Restroom | AncillaryRestroom | Lights | T24 2022 - Appendix 5.4B [School] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.6 | 0.65 | 0.65 | 0.65 | 0.55 | 0.55 | 0.55 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.3 | 0.05 | 0.05
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Restroom | AncillaryRestroom | ElecEquipment | T24 2022 - Appendix 5.4B [School] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.85 | 0.95 | 0.95 | 0.95 | 0.8 | 0.8 | 0.8 | 0.7 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.3 | 0.05 | 0.05
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Restroom | AncillaryRestroom | ServiceHotWater | T24 2022 - Appendix 5.4B [School] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09
|  |  |  | Saturday | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
|  |  |  | Sunday | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
Restroom | AncillaryRestroom | HVACAvail | T24 2022 - Appendix 5.4B [School] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Restroom | AncillaryRestroom | Infiltration | T24 2022 - Appendix 5.4B [School] | Weekday | 0 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1
|  |  |  | Saturday | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Sunday | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Restroom | AncillaryRestroom | HtgSetpt |  | Weekday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  |  | Saturday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  |  | Sunday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Restroom | AncillaryRestroom | ClgSetpt |  | Weekday | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
|  |  |  | Saturday | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
|  |  |  | Sunday | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80

## Energy Usage (hidden)
CalBEM Energy Consumption - Large School | [11 empty] | Energy Consumption - SchoolLarge
Prototype | CZ | CalBEM Electricity EUI (KBTU/ft²) | CalBEM Gas EUI (KBTU/ft²) | CalBEM Total EUI (KBTU/ft²) | New Construction Electricity EUI (KBTU/ft²) | New Construction Gas EUI (KBTU/ft²) | New Construction Total EUI (KBTU/ft²) | National Average | Acceptable Range (25% Higher) | Acceptable Range (25% Lower) | National Average Acceptable EUI Range | Prototype | CZ | Total Floorspace (Thousand of ft²) | CEUS 2023 Electricity EUI (kBtu/ft²) | CEUS 2023 Gas EUI (kBtu/ft²) | CEUS 2023 Total EUI (kBtu/ft²) | Acceptable Range (25% Higher) | Acceptable Range (25% Lower) | CEUS 2022 Acceptable EUI Range
Large School | 1 | [6 empty] | 84 | 105 | 63 | 42 | Large School | 1 | 7618.5337 | 32.3492 | 12.8481 | 55.3648 | 69.206 | 41.5236 | 27.6824
| 2 | [6 empty] | 84 | 105 | 63 | 42 |  | 2 | 11477.6706 | 15.4216 | 12.914 | 47.8933 | 59.8666 | 35.92 | 23.9466
| 3 | [6 empty] | 84 | 105 | 63 | 42 |  | 3 | 46411.8605 | 20.4796 | 12.7992 | 100.095 | 125.1187 | 75.0712 | 50.0475
| 4 | [6 empty] | 84 | 105 | 63 | 42 |  | 4 | 23032.968 | 21.4937 | 13.0198 | 106.6213 | 133.2767 | 79.966 | 53.3107
| 5 | [6 empty] | 84 | 105 | 63 | 42 |  | 5 | 5978.4428 | 11.9981 | 11.5852 | 59.1493 | 73.9366 | 44.362 | 29.5746
| 6 | [6 empty] | 84 | 105 | 63 | 42 |  | 6 | 57755.9589 | 22.6073 | 9.9467 | 82.3475 | 102.9344 | 61.7606 | 41.1737
| 7 | [6 empty] | 84 | 105 | 63 | 42 |  | 7 | 35149.9926 | 24.8484 | 6.97 | 88.5535 | 110.6918 | 66.4151 | 44.2767
| 8 | [6 empty] | 84 | 105 | 63 | 42 |  | 8 | 92353.4113 | 22.9353 | 8.8422 | 103.4418 | 129.3023 | 77.5814 | 51.7209
| 9 | [6 empty] | 84 | 105 | 63 | 42 |  | 9 | 141795.4506 | 26.7973 | 10.0891 | 119.1513 | 148.9391 | 89.3635 | 59.5757
| 10 | [6 empty] | 84 | 105 | 63 | 42 |  | 10 | 92589.8669 | 22.4904 | 10.109 | 67.4191 | 84.2739 | 50.5643 | 33.7096
| 11 | [6 empty] | 84 | 105 | 63 | 42 |  | 11 | 33810.4884 | 26.9287 | 8.7604 | 68.8393 | 86.0491 | 51.6294 | 34.4196
| 12 | [6 empty] | 84 | 105 | 63 | 42 |  | 12 | 108342.4341 | 31.7996 | 12.2303 | 85.5874 | 106.9842 | 64.1905 | 42.7937
| 13 | [6 empty] | 84 | 105 | 63 | 42 |  | 13 | 46676.8078 | 32.656 | 15.4735 | 57.7357 | 72.1696 | 43.3018 | 28.8678
| 14 | [6 empty] | 84 | 105 | 63 | 42 |  | 14 | 22787.7389 | 21.8072 | 11.4332 | 68.5025 | 85.6282 | 51.3769 | 34.2513
| 15 | [6 empty] | 84 | 105 | 63 | 42 |  | 15 | 54746.0029 | 21.9543 | 10.4391 | 47.7153 | 59.6441 | 35.7864 | 23.8576
| 16 | [6 empty] | 84 | 105 | 63 | 42 |  | 16 | 85267.8904 | 27.0269 | 11.6529 | 67.5765 | 84.4706 | 50.6824 | 33.7882
Ref: CEUS 2022 Report
And by applying FZ-CZ multipliers for converting FZ data to CZ data

## Weights (hidden)
% of Floor Area per CZ and Vintage Bin - Schools
Prototype | CZ | Vintage Bin
|  | Pre-1978 | 1978-1997 | 1998-2007 | 2008-2018 | Not available
Large School | 1 | [5 empty] | 0%
| 2 | [5 empty] | 0%
| 3 | [5 empty] | 0%
| 4 | [5 empty] | 0%
| 5 | [5 empty] | 0%
| 6 | [5 empty] | 0%
| 7 | [5 empty] | 0%
| 8 | [5 empty] | 0%
| 9 | [5 empty] | 0%
| 10 | [5 empty] | 0%
| 11 | [5 empty] | 0%
| 12 | [5 empty] | 0%
| 13 | [5 empty] | 0%
| 14 | [5 empty] | 0%
| 15 | [5 empty] | 0%
| 16 | [5 empty] | 0%
Statewide
Ref: CEUS 2022 dataset

## PV (hidden)
PV - SchoolLarge
TBD

## EV Charger (hidden)
EV Charger - SchoolLarge
TBD
Background Data [To be deleted prior to publication]

## Data (hidden)
Space Function
Aging Eye/Low-vision (Corridor Area)
Aging Eye/Low-vision (Dining)
Aging Eye/Low-vision (Lobby, Main Entry)
Aging Eye/Low-vision (Lounge/Waiting Area)
Aging Eye/Low-vision (Multipurpose Room)
Aging Eye/Low-vision (Religious Worship Area)
Aging Eye/Low-vision (Restroom)
Aging Eye/Low-vision (Stairwell)
Audience Seating Area
Auditorium Area
Auto Repair / Maintenance Area
Barber, Beauty Salon, Spa Area
Civic Meeting Place Area
Classroom, Lecture, Training, Vocational Areas
Concourse and Atria Area
Convention, Conference, Multipurpose and Meeting Area
Copy Room
Corridor Area
Dining Area (Bar/Lounge and Fine Dining)
Dining Area (Cafeteria/Fast Food)
Dining Area (Family and Leisure)
Electrical, Mechanical, Telephone Rooms
Exercise/Fitness Center and Gymnasium Areas
Financial Transaction Area
Healthcare Facility and Hospitals (Exam/Treatment Room)
Healthcare Facility and Hospitals (Imaging Room)
Healthcare Facility and Hospitals (Medical Supply Room)
Healthcare Facility and Hospitals (Nursery)
Healthcare Facility and Hospitals (Nurse's Station)
Healthcare Facility and Hospitals (Operating Room)
Healthcare Facility and Hospitals (Patient Room)
Healthcare Facility and Hospitals (Physical Therapy Room)
Healthcare Facility and Hospitals (Recovery Room)
Hotel Function Area
Kitchen/Food Preparation Area
Kitchenette or Residential Kitchen
Laboratory, Scientific
Laundry Area
Library (Reading Area)
Library (Stacks Area)
Lobby, Main Entry
Locker Room
Lounge, Breakroom, or Waiting Area
Manufacturing, Commercial & Industrial Work Area (Low Bay)
Manufacturing, Commercial & Industrial Work Area (High Bay)
Manufacturing, Commercial & Industrial Work Area (Precision)
Museum Area (Exhibition/Display)
Museum Area (Restoration Room)
Office Area (>250 square feet)
Office Area (<250 square feet)
Parking Garage Area (Parking Zone and Ramps)
Parking Garage Area (Daylight Adaptation Zones) (Note 2)
Pharmacy Area
Retail Sales Area (Grocery Sales)
Retail Sales Area (Retail Merchandise Sales)
Retail Sales Area (Fitting Room)
Religious Worship Area
Restrooms
Stairwell
Storage, Commercial/Industrial (Warehouse)
Storage, Commercial/Industrial (Refrigerated)
Storage, Commercial/Industrial (Shipping & Handling)
Storage (General)
Sports Arena - Playing Area (> 5,000 Spectators)
Sports Arena - Playing Area (2,000 - 5,000 Spectators)
Sports Arena - Playing Area (< 2,000 Spectators)
Sports Arena - Playing Area (Recreational)
Theater Area (Motion Picture)
Theater Area (Performance)
Transportation Function (Baggage Area)
Transportation Function (Ticketing Area)
Videoconferencing Studio
High-Rise Residential Living Spaces
Hotel/Motel Guest Room
All other
Attic
Reception Area
Elevator