## Notes
Data Sources
Dataset | Dodge 2023
CEUS 2022
ComStock 2023
Prototype | CEC Open parking garage prototype (CBECC 2022.3.1) | https://bees.noresco.com/software2022.html
Codes | Title 24, part 6, referred to as T24 (1984, 2001, 2007, 2013, 2016, 2022, 2025)
ASHRAE 90.1 (2022)
CFR Title 10 (2008, 2010, 2025)
ACM 2022
| T24 2022 - Appendix 5.4A and Appendix 5.4B | https://www.energy.ca.gov/publications/2022/2022-nonresidential-and-multifamily-alternative-calculation-method-reference
Other | 2022 Reduced infiltration CASE report | https://title24stakeholders.com/wp-content/uploads/2020/10/2022-T24-Final-CASE-Report_Reduce-Infiltration.pdf
| 2019 Outdoor Lighting CASE Report | https://title24stakeholders.com/wp-content/uploads/2016/10/T24-2019-CASE-Study-Results-Report-Outdoor-Sources_Final_with-Attachments.pdf
| 2019 High Efficiency Fume Hoods in Laboratory Spaces CASE Report | https://title24stakeholders.com/wp-content/uploads/2017/09/2019-T24-CASE-Report_Fume-Hoods_Final_September-2017.pdf?
| PNNL 20405, 2011 | file:///N:/Prj_SUS/2023/S23668%20SCE%20CA%20Prototypes%20Development/Technical/NR/0_Input%20data/Lighting/PNNL-20405.pdf
| Air leakage Memo, NORESCO, 2025 | Infiltration_rate_report_14May2025-Short-Version.docx
Water Heater | ENERGY STAR certified commercial water heaters (gas storage input ≥76 kBtu/h; ES tank sizes) | ENERGY STAR product finder — gas
| ENERGY STAR commercial WH dataset (download) | ENERGY STAR dataset xmq6-bm79
| ENERGY STAR commercial WH eligibility (gas storage >75 kBtu/h) | ENERGY STAR key product criteria
| Grainger gas tank water heaters (sizes below ES commercial, e.g. 30–75 kBtu/h) | Grainger — gas tank WH
| Grainger electric tank water heaters (kW ladder, tank gallons) | Grainger — electric tank WH
| ES commercial electric = heat pumps only; not used for resistance tank list | ENERGY STAR — electric (HPWH)
Construction Rate
Notes
*Definitions are from T24 2025 | Parking Garage Building is a building with building floor areas used for parking vehicles, and consists of at least a roof over the parking area enclosed with walls on all sides. The building includes areas for vehicle maneuvering to reach designated parking spaces. If the roof of a parking structure is also used for parking, the section without an overhead roof is considered an outdoor parking lot instead of a parking garage.
Daylight Adaptation Zone in a Parking Garage is the interior path of travel for vehicles adjacent to the entrance or exit of a parking garage as needed for visual adaptation to transition from exterior daylight levels to interior light levels. Daylight Adaptation Zones only include the path of vehicular travel and do not include adjacent Parking Areas.
Parking Zone and Ramps in a Parking Garage is used for the purpose of parking and maneuvering of vehicles. Parking areas include sloping floors of a parking garage. Ramps and driveways specifically for the purpose of moving vehicles between floors of a parking garage. Parking areas and ramps do not include Daylight Adaptation Zones or the roof of a Parking Garage, which may be present in a Parking Garage.

## Prototype
NORESCO, Updated September 2026
ParkingOpen
Characteristic | Value | Data Sources
Building Type | Open Parking
Building Category | Nonresidential
Version | v2-0
Vintages | 4 Vintages: Pre-1978 , 1978-1997 ,1998-2007 , 2008-2018 New Construction (2019+) | Based on the vintage bin analysis. A summary of the findings is presented in the following paper, with a link provided in the Notes tab: Yousefi, F., Athalye, R. (2025). “Determining Vintage Bins for Prototype Development: An Analysis of California Commercial Buildings.” ASHRAE Annual Conference.
Shape |  | The analysis uses prototype geometry originally developed by CEC. This is an open parking garage, there are no actual windows—the space is fully open to ambient air and therefore unconditioned.
Total Floor Area (ft²) | 185627.8 | Same as CEC
Aspect Ratio | 1 | Same as CEC
Number of Floors | 3 | Same as CEC
Roof type | Flat | Same as CEC
WWR | n/a (50% openings all around the building) | Same as CEC
Shading Geometry | No Shades | Same as CEC
Floor to floor height (feet) | 13 | Same as CEC
Floor to ceiling height (feet) | 13 | Same as CEC
Glazing sill height (feet) | n/a | Same as CEC
Above grade wall area (ft²) | 27302.66
Gross wall area (ft²) | 27302.66
Roof area (ft²) | 63116
Underground Gross Wall Area (ft²) | 0

## Zones
Proposed Layout - ParkingOpen
Building | Space/Thermal Zone | Space Type [Primarily from: T24, 2022 Appendix 5.4A] - See Notes column | HVAC System Name/AHU Name | Schedule Category | Conditioned (Y/N) | Area Fraction | Area (ft²) | Volume (ft³) | Multipliers | Number of People | People (Persons/1,000 ft²) [T24, 2025,Table 120.1-A] | Notes
ParkingOpen | Core | Parking Garage Area (Parking Zone and Ramps) | n/a | Parking | Yes | 3.26% | 6050.55 | 13110.37 | 3 | 30.2527 | 5
ParkingOpen | Daylight adaption | Parking Garage Area (Daylight Adaptation Zones) | n/a | Parking | Yes | 0.9805% | 1820.14 | 23663.58 | 1 | 9.1007 | 5
ParkingOpen | East perimeter | Parking Garage Area (Parking Zone and Ramps) | n/a | Parking | Yes | 7.435% | 13801.33 | 29904.25 | 3 | 69.0066 | 5
ParkingOpen | North perimeter | Parking Garage Area (Parking Zone and Ramps) | n/a | Parking | Yes | 7.435% | 13801.33 | 29904.25 | 3 | 69.0066 | 5
ParkingOpen | Parking attendant | Retail Sales Area (Retail Merchandise Sales) | AHU-1 | TicketAttendant | Yes | 0.02158% | 40.05 | 320 | 1 | 0.68085 | 17
ParkingOpen | South perimeter | Parking Garage Area (Parking Zone and Ramps) | n/a | Parking | Yes | 7.435% | 13801.33 | 29904.25 | 3 | 69.0066 | 5
ParkingOpen | West perimeter | Parking Garage Area (Parking Zone and Ramps) | n/a | Parking | Yes | 7.435% | 13801.33 | 29904.25 | 3 | 69.0066 | 5
Total (1 Building) | Total ( 8 spaces) | Total (3 Space types) | Total ( 1Thermal Zones) |  | Total (1 Conditioned zones) |  | 185627.8 |  |  | 316.0609
Background Data [To be deleted prior to publication]
N

## Envelope
Envelope - ParkingOpen
Element | Prototype | Assembly Type | Construction | Thermal properties | Vintage | Selected T24 | Notes | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
External Wall | ParkingOpen | ExtWall_Concrete4in_Insulated | 4 in. Concrete- Insulation (insulation only for ticket attendance ext wall) | U-value IP | Pre 1978 | N/A | ASHRAE 90.1, 2022 Table A3.1-2, 4", R-0, 135 lb/ft3 Density | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87
[5 empty] | 1978-1997 | 1986 | Package A/ Heat Capacity was considered ~10 (BTU/F/ft²) | 0.39968 | 0.39968 | 0.39968 | 0.39968 | 0.39968 | 0.39968 | 0.39968 | 0.39968 | 0.39968 | 0.39968 | 0.39968 | 0.39968 | 0.39968 | 0.39968 | 0.39968 | 0.39968
[5 empty] | 1998-2007 | 2001 | Table 1-H | 0.34 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.34
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.196 | 0.17 | 0.278 | 0.227 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.17 | 0.138 | 0.227 | 0.196 | 0.364 | 0.364 | 0.364 | 0.364 | 0.364 | 0.138 | 0.138 | 0.138 | 0.138 | 0.138 | 0.138 | 0.138
Roof | ParkingOpen | FlatRoof_Concrete8in_Insulated | Built-up Roof 8 in concrete deck + isulation ((insulation only for ticket attendant ceiling) | U-value IP | Pre 1978 | N/A | Considering 30 years for roof/ insulation replacement. | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 1978-1997 | 1992 |  | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 1998-2007 | 2001 | Table 1-H | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.049 | 0.039 | 0.039 | 0.039 | 0.049 | 0.075 | 0.067 | 0.067 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038
**The unconditioned portion of the parking garage should only have concrete walls. However, there is also a small conditioned area served by an AHU system which should still use insulation in the assembly.

## HVAC System
HVAC system - ParkingOpen
Vintage | Zones | Heating | Cooling | Air Distribution | Source | Note
Exisiting | Conditioned zones-Parking Attendant Zone | Electric Unit heater | n/a | n/a | Engineering judgement
New Construction | Conditioned zones-Parking Attendant Zone | Electric Unit heater | n/a | n/a | Engineering judgement
Efficiency of HVAC System (Efficiency is capacity-dependent. The following table provides a general estimate of system efficiency based on preliminary simulations in one climate zone, or assuming cooling load based on rule of thumb)
Vintage | Upgrade/Installed year | Electric Unit heater | Heating DX | Cooling DX | Sources | Note
Pre 1978 | 2008 | Thermal Efficiency of 1 | n/a | n/a
1978-1997
1998-2007
2008-2018 | 2013 | Thermal Efficiency of 1 | n/a | n/a
New Construction | 2025 | Thermal Efficiency of 1 | n/a | n/a
|  | * Et = Combustion efficiency | * Et = Thermal efficiency
Fan power
Vintage | Approach | System | Total Static Pressure (TSP) (in w.c.) | Fan Efficiency [ACM 2025] | Motor Efficiency | Fan Power Index (W/cfm) | Data Source | Note
Existing | PNNL 90.1-2011, TSP | Electric unit heater, attendant zone | 0.2 | 0.65 | ASHRAE 90.1, 2004, Table 10.8 * |  | Fan power formula: PNNL 20405, 2010, section 5.2.2.5 TSP and fan efficiency: PNNL 20405, 2010, Table 5.11, 90.1-04ac values Motor efficiency: ASHRAE 90.1, 2004, Table 10.8
Brake horsepower (bhp) = (Supply cfm × TSP in w.c.) / (6356 × fan efficiency)
Fan power (w/cfm) = (bhp × 746) / ( supply cfm × motor efficiency )
New Construction | ACM 2025 | HEATVENT (System 9), attendant zone, ≤5,000 cfm | TSP = fan power × motor efficiency × fan efficiency × 6356 / 746 | 0.65 | 2025 ACM Table 12 ** | 0.616 | Fan power index: [ACM 2025, Table 13] Motor efficiency: [ACM 2025, Table 12]
* According to PNNL 20405 section 5.2.2.5, the full-load efficiency of the motor serving the fan is taken from ASHRAE 90.1, 2004, Table 10.8, based on motor nameplate and assuming enclosed motors operating at 1,800 rotations per minute (rpm) Motor nameplate size (bhp) = brake horsepower (bhp) × 1.1 ( using a 10% oversizing factor)
** The full‑load efficiency of the motor serving the fan is taken from ACM 2025 Table 12 based on the cfm of the fan. Brake horsepower (bhp) = (Supply cfm from sizing run × fan power in W/cfm) / 746. Note: HVAC tab is an electric unit heater, not PTAC/PTHP/FCU. Existing static pressure 0.2 in. w.c. is the PNNL unit-heater value used on Warehouse. New Construction 0.616 W/cfm is ACM Table 13 System 9 HEATVENT ≤5,000 cfm (replaces 0.53, which is not a Table 13 index). >5,000–10,000 cfm would be 0.620.
Background Data [To be deleted prior to publication]

## Ventilation
Outdoor Airflow Rate - ParkingOpen
Space Type | Space/Thermal Zone | Number of People | Floor Area (ft²) | cfm/person [T24, 2025, Equation 120.1-F and Table 120.1-A] | cfm/ft² [T24, 2025, Equation 120.1-F and Table 120.1-A] | Required exhaust rate-CFM/ft²- [T24, 2025, Table 120.1-B – minimum exhaust rates] | Total cfm driven by people | Total cfm driven by area | Total cfm driven by exhaust | Total cfm | Notes
Parking Garage Area (Parking Zone and Ramps) | Core | 30.2527 | 6050.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Parking Garage Area (Daylight Adaptation Zones) | Daylight adaption | 9.1007 | 1820.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Parking Garage Area (Parking Zone and Ramps) | East perimeter | 69.0066 | 13801.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Parking Garage Area (Parking Zone and Ramps) | North perimeter | 69.0066 | 13801.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Retail Sales Area (Retail Merchandise Sales) | Parking attendant | 0.68085 | 40.05 | 15 | 0.2 | 0 | 10.2127 | 8.01 | 0 | 10.2127 | Exhaust shall not be required where two or more sides comprise walls that are at least 50% open to the outside.
Parking Garage Area (Parking Zone and Ramps) | South perimeter | 69.0066 | 13801.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Parking Garage Area (Parking Zone and Ramps) | West perimeter | 69.0066 | 13801.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Thermostat
Thermostat Setpoints - ParkingOpen
Setpoint | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16 | Source | Note
Parking Attendant Heating Setpoint (F) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | T24 2022 - Appendix 5.4B | The parking attendant area is fully conditioned in the CEC model, this is the setpoint requirement for that area.
Parking AttendantSetback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Parking Attendant Setpoint (F) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
Parking Attendant Setback (F) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
Office Cooling Setback (F) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85

## Water Heater
Water Heater - ParkingOpen
Vintage | WH Type | Efficiency | Number of WH | Tank Volume (gal) | Tank Loss | Source
Existing | Electric | 1 | 1 | See table below for CZ-specific values: Climate Zone Water Heater Sizing and Loss Coefficients, Storage Volume column (col F) | See table below: Climate Zone Water Heater Sizing and Loss Coefficients, Standby Loss column (col G) | See table below for sources: Climate Zone Water Heater Sizing and Loss Coefficients
New Construction | Electric | 1 | 1 | See table below for CZ-specific values: Climate Zone Water Heater Sizing and Loss Coefficients, Storage Volume column (col F) | See table below: Climate Zone Water Heater Sizing and Loss Coefficients, Standby Loss column (col G) | See table below for sources: Climate Zone Water Heater Sizing and Loss Coefficients
Peak Hot Water Consumption
Space Name | Baseline WH Type [CEUS 2022] | Total Area (ft²) | Number of People | Hot Water Usage Specification (gal/hr per person) [T24, 2022, Appendix 5.4A , sheet: "2022 SpaceFuncData-Input"] | Peak Hot Water Usage (gal/hr) | Peak Hot Water Usage (gal/min) | Note
Core | Electric | 6050.55 | 30.2527 | 0 | 0 | 0 | For space types marked with an asterisk (the ‘*’ symbol), the water‑heater type is listed as electric in Appendix 5.4A, sheet ‘2022 SpaceFuncData‑Input.’ However, we modified the value based on CEUS data, which indicates that gas is the primary fuel type.
Daylight adaption | Electric | 1820.14 | 9.1007 | 0 | 0 | 0
East perimeter | Electric | 13801.33 | 69.0066 | 0 | 0 | 0
North perimeter | Electric | 13801.33 | 69.0066 | 0 | 0 | 0
Parking attendant | Electric | 40.05 | 0.68085 | 0.18 | 0.12255 | 0.0020425
South perimeter | Electric | 13801.33 | 69.0066 | 0 | 0 | 0
West perimeter | Electric | 13801.33 | 69.0066 | 0 | 0 | 0
Total | Gas storage |  |  |  | 0 |  | Minimum peak hot water usage is 75 gal according to ACM 2025
Total | Electric resistance |  |  |  | 75
Design supply temperature (°F) | 135 | Title 24 2022 Reference Appendices, Appendix 5.4B
WH system factor | 0.6 | 2025 ACM §5.9.2 Rated Capacity
Water mass conversion (lb/gal) | 8.2877 | 2025 ACM §5.9.2 Rated Capacity
Reheat multiplier | 0.4 | 2025 ACM §5.9.2 Storage Volume
Climate Zone Water Heater Sizing and Loss Coefficients
Climate Zone | Minimum Monthly Mains Temp (°F) [T24 2022 - Appendix 5.4B] | Heat Output (Btu/hr) [ACM, 2025, 5.9.2: Rated capacity section] | WH Capacity (Btu/hr) [ACM, 2025, 5.9.2: Rated capacity section] | Required Energy Input (Btu/hr) | Storage Volume (gal) | Standby Loss [Title 20, §1605.1 Table F-4; Appendix B: Water Heating Calculation Method] |  | Off/On Cycle Loss Coefficient to Ambient Temp |  | Source/Note
CZ01 | 47.9 | 54139.4002 | 32483.6401 | 34121 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F | Required Energy Input: vendor/available catalog size (Market data table). Storage Volume: standard/available catalog tank size (Market data table).
CZ02 | 50.8 | 52336.8255 | 31402.0953 | 34121 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F
CZ03 | 52.2 | 51466.617 | 30879.9702 | 34121 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F
CZ04 | 52.7 | 51155.8282 | 30693.4969 | 30709 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F
CZ05 | 51.6 | 51839.5635 | 31103.7381 | 34121 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F
CZ06 | 56.8 | 48607.3605 | 29164.4163 | 30709 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F
CZ07 | 58.4 | 47612.8365 | 28567.7019 | 30709 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F
CZ08 | 58.4 | 47612.8365 | 28567.7019 | 30709 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F
CZ09 | 57.6 | 48110.0985 | 28866.0591 | 30709 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F
CZ10 | 57.1 | 48420.8872 | 29052.5323 | 30709 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F
CZ11 | 50.5 | 52523.2987 | 31513.9792 | 34121 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F
CZ12 | 51.4 | 51963.879 | 31178.3274 | 34121 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F
CZ13 | 51.7 | 51777.4057 | 31066.4434 | 34121 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F
CZ14 | 50.1 | 52771.9297 | 31663.1578 | 34121 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F
CZ15 | 63.2 | 44629.2645 | 26777.5587 | 27297 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F
CZ16 | 41.4 | 58179.654 | 34907.7924 | 40946 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F
Market data
Catalog gas input (Btu/h) | Input source | Elec resistance tank (kW) | Elec resistance (Btu/h) | Catalog gas tank (gal) | Tank source | Elec tank (gal) | Elec tank source | Sources and links → Note tab
60000 | Grainger | 1.5 | 5118 | 34 | ENERGY STAR | 6 | Grainger
75100 | Grainger | 2 | 6824 | 35 | Grainger | 10 | Grainger
76000 | Both | 3 | 10236 | 48 | Grainger | 15 | Grainger
80000 | Grainger | 4.5 | 15355 | 50 | Both | 20 | Grainger
99900 | ENERGY STAR | 6 | 20473 | 55 | ENERGY STAR | 28 | Grainger
100000 | Both | 8 | 27297 | 60 | ENERGY STAR | 30 | Grainger
120000 | ENERGY STAR | 9 | 30709 | 65 | Both | 36 | Grainger
125000 | Both | 10 | 34121 | 72 | Grainger | 40 | Grainger
130000 | Both | 12 | 40946 | 75 | Both | 47 | Grainger
145000 | ENERGY STAR | 12.1 | 41287 | 76 | Grainger | 50 | Grainger
150000 | ENERGY STAR | 18 | 61419 | 80 | Both | 65 | Grainger
156000 | Grainger | 24 | 81891 | 82 | Grainger | 80 | Grainger
160000 | Both | 27 | 92128 | 85 | Grainger | 85 | Grainger
175000 | ENERGY STAR | 36 | 122837 | 90 | Both | 105 | Grainger
180000 | Grainger | 54 | 184256 | 91 | Grainger | 120 | Grainger
199000 | ENERGY STAR |  |  | 100 | Both
199900 | Both |  |  | 110 | ENERGY STAR
200000 | ENERGY STAR |  |  | 119 | Both
250000 | Both |  |  | 125 | ENERGY STAR
251000 | ENERGY STAR
270000 | Grainger
285000 | ENERGY STAR
300000 | Both
320000 | ENERGY STAR
360000 | Grainger
398000 | ENERGY STAR
399000 | ENERGY STAR
399900 | Both
499900 | Grainger
550000 | Grainger
715000 | Grainger

## Interior Lights
Interior Lighting - ParkingOpen
Space Type | New Construction |  |  | Existing
| Lighting density (W/ft²) | Additional lighting power for porTable lighting (W/ft²) | Source | LPD (W/ft²) | Additional LPD for PorTable Lighting (W/ft²) | Source
Parking Garage Area (Parking Zone and Ramps) | 0.1 |  | T24, 2025, Table 140.6 C (Area category method) | 0.14 |  | T24, 2016, Table 140.6 C (Area category method)
Parking Garage Area (Daylight Adaptation Zones) | 1 |  |  | 0.75
Retail Sales Area (Retail Merchandise Sales) | 0.95 |  |  | 1.2 |  |  | *Parking attendant zone

## Ext Lighting
Exterior Lighting - ParkingOpen
Motion Controlled Luminaires (W) | Non-motion Controlled Luminaires (W) | Total (W) | Source
200 | 782.541 | 982.541 | T24, 2022 & 2025 2019 Outdoor Lighting CASE report PNNL 90.1-2010 TSD
Exterior Lighting
Items (Assume LZ2) | Assumptions [2019 Outdoor Lighting CASE Report & PNNL 90.1-2010 TSD] |  | Unit | Lighting Power Allowance [T24, 2025, Table 140.7-A & 140.7-B] | Unit | Exterior Lighting Power (W)
IWA (Initial Wattage Allowance) |  |  |  | 200 | (W) | 200
Parking area | 400 ft² for every parking space 1 parking space per 830 ft² of gross building area | 0 | (ft²) | 0.019 | (W/ft²)
Building Entrance | 14 building entrance per PNNL Model |  | (count) | 15 | (W/ea) | 0
Hardscape Ornamental Light | 0.1 ft² per 1 ft² of gross building area for hardscape ornamental light | 18563 | (ft²) | 0.007 | (W/ft²) | 129.941
Building façade | 0.1 W per 1 ft² of facade area Façade Area = Perimeter × 0.5 × 13 ft * The 0.5 factor assumes that only half of the perimeter walls are lit. -Formula ia developed based on the 2019 Outdoor Lighting CASE report | 6526 | (ft²) | 0.1 | (W/ft²) | 652.6
Security lighting for retail parking | 1 sf per 100 sf of gross building area |  | (ft²) | 0.005 | (W/ft²) | 0
Non-sales canopy |  |  | (ft²) | 0.137 | (W/ft²) | 0
Motion Controlled Luminaires (W) | [5 empty] | 200
Non-motion-controlled Luminaires | [5 empty] | 782.541
Total | [5 empty] | 982.541
Total floor area | 185627.8
Perimeter | 1004
Floors | 3
Background Data [To be deleted prior to publication]

## Equipment
Equipment - ParkingOpen
Spaces | Plug load Power Density (W/ft²) | Gas Power Density (Btu/hr-ft²) | Refrigeration Power Density (W/ft²) | Source | Note
Parking Garage Area (Parking Zone and Ramps) | 0 | 0 | 0 | T24 2022 - Appendix 5.4A
Parking Garage Area (Daylight Adaptation Zones) | 0 | 0 | 0
Retail Sales Area (Retail Merchandise Sales) | 0.4 | 0 | 0 |  | Parking attendant zone - Plug load and schedules project with CEC, 2025
Elevator
Vintage | Class | Number of elevators (ne) | Cab Lighting Power Limit (W/ft2) | Fan Power Limit (W/CFM) | Cab Ventilation Fan & Lighting Shutoff | Design Motor Load (W) | Fan Load (W) | Lighting Load (W) | Total (W) | Note
Existing | F/G | 2 | 1.14 | 0.33 | When stopped and unoccupied with doors closed for over 15 minutes, cab interior lighting and ventilation shall be de-energized until required for operation. | 21383.9 | 165 | 68.17 | 21617.07 | Design load is calculated according to ISO 25745-2 method using Class F/G. Cab lighting and fan requirements are based on ASHRAE 90.1 2013.
New Construction | E | 2 | 0.6 | 0.33 | When the elevator cab is stopped and unoccupied with doors closed for over 15 minutes, the cab interior lighting and ventilation fans shall be switched off until elevator cab operation resumes. | 11276.14 | 165 | 35.88 | 11477.02 | Design load is calculated according to ISO 25745-2 method using Class E. Cab lighting and fan requirements are based on T24 2025 §120.6 (f).
Parking Elevator Calculations
Symbol | Definition | Value | Units | Source
E | Annual energy consumption of the elevator - Existing | 32654.71 | kWh/year | Calculated
| Annual energy consumption of the elevator - New Construction | 17219.45 | kWh/year | Calculated
C1 | Running-energy coefficient | 3.65 for Class E; 5.47 for Class F | Coefficient | ISO 25745-2 Table 7
C2 | Idle/standby coefficient | 800 for Class E; 1,600 for Class F | Coefficient | ISO 25745-2 Table 7
Q | Rated load of elevator | 1361 | kg | Assumed for all prototypes
Elevator Size | Cab floor area | 29.9 | ft^2 | W=6.781 ft, L=4.406 ft; assumed based on representative manufacturer
CFM | Cab fan airflow | 250 | cfm | Assumed for multifamily and commercial prototypes
cat | Usage category | 2 | - | ISO 25745-2 Table A.1
d | Operating days per year | 360 | days/year | ISO 25745-2 Table A.1
nf | Number of floors | 3 | floors | Prototype assumptions
h | Floor-to-floor height | 3.96 | m | Prototype assumptions
v | Elevator lift speed | 1 | m/s | ISO 25745-2 Table A.1
nd | Number of trips per day | 125 | trips/day | ISO 25745-2 Table A.1
S_pct | Percent of average travel distance | 0.67 | % | ISO 25745-2 Table 2
a | Acceleration | 1 | m/s^2 | Annex B of ISO 25745-2
j | Jerk | 1.25 | m/s^3 | Annex B of ISO 25745-2
td | Door time | 8 | seconds | Annex B of ISO 25745-2
S_av | Average distance traveled per trip | 7.96 | m/trip | Calculated (nf * h * S_pct)
t_av | Average trip time | 17.76 | seconds/trip | Calculated (S_av/v + v/a + a/j + td)
t_nr | Time not running per day | 23.38 | hours/day | Calculated (24 - nd * t_av)
Standby Hours | Annual standby hours | 8538.01 | hours/year | Calculated (24*(365-d)+t_nr*d)
Total light level | Total light level | 40 | lm/ft2 | PNNL
EFLH | Equivalent full load hours | 1527.07 | hours | Calculated using the elevator schedule
Background Data [To be deleted prior to publication]

## Schedules
Schedules - ParkingOpen
Zone | Schedule Category | Schedule | Source | Type | Hour
[5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Parking Zones | Parking | Occupancy | T24 2022 - Appendix 5.4B, [Parking] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Parking Zones | Parking | Lights | T24 2022 - Appendix 5.4B, [Parking] | Weekday | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5
|  |  |  | Saturday | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  |  | Sunday | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Parking Zones | Parking | ElecEquipment | T24 2022 - Appendix 5.4B, [Parking] | Weekday | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5
|  |  |  | Saturday | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  |  | Sunday | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Parking Zones | Parking | GasEquipment | T24 2022 - Appendix 5.4B, [Parking] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Parking Attendant
Ticket Attendant Zone | TicketAttendant | Occupancy | T24 2022 - Appendix 5.4B, [Parking] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ticket Attendant Zone | TicketAttendant | Lights | T24 2022 - Appendix 5.4B, [Parking] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ticket Attendant Zone | TicketAttendant | ElecEquipment | T24 2022 - Appendix 5.4B, [Parking] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ticket Attendant Zone | TicketAttendant | ServiceHotWater | T24 2022 - Appendix 5.4B, [Parking] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ticket Attendant Zone | TicketAttendant | HVACAvail | T24 2022 - Appendix 5.4B, [Parking] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ticket Attendant Zone | TicketAttendant | Infiltration | T24 2022 - Appendix 5.4B, [Parking] | Weekday | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Saturday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Sunday | bar: Hour 1 to Hour 24
Ticket Attendant Zone | TicketAttendant | HtgSetpt | T24 2022 - Appendix 5.4B, [Parking] | Weekday | 60 | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  |  | Saturday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  |  | Sunday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Ticket Attendant Zone | TicketAttendant | ClgSetpt | T24 2022 - Appendix 5.4B, [Parking] | Weekday | 85 | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 85 | 85 | 85 | 85 | 85 | 85 | 85
|  |  |  | Saturday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
|  |  |  | Sunday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
Other | [28 empty] | EFLH
| Building | Elevator | T24 2022 - Appendix 5.4B, [Parking] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.69 | 0.43 | 0.37 | 0.43 | 0.58 | 0.48 | 0.37 | 0.37 | 0.46 | 0.62 | 0.2 | 0.12 | 0.04 | 0.04 | 0 | 0 | 1527.07
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.14 | 0.21 | 0.18 | 0.25 | 0.21 | 0.13 | 0.08 | 0.04 | 0.05 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Building | ExtLightingNonMotionCtrl | Siimlar | Weekday | bar: Hour 1 to Hour 24
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
| Building | ExtLightingMotionCtrl | PNNL Hospital Prototype (2022) Modified to 0 for 11 pm to 5 am during weekday and 12 am to 5 am during weekend | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Parking Zones | Building | ParkingPeopleActivityLevel | same as stairs | Weekday | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5
|  |  |  | Saturday | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5
|  |  |  | Sunday | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5
Ticket Attendant Zone | Building | TicketAttendantPeopleActivityLevel | assumed same as meeting room | Weekday | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2
|  |  |  | Saturday | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2
|  |  |  | Sunday | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2

## Energy Usage (hidden)
CalBEM Energy Consumption - ParkingOpen | [11 empty] | Energy Consumption - ParkingOpen
Prototype | CZ | CalBEM Electricity EUI (KBTU/ft²) | CalBEM Gas EUI (KBTU/ft²) | CalBEM Total EUI (KBTU/ft²) | New Construction Electricity EUI (KBTU/ft²) | New Construction Gas EUI (KBTU/ft²) | New Construction Total EUI (KBTU/ft²) | National Average | Acceptable Range (25% Higher) | Acceptable Range (25% Lower) | National Average Acceptable EUI Range | Prototype | CZ | Total Floorspace (Thousand of ft²) | CEUS 2023 Electricity EUI (kBtu/ft²) | CEUS 2023 Gas EUI (kBtu/ft²) | CEUS 2023 Total EUI (kBtu/ft²) | Acceptable Range (20% Higher) | Acceptable Range (20% Lower) | CEUS 2022 Acceptable EUI Range
ParkingOpen | 1 | [6 empty] | 4.2 | 5.25 | 3.15 | 2.1 | ParkingOpen | 1
| 2 | [6 empty] | 4.2 | 5.25 | 3.15 | 2.1 |  | 2
| 3 | [6 empty] | 4.2 | 5.25 | 3.15 | 2.1 |  | 3
| 4 | [6 empty] | 4.2 | 5.25 | 3.15 | 2.1 |  | 4
| 5 | [6 empty] | 4.2 | 5.25 | 3.15 | 2.1 |  | 5
| 6 | [6 empty] | 4.2 | 5.25 | 3.15 | 2.1 |  | 6
| 7 | [6 empty] | 4.2 | 5.25 | 3.15 | 2.1 |  | 7
| 8 | [6 empty] | 4.2 | 5.25 | 3.15 | 2.1 |  | 8
| 9 | [6 empty] | 4.2 | 5.25 | 3.15 | 2.1 |  | 9
| 10 | [6 empty] | 4.2 | 5.25 | 3.15 | 2.1 |  | 10
| 11 | [6 empty] | 4.2 | 5.25 | 3.15 | 2.1 |  | 11
| 12 | [6 empty] | 4.2 | 5.25 | 3.15 | 2.1 |  | 12
| 13 | [6 empty] | 4.2 | 5.25 | 3.15 | 2.1 |  | 13
| 14 | [6 empty] | 4.2 | 5.25 | 3.15 | 2.1 |  | 14
| 15 | [6 empty] | 4.2 | 5.25 | 3.15 | 2.1 |  | 15
| 16 | [6 empty] | 4.2 | 5.25 | 3.15 | 2.1 |  | 16
chrome-extension://efaidnbmnnnibpcajpcglclefindmkaj/https://www.energystar.gov/sites/default/files/tools/Parking%20Adjustment%20Technical%20Reference_508.pdf | [11 empty] | Ref: CEUS 2022 Report
And converted FZ level data to CZ level

## Weights (hidden)
% of Floor Area per CZ and Vintage Bin - ParkingOpen | [7 empty] | % of Floor Area per CZ and Vintage Bin - ParkingOpen
Prototype | CZ | Vintage Bin | [5 empty] | Prototype | Vintage Bin | CZ
|  | Pre-1978 | 1978-1997 | 1998-2007 | 2008-2018 | Not available |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
Open Parking | 1 | [5 empty] | 0% | Open Parking | Pre-1978 | [16 empty] | 0%
| 2 | [5 empty] | 0% |  | 1978-1997 | [16 empty] | 0%
| 3 | [5 empty] | 0% |  | 1998-2007 | [16 empty] | 0%
| 4 | [5 empty] | 0% |  | 2008-2018 | [16 empty] | 0%
| 5 | [5 empty] | 0% |  | Not available | [16 empty] | 0%
| 6 | [5 empty] | 0% |  | Total
| 7 | [5 empty] | 0%
| 8 | [5 empty] | 0%
| 9 | [5 empty] | 0%
| 10 | [5 empty] | 0%
| 11 | [5 empty] | 0%
| 12 | [5 empty] | 0%
| 13 | [5 empty] | 0%
| 14 | [5 empty] | 0%
| 15 | [5 empty] | 0%
| 16 | [5 empty] | 0%
Statewide
Ref: CEUS 2022 dataset

## PV (hidden)
PV - ParkingOpen
TBD

## EV Charger (hidden)
EV Charger - ParkingOpen
TBD
Background Data [To be deleted prior to publication]

## Data (hidden)
Space Function | Electric Equipment Load Intensity | Electric Equipment Load Intensity | LPD
Aging Eye/Low-vision (Corridor Area) |  |  | 2013 | 2016 | 2019 | 2025
Aging Eye/Low-vision (Dining)
Aging Eye/Low-vision (Lobby, Main Entry)
Aging Eye/Low-vision (Lounge/Waiting Area)
Aging Eye/Low-vision (Multipurpose Room)
Aging Eye/Low-vision (Religious Worship Area)
Aging Eye/Low-vision (Restroom)
Aging Eye/Low-vision (Stairwell)
Audience Seating Area
Auditorium Area
Auto Repair / Maintenance Area
Barber, Beauty Salon, Spa Area
Civic Meeting Place Area
Classroom, Lecture, Training, Vocational Areas
Concourse and Atria Area
Convention, Conference, Multipurpose and Meeting Area
Copy Room
Corridor Area
Dining Area (Bar/Lounge and Fine Dining)
Dining Area (Cafeteria/Fast Food)
Dining Area (Family and Leisure)
Electrical, Mechanical, Telephone Rooms
Exercise/Fitness Center and Gymnasium Areas
Financial Transaction Area
Healthcare Facility and Hospitals (Exam/Treatment Room)
Healthcare Facility and Hospitals (Imaging Room)
Healthcare Facility and Hospitals (Medical Supply Room)
Healthcare Facility and Hospitals (Nursery)
Healthcare Facility and Hospitals (Nurse's Station)
Healthcare Facility and Hospitals (Operating Room)
Healthcare Facility and Hospitals (Patient Room)
Healthcare Facility and Hospitals (Physical Therapy Room)
Healthcare Facility and Hospitals (Recovery Room)
Hotel Function Area
Kitchen/Food Preparation Area
Kitchenette or Residential Kitchen
Laboratory, Scientific
Laundry Area
Library (Reading Area)
Library (Stacks Area)
Lobby, Main Entry
Locker Room
Lounge, Breakroom, or Waiting Area
Manufacturing, Commercial & Industrial Work Area (Low Bay)
Manufacturing, Commercial & Industrial Work Area (High Bay)
Manufacturing, Commercial & Industrial Work Area (Precision)
Museum Area (Exhibition/Display)
Museum Area (Restoration Room)
Office Area (>250 square feet)
Office Area (<250 square feet)
Parking Garage Area (Parking Zone and Ramps)
Parking Garage Area (Daylight Adaptation Zones)
Pharmacy Area
Retail Sales Area (Grocery Sales)
Retail Sales Area (Retail Merchandise Sales)
Retail Sales Area (Fitting Room)
Religious Worship Area
Restrooms
Stairwell
Storage, Commercial/Industrial (Warehouse)
Storage, Commercial/Industrial (Refrigerated)
Storage, Commercial/Industrial (Shipping & Handling)
Storage (General)
Sports Arena - Playing Area (> 5,000 Spectators)
Sports Arena - Playing Area (2,000 - 5,000 Spectators)
Sports Arena - Playing Area (< 2,000 Spectators)
Sports Arena - Playing Area (Recreational)
Theater Area (Motion Picture)
Theater Area (Performance)
Transportation Function (Baggage Area)
Transportation Function (Ticketing Area)
Videoconferencing Studio
High-Rise Residential Living Spaces
Hotel/Motel Guest Room
All other
Attic
Reception Area
Elevator
Plenum
IT Room (EPD 12)
Computer Room (EPD 20)
Server Room (EPD 45)