## Notes
Data Sources
Dataset | Dodge 2023
CEUS 2022
CBECS 2018
ComStock 2023
Prototype | CEC prototype (CBECC 2022.3.1) | https://bees.noresco.com/software2022.html
| PNNL prototype (90.1-2022) | https://www.energycodes.gov/prototype-building-models#Commercial
| DEER prototype (June 2023) | https://github.com/sound-data/DEER-Prototypes-EnergyPlus
Codes | Title 24, part 6, referred to as T24 (1986, 1992, 2001, 2007, 2013, 2016, 2019, 2022, 2025)
ASHRAE 90.1 (2022)
| CFR Title 10 (2009) | https://www.govinfo.gov/content/pkg/FR-2009-03-23/pdf/FR-2009-03-23.pdf
| CFR Title 10 ( 2013) | https://www.govinfo.gov/content/pkg/CFR-2013-title10-vol3/pdf/CFR-2013-title10-vol3-part431.pdf
| CFR Title 10 ( 2024) | https://www.govinfo.gov/content/pkg/CFR-2024-title10-vol3/pdf/CFR-2024-title10-vol3-part431-subpartF.pdf
Others | ACM (2013, 2019, 2022, 2025)
| Title 24, 2022 - Appendix 5.4A and Appendix 5.4B | https://www.energy.ca.gov/publications/2022/2022-nonresidential-and-multifamily-alternative-calculation-method-reference
| 2022 Reduced infiltration CASE report | https://title24stakeholders.com/wp-content/uploads/2020/10/2022-T24-Final-CASE-Report_Reduce-Infiltration.pdf
| 2019 Outdoor Lighting CASE Report | https://title24stakeholders.com/wp-content/uploads/2016/10/T24-2019-CASE-Study-Results-Report-Outdoor-Sources_Final_with-Attachments.pdf
| PNNL 20405, 2011 | https://www.pnnl.gov/main/publications/external/technical_reports/PNNL-20405.pdf
| Air leakage Memo, NORESCO, 2025 | https://2050partners.sharepoint.com/:w:/r/sites/CalBEMCollaborativeEfforts/_layouts/15/Doc.aspx?sourcedoc=%7B3BEF8F74-7FAC-44F2-A70C-D76617660066%7D&file=Infiltration_rate_report_14May2025-Short-Version.docx&action=default&mobileredirect=true
| Yousefi, F., Athalye, R., (2025), "Determining Vintage Bins for Prototype Development: An Analysis of California Commercial Buildings," ASHRAE Annual Conference | https://www.thefreelibrary.com/Determining+Vintage+Bins+for+Prototype+Development%3a+An+Analysis+of...-a0879271125
| Design Guide: Advanced Water Heating for Foodservice (20232) (by GTI and Frontier funded by SoCalGas and Pacific Gas and Electric Company | https://caenergywise.com/design-guides/hot-water/Technical_Design_Guide.pdf
| Design Guide 1 : Improving Commercial Kitchen Ventilation System Performance : Selecting & Sizing Exhaust Hoods referred as CKV (2004) (by SCE) | https://www.streivor.com/wp-content/uploads/2020/11/CKV-Design-Guide-1-Selecting-and-Sizing-Exhaust-Hoods.pdf
| Proposed Updates to Equipment Power Densities and Building Schedules for the 2028 Energy Code, referred to as "Plug load and schedules project with CEC, 2025" (Docket Number =25-BSTD-03 & TN=265693) | https://efiling.energy.ca.gov/GetDocument.aspx?tn=265693&DocumentContentId=102545
| ENERGY STAR certified commercial water heaters | https://www.energystar.gov/productfinder/product/certified-commercial-water-heaters/results?fuel_filter=Gas&markets_filter=United+States
| Grainger gas tank water heaters (sizes below commercial, e.g. 30–75 kBtu/h) | https://www.grainger.com/category/plumbing/water-heaters/gas-tank-water-heaters
| Grainger electric tank water heaters | https://www.grainger.com/category/plumbing/water-heaters/electric-tank-water-heaters
Notes
RestaurantFastFood | Is a subcategory of food service building used for prepared-food sales. These places are often quick-service operations (e.g., drive-throughs, counter-service eateries,...).
EIS, 2018: | U.S. Energy Information Administration - EIA - Independent Statistics and Analysis
RestaurantFastFood (STC:3)
Year | Total floor area (k ft2) | Count
1967 | 5361.9 | 152
1968 | 8271 | 452
1969 | 13593.6 | 655
1970 | 14323.7 | 601
1971 | 13719.8 | 592
1972 | 16513.9 | 687
1973 | 27619.6 | 920
1974 | 26732 | 804
1975 | 13654.6 | 710
1976 | 19608.4 | 853
1977 | 29745.3 | 1055
1978 | 40044.4 | 1359
1979 | 40268.5 | 1053
1980 | 26862.2 | 851
1981 | 21498.2 | 812
1982 | 14017.9 | 606
1983 | 19364.4 | 880
1984 | 31271.7 | 1271
1985 | 44833.1 | 1461
1986 | 46291.2 | 1382
1987 | 46613.6 | 1265
1988 | 50555.2 | 1237
1989 | 48019.1 | 1233
1990 | 37809.8 | 1111
1991 | 20082.4 | 768
1992 | 11010.9 | 426
1993 | 7511.2 | 470
1994 | 11961.3 | 465
1995 | 13270.9 | 521
1996 | 20653.8 | 570
1997 | 27588.9 | 407
1998 | 41631.3 | 476
1999 | 48039.6 | 533
2000 | 52612.2 | 500
2001 | 40337.2 | 432
2002 | 33147.2 | 399
2003 | 30982.8 | 398
2004 | 29560.8 | 417
2005 | 27484.1 | 347
2006 | 25891.9 | 299
2007 | 25769.2 | 248
2008 | 20632.6 | 236
2009 | 5608 | 122
2010 | 2602.9 | 47
2011 | 3617.9 | 36
2012 | 8233.2 | 63
2013 | 17625.9 | 46
2014 | 13973.9 | 72
2015 | 29759.5 | 104
2016 | 25538.8 | 152
2017 | 27796.9 | 105
2018 | 32684.7 | 117
2019 | 30948.5 | 141
2020 | 34022.9 | 162
2021 | 53815 | 225
2022 | 41442.1 | 218
2023 | 10975.7 | 44
Dodge Construction data , 2023

## Prototype
NORESCO, Updated September 2026
RestaurantFastFood
Characteristic | Value | Data Sources
Building Type | Fast Food Restaurant
Building Category | Nonresidential
Version | v2-0
Vintages | 4 Vintages: Pre-1978 , 1978-1997 ,1998-2007 , 2008-2018 New Construction (2019+) | Based on the vintage bin analysis. A summary of the findings is presented in the following paper: Yousefi, F., Athalye, R. (2025). “Determining Vintage Bins for Prototype Development: An Analysis of California Commercial Buildings.” ASHRAE Annual Conference. | https://www.thefreelibrary.com/Determining+Vintage+Bins+for+Prototype+Development%3a+An+Analysis+of...-a0879271125 | NonRes-Vintage bins-Draft Report-30Nov2023-Final.docx
Shape |  | Assumption; same as CEC Prototype 2022
Total Floor Area (ft²) | 2501 (50 ft * 50 ft) | Assumption; same as CEC Prototype 2022
Aspect Ratio | 1 | Assumption; same as CEC Prototype 2022
Number of Floors | 1 | Assumption; same as CEC Prototype 2022
Roof type | Attic (17°) | Assumption; same as CEC Prototype 2022
WWR | Average 14% (South: 28% , East: 14% ,North: 0% ,West: 14% | Assumption; same as CEC Prototype 2022
Shading Geometry | No shades | Assumption; same as CEC Prototype 2022
Floor to floor height (ft) | N/A | Assumption; same as CEC Prototype 2022
Floor to ceiling height (ft) | 10 | Assumption; same as CEC Prototype 2022
Glazing sill height (ft) | 3.5 (top of the window is 6.5 ft high with 3 ft high glass) | Assumption; same as CEC Prototype 2022
Existing public prototypes
|  | PNNL (Fast Food) | CEC (Small Restaurant) | CPUC (Fast Food)
Geometry | Whole building
Floor area (ft²) | Total | 2500 | 2500 | 1998
Height (ft) | All | 10 | 10 | 10
Zones |  | Dining 50%, Kitchen 50%, Attic (NOT conditioned) | Dining 50% , Kitchen 50%, Attic (NOT conditioned) | Dining 40% , Kitchen 40% , Waiting Area 15% , Restroom 5% (100 sf)
Internal Load
People (person/ft²) | Dining | 0.07 | 0.033 | 0.033
| Kitchen | 0.005 (6.3 people) | 0.0025 | 0.0025
| Other zones (if any) | - | - | 0.033 Lobby & 0.005 Restroom
Lights (W/ft²) | Dining | 0.38 | 0.45 | 0.45
| Kitchen | 0.89 | 0.95 | 0.95
| Other zones (if any) |  |  | 0.7 Lobby, 0.65 Restroom
Ext lights (W) | Whole building | 952 (209 and 743) | - | -
Gas Equipment (Btu/h-ft2) | Kitchen | 237.4 (296,748 Btu/h) | 32.4 | 17.5
Electric Equipment (W/ft²) | Dining | 10.3 (12,835 W) | 0.75 (0.5 receptacle & 0.25 refrigerator ) | 0.75 (0.5 & 0.25)
| Kitchen | 24.29 (29,769 W receptacle & 313 W ReachIn Refrigerator & 277 W ReachInFreezer) | 2.62 (1.5 receptacle & 1.12 refrigerator) | 2.62 (1.5 & 1.12)
| Other zones (if any) | - | - | 0.5 Lobby
Refrigerator | Kitchen | In addition to the Reachin freezer and refrigerator load defined as electric load, it has : 2 Case refrigerator : 716 and 763 Btu/hr-ft for 8 and 10 ft cases 2.5 COP for design compressor rack 1126 Btu/h for fan power of design compressor | Two refrigerator loads is defined as electric equipment load for dining and kitchen | expected to simulate the Refrigerator loads as electric equipment load ( like CEC)
HVAC System
Heating Sizing Factor | All | H&C: 1.2 | H&C:1 | H: 2.5 , C: 2.3
HVAC | Dining | PSZ AC: CAV no reheat, DX cooling coil: multi speed, Gas heating coil | (BAseAirSys 13): VAV no Reheat +DX cooling coil:two speed, Gas Heating coil | Single Zone VAV no Reheat , DX cooling coil:multi speed, Gas heating coil
| Kitchen | PSZ AC : CAV no reheat, DX cooling coil: multi speed, Gas heating coil | (sys7or3a): CAV no Reheat+DX cooling coil: single speed+ Gas Heating coil | Single Zone VAV no Reheat , DX cooling coil:single speed, Gas heating coil
| Other zones (if any) | - | - | For each Lobby and Restroom: Single Zone VAV no Reheat, DX cooling coil:multi speed , Gas heating coil
Exhaust Fan | Dining | 881 cfm with efficiency of 1
| Kitchen | 3300 cfm with efficiency of 0.385 | 2400 cfm with efficiency of 0.43
Thermostat Setpoint (F) | Dining Heating | 70 (setback: 60) | 70 (setback: 60) | 70 (setback: 60)
| Dining Cooling | 75 (setback: 86) | 75 (setback: 85) | 75 (setback: 85)
| Kitchen Heating | 66 (setback: 60) | 70 (setback: 60) | 70 (setback: 60)
| Kitchen Cooling | 79 (setback: 86) | 75 (setback: 85) | 75 (setback: 85)
Water Heater
Tank Volume (gal |  | 100 | 30 | Autosize (Nominal tank volume for autosizing: 39.6) Output file :69 gal
Peak Flow Rate (gpm) | Dining | - | 0.4 | 0.51
| Kitchen | 1.52 | 0.03 | 0.04
| Other zones (if any) |  |  | 0.03 Lobby
Loop Max and Min Temperature (F) |  | 140, 50 | 212, 32 | 212 , 50
Tank Max Temperature (F) |  | 180 | 180 | 212
Yealy Water Usage (gal) from the output files |  | 204731.75 | 71224 | 95967.6776
ASHRAE DOE
Kitchen loads are included in the EnergyPlus Electric Equipment and Gas Equipment objects
Prototype Comparison
Program | CalBEM (RestaurantFastFood) | CEC (RestaurantSmall) | DEER (Restaurant-FastFood) | PNNL (RestaurantFastFood)
Geometry
Number of Floors | 1 | 1 | 1 | 1
Envelope
Floor Area (ft2) | 2500.24 | 5002.33 | 3996.2094 | 2500.8869
Roof Area (ft2) | 2786.59 | 2786.59 | 1998.1047 | 2786.3459
Gross Exterior Wall Area (ft2) | 2001.08 | 2001.08 | 2324.3588 | 2000.9033
Window Area (ft2) | 280.14 | 280.14 | 580.8206 | 280.0769
Skylight Area (ft2) | 0 | 0 | 0 | 0
Window-to-Wall Ratio (%) | 14 | 14 | 24.99 | 14
Loads
Occupants | 45 | 45.02 | 39.0834 | 93.82
Occupancy Density (people/1000 ft2) | 17.9983 | 8.9998 | 9.7801 | 37.5147
Interior Lighting Power (W) | 1749.9488 | 1750.5927 | 2786.5021 | 1591.4941
Interior LPD (W/ft2) | 0.69991 | 0.34996 | 0.69729 | 0.63637
Equipment Power (W) | 17067.24 | 16083.7997 | 6950.2541 | 130161.4683
Equipment Density (W/ft2) | 6.8262 | 3.2153 | 1.7392 | 52.0461
Ventilation
Design OA Sum (cfm) | 381.7074 | 2806.2322 | 669.2378 | 1202.0406
Design OA Density (cfm/ft2) | 0.15267 | 0.56099 | 0.16747 | 0.48065
Design OA per Person (cfm/person) | 8.4824 | 62.333 | 17.1233 | 12.8122
HVAC and Water Heater
HVAC System Type | System: central air loops Distribution: 2 air loops; constant-volume no-reheat terminal; DX cooling; natural-gas heating Plant: 1 heat exchanger | System: central VAV air loops Distribution: 2 air loops; VAV no-reheat and constant-volume no-reheat terminals; DX cooling; natural-gas heating | System: unitary/package systems + central VAV air loops Distribution: 4 air loops; VAV no-reheat terminal; DX cooling; natural-gas heating | System: unitary/package systems + central air loops Distribution: 2 air loops; constant-volume no-reheat terminal; DX cooling; natural-gas heating
Water Heater | 1 water heater: 1 natural-gas 1 service water loop | 1 water heater: 1 natural-gas 1 service water loop | 1 water heater: 1 natural-gas 1 service water loop | 1 water heater: 1 natural-gas 1 service water loop

## Zones
Proposed Layout - RestaurantFastFood
Building | Space/Thermal Zone | Space Type Primarily from [T24, 2022 Appendix 5.4A] - See Notes column | HVAC zone | Schedule Category | Conditioned (Y/N) | Area Fraction | Area (ft²) | Volume (ft³) | Multipliers | Number of People | People (Persons/1,000 ft²) [T24, 2025,Table 120.1-A] | Notes
RestaurantFastFood | Dining | Dining Area (Cafeteria/Fast Food) | AHU_1 | Restaurant | Y | 50% | 1250.46 | 12504.6 | 1 | 41.2652 | 33
RestaurantFastFood | Kitchen | Kitchen/Food Preparation Area | AHU_2 | Kitchen | Y | 50% | 1250.46 | 12504.6 | 1 | 3.7514 | 3
RestaurantFastFood | Attic | Attic | n/a |  | N |  | 2500 | 25000 | 1 | 0
Total (1 Building) | Total (3 Space) | Total (3 space type) | Total ( 2 HVAC Zones) | Total (2 category) | Total (2 Conditioned zones) | 1 | 2500.92 | 25009.2
Background Data [To be deleted prior to publication]
N
Kitchen
Kitchen
Dining

## Envelope
Envelope - RestaurantFastFood
Element | Prototype | Assembly Type | Construction | Thermal properties | Vintage | Selected T24 | Notes | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
External Wall | RestaurantFastFood | ExtWall_WoodFramed_NonRes | Stucco + insulation + wood framing + gypsum board | U-factor IP | Pre 1978 | N/A | ASHRAE 90.1, 2022 Table A3.4.3.1, 3.5", R-0 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292
[5 empty] | 1978-1997 | 1986 | Copied from low-rise office alternative table: Package A with heat capacity of 0.0-3.99 (Btu/F-ft²) | 0.13298 | 0.13298 | 0.13298 | 0.13298 | 0.13298 | 0.13298 | 0.13298 | 0.13298 | 0.13298 | 0.13298 | 0.13298 | 0.13298 | 0.13298 | 0.13298 | 0.13298 | 0.13298
[5 empty] | 1998-2007 | 2001 | Table 1-H | 0.084 | 0.084 | 0.092 | 0.092 | 0.092 | 0.092 | 0.092 | 0.092 | 0.092 | 0.084 | 0.084 | 0.084 | 0.084 | 0.084 | 0.084 | 0.084
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.102 | 0.059 | 0.11 | 0.059 | 0.102 | 0.11 | 0.11 | 0.102 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.042 | 0.059
[5 empty] | 2019+ | 2025 | Table 140.3-C | 0.078 | 0.053 | 0.102 | 0.053 | 0.095 | 0.102 | 0.102 | 0.095 | 0.053 | 0.053 | 0.042 | 0.053 | 0.053 | 0.053 | 0.038 | 0.053
Ceiling/Roof | RestaurantFastFood | AtticFloor Reversed | Attic roof (no insulation): asphalt shingles + gypsum board Ceiling (wood-joist): insulation + gypsum board | U-factor IP | Pre 1978 | N/A | Considering 30 years for roof/ insulation replacement. | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 1978-1997 | 1992 |  | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 1998-2007 | 2001 | Table 1-H | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 2008-2018 | 2013 | Table 140.3-B (Wood Framed and Other) | 0.049 | 0.039 | 0.039 | 0.039 | 0.049 | 0.075 | 0.067 | 0.067 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039
[5 empty] | 2019+ | 2025 | Table 140.3-B (Wood Framed and Other) | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.047 | 0.047 | 0.047 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028
Windows | RestaurantFastFood | FixedWindow_NonRes | Single Pane (CBECS 2018, ~ 30 % of windows of Restaurant built before 2000 are single pane) | U-factor IP | Pre 1978 | N/A | 2021 ASHRAE Handbook of Fundamentals - Section 15.9 Table 4 for single pane & T24 2013 Table 140.3-B for double pane (30%-70%) | 0.588 | 0.588 | 0.588 | 0.588 | 0.588 | 0.588 | 0.588 | 0.588 | 0.588 | 0.588 | 0.588 | 0.588 | 0.588 | 0.588 | 0.588 | 0.588
[5 empty] | 1978-1997 | N/A |  | 0.588 | 0.588 | 0.588 | 0.588 | 0.588 | 0.588 | 0.588 | 0.588 | 0.588 | 0.588 | 0.588 | 0.588 | 0.588 | 0.588 | 0.588 | 0.588 | These vintages have better performance because of partial retrofit
|  |  | Double pane |  | 1998-2007 | 2001 | Table 1-H | 0.49 | 0.49 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.34 | 0.36 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.36
|  |  | Single Pane (CBECS 2018, ~ 30 % of windows of Restaurant built before 2000 are single pane) | SHGC | Pre 1978 | N/A | 2021 ASHRAE Handbook of Fundamentals - Section 15.22 Table 10 for single pane & T24, 2013 Table 140.3-B for double pane (30%-70%) | 0.412 | 0.412 | 0.412 | 0.412 | 0.412 | 0.412 | 0.412 | 0.412 | 0.412 | 0.412 | 0.412 | 0.412 | 0.412 | 0.412 | 0.412 | 0.412
[5 empty] | 1978-1997 | N/A |  | 0.412 | 0.412 | 0.412 | 0.412 | 0.412 | 0.412 | 0.412 | 0.412 | 0.412 | 0.412 | 0.412 | 0.412 | 0.412 | 0.412 | 0.412 | 0.412 | These vintages have better performance because of partial retrofit
|  |  | Double pane |  | 1998-2007 | 2001 | Table 1-H (Non North, 10-20% total WWR) | 0.43 | 0.36 | 0.55 | 0.55 | 0.55 | 0.61 | 0.61 | 0.61 | 0.61 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.43
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.22 | 0.25 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.25
Infiltration
|  |  | Building | Zones | Vintage | I_75 (cfm/ft2) 6-sdied Infiltration rate @ 75 pa | Source | CZ1: I-design (cfm/ft²) (4-sided Infiltration rate at normal pressure) (Design flow rate approach and Flow/Exterior Wall Area calculation method)
|  | Infiltration | RestaurantFastFood |  | Pre 1978 | 1.1 | 2022 CASE report (Table 38) | CZ1: 0.43126 |  | Floor or roof area | 2501.0001
[5 empty] | 1978-1997 | 1.1 | 2022 CASE report (Table 38) | CZ1: 0.43126 |  | Walls area | 2000.4
[5 empty] | 1998-2007 | 1.1 | 2022 CASE report (Table 38) | CZ1: 0.43126 |  | Building 4 sided area= | 2000.4
[5 empty] | 2008-2018 | 1 | 2022 CASE report (Table 38) & T24, 2008-2016 (Table 140.3-B) | CZ1: 0.39206 |  | Building 6 sided area= | 7002.4002
[5 empty] | 2019+ | 0.6 | 2022 CASE report (Table 38) & T24, 2025 (Table 140.3-B) | CZ1: 0.23523 |  | 6 sided /4 sided factor= | 3.5005
Source: T24 air barrier requirements (all editions) , the standardized infiltration rate reported in the 2022 CASE report, and Dodge 2023 data
Infiltration_rate_report_14May2025-Short-Version.docx

## HVAC System
HVAC system - RestaurantFastFood
Vintage | Space/Thermal Zone | Heating | Cooling | Air Distribution | Other Systems | Source
Existing | Dining | Gas Furnace (PSZAC) | DX Coil (PSZAC) | CAV (PSZAC) | Economizer for after 2008 | CEUS 2022 + Engineering Judgement
| Kitchen | Gas Furnace (PSZAC) | DX Coil (PSZAC) | CAV (PSZAC) | Makeup Air Unit (Combo with RTU) to supply make-up air exceeding transfer air from dining space (can be included in system13b)
New Construction | Dining | Gas Furnace (PSZAC) | DX Coil (PSZAC) | CAV (PSZAC) | Economizer | T24, 2025 | Demand control ventilation
| Kitchen | Gas Furnace (PSZAC) | DX Coil (PSZAC) | CAV (PSZAC) | HR-Makeup Air Unit (systems that integrate make-up air and heat recovery functions) (can be included in system13b)
Efficiency of HVAC System (Efficiency is capacity-dependent. The following table provides a general estimate of system efficiency based on preliminary simulations in one climate zone, or assuming cooling load based on rule of thumb)
Vintage | Upgrade/Installed year | Gas Furnace | Dining DX cooling (<65,000 Btu/h) | Kitchen DX cooling (>=65,000 and < 135,000 Btu/h ) | Source | Note
Pre 1978 | 2008 | Efficiency 80% | SEER 13 | EER 10.3 | System <65,000: 10 CFR, 2009 (Vol. 74, No. 54 , page 12074) system >65,000: T24, 2008, Table 112-A | Econ Max Position=0.9. *Econ Max Position is set to below 1 to approximate effects of not having fault detection and diagnostics (FDD) requirements, which began in 2013. it can be modeled in E+ either by: - Reducing Maximum Outdoor Air Flow Rate in Controller:OutdoorAir. - Or using FaultModel objects to simulate pre-2013 “no FDD” conditions
1978-1997
1998-2007
2008-2018 | 2013 | Efficiency 80% | SEER 13 | EER 11.2 | System <65,000: 10 CFR, 2013, Table 1 TO § 431.97 System >65,000: T24, 2013, Table 110.2-A | Econ Max Position=0.9
New Construction | 2025 | Efficiency 80% | SEER2 13.4 | EER 11.2 | System <65,000: 10 CFR, 2024 ,Table 19 TO § 431.97(h) System >65,000: T24, 2025, Table 110.2-A | - Econ Max Position=1 - Deduct 0.2 from the required EERs and IEERs for units with a heating section other than electric resistance heat.
Fan Power
Vintage | Approach | System | Total Static Pressure (TSP) (in w.c.) | Fan Efficiency [ACM 2025] | Motor Efficiency | Fan Power Index (W/cfm) | Data Source
Existing | PNNL 90.1-2011, TSP | CAV Kitchen (system <7,437 cfm) | 2.5 | 0.65 | ASHRAE 90.1, 2004, Table 10.8 * |  | Fan power formula: PNNL 20405, 2010, section 5.2.2.5 TSP and fan efficiecncy: PNNL 20405, 2010, Table 5.11, 90.1-04ac values Motor and drive efficiency: ASHRAE 90.1, 2004, Table 10.8
|  | CAV Dining (system <7,437 cfm) | 2.5
Brake horsepower (bhp) = (Supply cfm × TSP in w.c.) / (6356 × fan efficiency)
Fan power (w/cfm) = (bhp × 746) / ( supply cfm × motor efficiency )
New Construction | ACM 2025 | PSZAC (System 3a), CAV kitchen, ≤5,000 cfm | TSP = fan power × motor efficiency × fan efficiency × 6356 / 746 | 0.65 | 2025 ACM Table 12 ** | 0.802 | Fan power index: [ACM 2025, Table 13] Motor efficiency: [ACM 2025, Table 12]
|  | PSZAC (System 3a), CAV dining, ≤5,000 cfm | TSP = fan power × motor efficiency × fan efficiency × 6356 / 746 |  |  | 0.802
* According to PNNL 20405 section 5.2.2.5, the full-load efficiency of the motor serving the fan is taken from ASHRAE 90.1, 2004, Table 10.8, based on motor nameplate and assuming enclosed motors operating at 1,800 rotations per minute (rpm) Motor nameplate size (bhp) = brake horsepower (bhp) × 1.1 ( using a 10% oversizing factor)
** The full‑load efficiency of the motor serving the fan is taken from ACM 2025 Table 12 based on the cfm of the fan. Brake horsepower (bhp) = (Supply cfm from sizing run × fan power in W/cfm) / 746. Note: PSZAC with gas furnace (System 3a SZAC) ≤5,000 cfm. Same index as Restaurant Sit-Down kitchen. Note: PSZAC with gas furnace (System 3a SZAC) ≤5,000 cfm. Same index as Restaurant Sit-Down kitchen.
〖𝐹𝑎𝑛 𝑝𝑜𝑤𝑒𝑟〗_(𝑤/𝑐𝑓𝑚)=(〖𝑇𝑆𝑃〗_(𝑖𝑛 𝑤.𝑐)∗746)/(6356∗𝜇_𝑓𝑎𝑛∗𝜇_𝑚𝑜𝑡𝑜𝑟 )
𝑏ℎ𝑝=(𝑐𝑓𝑚∗〖𝑇𝑆𝑃〗_(𝑖𝑛 𝑤.𝑐.))/〖6356∗𝜇〗_𝑓𝑎𝑛
〖𝐹𝑎𝑛 𝑝𝑜𝑤𝑒𝑟〗_(𝑤/𝑐𝑓𝑚)=(𝑏ℎ𝑝∗746)/(𝑐𝑓𝑚∗𝜇_𝑚𝑜𝑡𝑜𝑟 )
𝑏ℎ𝑝=(〖𝐹𝑎𝑛 𝑝𝑜𝑤𝑒𝑟〗_(𝑤/𝑐𝑓𝑚)∗𝑐𝑓𝑚∗𝜇_𝑚𝑜𝑡𝑜𝑟)/746

## Thermostat
Thermostat Setpoints - RestaurantFastFood
Space/Thermal Zone | Setpoint | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16 | Source
Dining | Heating Setpoint (F) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | T24 2022 - Appendix 5.4B
| Heating Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
| Cooling Setpoint (F) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
| Cooling Setback (F) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
Kitchen | Heating Setpoint (F) | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | PNNL 09.1, 2022 Restaurant prototype
| Heating Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
| Cooling Setpoint (F) | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79
| Cooling Setback (F) | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86
PNNL's comfort range in kitchen is 4 F wider : 66 -79 F (with Heating setback of 60 F and Cooling setback of 86 F)
CPUC has the same setpoint and setback as CEC

## Ventilation
Outdoor Airflow Rate - RestaurantFastFood
Space/Thermal Zone | Number of People | Floor Area (ft²) | cfm/person [T24, 2025, Equation 120.1-F and Table 120.1-A] | cfm/ft² [T24, 2025, Equation 120.1-F and Table 120.1-A] | Required Exhaust Rate [T24, 2025, Table 120.1-B – minimum exhaust rates] | Total cfm Driven by People | Total cfm Driven by Area | Total cfm Driven by Exhaust | Total cfm | Notes
Dining | 41.2652 | 1250.46 | 15 | 0.15 | 2 restroom, each 25/50 cfm pr unit | 618.9777 | 187.569 | 100 | 618.9777
Kitchen | 3.7514 | 1250.46 | 15 | 0.15 | 0.7 cfm/ft2 | 56.2707 | 187.569 | 875.322 | 875.322
Attic
Fine storage is defined for normal inventory that doesn't require an extra exhaust rate based on the space functions in T24, Part6, 2025, Table 120.1 B.
Exhaust hood
Type of Hood |  | Max Exhaust Flow Rate (cfm/ft) [T24, 2025, Table 140.9-C] | Hood Length (ft) * [CKV, 2004] & | Hood Exhaust Rate (cfm) | Note
Type I , wall-mounted canopy, medium duty hood |  | 210 | 15.25 | 3202.5
Efficiency of exhaust fan is 50% (according to ACM, 2025,section 5.7.3)
Quick Service Restaurant Hood Appliance
Appliance | Count | Length (ft) | Source
Two Fryers side | 2 | 2.5 | CKV Design Guide, 2004
Fryer drip station (doesn't generate heat or grease but still need to be covered) | 1 | 1.25
Griddle | 1 | 4
Convection oven | 1 | 2.5
Charbroiler | 1 | 4 | Charbroiler is common in fast food with burgers in the menu (e.g., KFC). So, we've decide to add this appliance to the above mentioned ones
Total cooking line length (ft) | 14.25
Hood length (ft) (+1 ft buffer) | 15.25

## Water Heater
Water Heater Summary - RestaurantFastFood
Vintage | WH Type | Efficiency | Number of WH | Tank Volume (gal) | Tank Loss | Source
Existing | Gas | 0.8 | 1 | See table below for CZ-specific values: Climate Zone Water Heater Sizing and Loss Coefficients, Storage Volume column (col F) | See table below: Climate Zone Water Heater Sizing and Loss Coefficients, Standby Loss column (col G) | See table below for sources: Climate Zone Water Heater Sizing and Loss Coefficients
New Construction | Gas | 0.8 | 1 | See table below for CZ-specific values: Climate Zone Water Heater Sizing and Loss Coefficients, Storage Volume column (col F) | See table below: Climate Zone Water Heater Sizing and Loss Coefficients, Standby Loss column (col G) | See table below for sources: Climate Zone Water Heater Sizing and Loss Coefficients
Peak Hot Water Consumption
Space Name | Baseline WH Type [T24, 2022, Appendix 5.4A , sheet: "2022 SpaceFuncData-Input"] | Total Area (ft²) | Number of People | Hot Water Usage Specification (gal/hr per person) [T24, 2022, Appendix 5.4A , sheet: "2022 SpaceFuncData-Input"] | Peak Hot Water Usage (gal/hr) | Peak Hot Water Usage (gal/min) | Note
Dining | Gas | 1250.46 | 41.2652 | 0.116 | 4.7868 | 0.079779 | Assumption: HW usage rate for the restaurant dining space was calculated at 20% of the hot water usage rate specified in the 2025 Nonres ACM 2024, Appendix 5.4A (equivalent to applying the full rate to 20% of the dining floor area)
Kitchen | Gas | 1250.46 | 3.7514 | N/A | 53.6 | 0.89333 | Peak HW Usage is based on the fixture calulcation from the table below.
Total | Gas storage |  |  |  | 75 |  | Minimum peak hot water usage is 75 gal according to ACM 2025
Total | Electric resistance |  |  |  | 0
[6 empty] | Design Guide: Advanced Water Heating for Foodservice, 2022, Table 8] |  |  | Design Guide: Advanced Water Heating for Foodservice, 2023, Table 11]
Technical_Design_Guide.pdf
Peak Water Heater Capacity, Tank Capacity, and Tank Loss
Fixture | Tank Recovery Rate (gal/h) | Fixture Count | Storage Heater Min Recovery Rate (gal/hr) | Source
Room sinks | 5 | 1 | 5 | Design Guide: Advanced Water Heating for Foodservice (2022) , Table 6,7: Small Quick Restaurant Kitchen Design Guide: Advanced Water Heating for Foodservice (2023) , Table11: Small Quick Restaurant Kitchen
Hand sinks | 5 | 1 | 5
3-Compartment sinks | 42 | 1 | 42
Mop sink | 15 | 1 | 15
Utility or pre-soak sinks | 5
Minimum Recovery Rate (gal/h) |  |  | 53.6 | Design Guide: Advanced Water Heating for Foodservice, 2023, Table 11] *Minimum recovery rate discount factor of 20% for using single service utensils
Input Rate (Btu/h) |  |  | 56000 | .Design Guide: Advanced Water Heating for Foodservice, 2023, Table 12]
Tank volume (gal) |  |  | 75 | .Design Guide: Advanced Water Heating for Foodservice, 2023, Table 12]
Standby Loss (Btu/hr) |  |  | 875.3322 | Title 20, §1605.1 Table F-4 (Standby loss equation: )
Off/On Cycle Loss Coefficient to Ambient Temperature (Btu/h-F) |  |  | 12.5047 | Title 20 / 10 CFR 431.102: UA = SL / 70 °F rating ΔT (same as climate-zone col I). Not ambient T.
For Gas Water Heater: UA (Btu/h-°F) = Q_SL (Btu/h) / 70 °F. 70 is the Title 20 / 10 CFR 431.102 rating ΔT (stored water minus ambient), not ambient T.
Rating ΔT (°F) | 70 | 10 CFR 431.102: gas standby loss is Btu/h based on a 70 °F temperature differential between stored water and ambient. Not ACM indoor temperature.
** For Electric Water Heater: UA(Btu/h-°F)​= 0.0834 *SL​ (%/hr)*V gal
Design supply temperature (°F) | 135 | CEC-400-2022-009-CMF-REV2-AP5.4B
WH system factor | 0.6 | 2025 ACM §5.9.2 Rated Capacity
Water mass conversion (lb/gal) | 8.2877 | 2025 ACM §5.9.2 Rated Capacity
Reheat multiplier | 0.4 | 2025 ACM §5.9.2 Storage Volume
Climate Zone Water Heater Sizing and Loss Coefficients
Climate Zone | Minimum Monthly Mains Temp (°F) [T24 2022 - Appendix 5.4B] | Heat Output (Btu/hr) [ACM, 2025, 5.9.2: Rated capacity section] | WH Capacity (Btu/hr) [ACM, 2025, 5.9.2: Rated capacity section] | Required Energy Input (Btu/hr) | Storage Volume (gal) | Standby Loss [Title 20, §1605.1 Table F-4; Appendix B: Water Heating Calculation Method] |  | Off/On Cycle Loss Coefficient to Ambient Temp |  | Source/Note
CZ01 | 47.9 | 54139.4002 | 32483.6401 | 60000 | 34 | 716.4047 | Btu/hr | 10.2344 | Btu/h·°F | Required Energy Input: vendor/available catalog size (Market data table). Storage Volume: standard/available catalog tank size (Market data table). Off/On-cycle UA (col I): gas SL / 70 °F rating ΔT (10 CFR 431.102 / Title 20), not ambient T.
CZ02 | 50.8 | 52336.8255 | 31402.0953 | 60000 | 34 | 716.4047 | Btu/hr | 10.2344 | Btu/h·°F
CZ03 | 52.2 | 51466.617 | 30879.9702 | 60000 | 34 | 716.4047 | Btu/hr | 10.2344 | Btu/h·°F
CZ04 | 52.7 | 51155.8282 | 30693.4969 | 60000 | 34 | 716.4047 | Btu/hr | 10.2344 | Btu/h·°F
CZ05 | 51.6 | 51839.5635 | 31103.7381 | 60000 | 34 | 716.4047 | Btu/hr | 10.2344 | Btu/h·°F
CZ06 | 56.8 | 48607.3605 | 29164.4163 | 60000 | 34 | 716.4047 | Btu/hr | 10.2344 | Btu/h·°F
CZ07 | 58.4 | 47612.8365 | 28567.7019 | 60000 | 34 | 716.4047 | Btu/hr | 10.2344 | Btu/h·°F
CZ08 | 58.4 | 47612.8365 | 28567.7019 | 60000 | 34 | 716.4047 | Btu/hr | 10.2344 | Btu/h·°F
CZ09 | 57.6 | 48110.0985 | 28866.0591 | 60000 | 34 | 716.4047 | Btu/hr | 10.2344 | Btu/h·°F
CZ10 | 57.1 | 48420.8872 | 29052.5323 | 60000 | 34 | 716.4047 | Btu/hr | 10.2344 | Btu/h·°F
CZ11 | 50.5 | 52523.2987 | 31513.9792 | 60000 | 34 | 716.4047 | Btu/hr | 10.2344 | Btu/h·°F
CZ12 | 51.4 | 51963.879 | 31178.3274 | 60000 | 34 | 716.4047 | Btu/hr | 10.2344 | Btu/h·°F
CZ13 | 51.7 | 51777.4057 | 31066.4434 | 60000 | 34 | 716.4047 | Btu/hr | 10.2344 | Btu/h·°F
CZ14 | 50.1 | 52771.9297 | 31663.1578 | 60000 | 34 | 716.4047 | Btu/hr | 10.2344 | Btu/h·°F
CZ15 | 63.2 | 44629.2645 | 26777.5587 | 60000 | 34 | 716.4047 | Btu/hr | 10.2344 | Btu/h·°F
CZ16 | 41.4 | 58179.654 | 34907.7924 | 60000 | 34 | 716.4047 | Btu/hr | 10.2344 | Btu/h·°F
Market data
Catalog gas input (Btu/h) | Input source | Elec resistance tank (kW) | Elec resistance (Btu/h) | Catalog gas tank (gal) | Tank source | Elec tank (gal) | Elec tank source | Sources and links → Note tab
60000 | Grainger | 1.5 | 5118 | 34 | ENERGY STAR | 6 | Grainger
75100 | Grainger | 2 | 6824 | 35 | Grainger | 10 | Grainger
76000 | Both | 3 | 10236 | 48 | Grainger | 15 | Grainger
80000 | Grainger | 4.5 | 15355 | 50 | Both | 20 | Grainger
99900 | ENERGY STAR | 6 | 20473 | 55 | ENERGY STAR | 28 | Grainger
100000 | Both | 8 | 27297 | 60 | ENERGY STAR | 30 | Grainger
120000 | ENERGY STAR | 9 | 30709 | 65 | Both | 36 | Grainger
125000 | Both | 10 | 34121 | 72 | Grainger | 40 | Grainger
130000 | Both | 12 | 40946 | 75 | Both | 47
145000 | ENERGY STAR | 12.1 | 41287 | 76 | Grainger | 50
150000 | ENERGY STAR | 18 | 61419 | 80 | Both | 65
156000 | Grainger | 24 | 81891 | 82 | Grainger | 80
160000 | Both | 27 | 92128 | 85 | Grainger | 85
175000 | ENERGY STAR | 36 | 122837 | 90 | Both | 105
180000 | Grainger | 54 | 184256 | 91 | Grainger | 120
199000 | ENERGY STAR |  |  | 100 | Both
199900 | Both |  |  | 110 | ENERGY STAR
200000 | ENERGY STAR |  |  | 119 | Both
250000 | Both |  |  | 125 | ENERGY STAR
251000 | ENERGY STAR
270000 | Grainger
285000 | ENERGY STAR
300000 | Both
320000 | ENERGY STAR
360000 | Grainger
398000 | ENERGY STAR
399000 | ENERGY STAR
399900 | Both
499900 | Grainger
550000 | Grainger
715000 | Grainger

## Interior Lights
Interior Lighting - RestaurantFastFood
Space Type | New Construction |  |  | Existing
| LPD (W/ft²) | Additional LPD for Portable Lighting (W/ft²) | Source | LPD (W/ft²) | Additional LPD for Portable Lighting (W/ft²) | Source
Dining Area (Cafeteria/Fast Food) | 0.45 | 0.25 | T24, 2025, Table 140.6-C (Area category method) | 1 |  | T24, 2016, Table 140.6-C (Area category method) LPD of "All other spaces" is considered for storage space
Kitchen/Food Preparation Area | 0.95 |  |  | 1.2
Attic
Background Data [To be deleted prior to publication]
Existing | Whole Building | All other building | 0.4 |  | T24, 2019, Table 140.6 B
| Area Category | 0 | 0.65 |  | T24, 2019, Table 140.6-C
|  | 0 | 0.4
|  | 0 | 0.4
Existing | Whole Building | All other building | 0.5 |  | T24, 2016, Table 140.6 B
| Area Category | ZONE1 OFFICE | 0.75 |  | T24, 2016, Table 140.6-C
|  | ZONE2 FINE STORAGE | 0.5
|  | ZONE3 BULK STORAGE | 0.5
Existing | Whole Building | All other building | 0.6 |  | T24, 2013, Table 140.6 B
| Area Category | ZONE1 OFFICE | 0.75 |  | T24, 2013, Table 140.6-C
|  | ZONE2 FINE STORAGE | 0.6
|  | ZONE3 BULK STORAGE | 0.6

## Ext Lighting
Exterior Lighting - RestaurantFastFood
Motion Controlled Luminaires (W) | Non-motion Controlled Luminaires (W) | Total (W) | Source
351.028 | 116.7562 | 467.7841 | T24, 2022
Exterior Lighting
Items (Assume LZ2) | Assumptions [2019 Outdoor Lighting CASE Report & PNNL 90.1-2010 TSD] |  | Unit | Lighting Power Allowance [T24, 2025, Table 140.7-A & 140.7-B] | Unit | Exterior Lighting Power (W)
IWA (Initial Wattage Allowance) |  |  |  | 200 | (W) | 200
Parking area | 400 ft² for every parking space [2019 Lighting CASE report, Appendix H] 1 parking space per 250 ft² of gross building area [2019 Lighting CASE report,Table 38] | 4001.472 | (ft²) | 0.019 | (W/ft²) | 76.028
Building Entrance | 2 building entrance (1 per 10,000 ft² footprint) | 1 | (count) | 15 | (W/ea) | 15
Hardscape Ornamental Light | 0.1 ft² per 1 ft² of gross building area [2019 Lighting CASE report,Table 36] | 250.092 | (ft²) | 0.007 | (W/ft²) | 1.7506
Building façade | 0.1 W per 1 ft² of facade area Façade Area = Perimeter × 0.5 × 10 ft (10 ft is the building height ) * The 0.5 factor assumes that only half of the perimeter walls are lit. -Formula ia developed based on the 2019 Outdoor Lighting CASE report | 1000 | (ft²) | 0.1 | (W/ft²) | 100
Drive up windows | 1 per 1500 ft² of gross building area [2019 Lighting CASE report,Table 36] | 2 | (count) | 30 | (W/ea) | 60
Outdoor dining | 1 ft² per 5 ft² of gross building area [2019 Lighting CASE report,Table 36] | 500.184 | (ft²) | 0.03 | (W/ft²) | 15.0055
Motion controlled Luminaires | [5 empty] | 351.028
Non-motion-controlled Luminaires | [5 empty] | 116.7562
TOTAL | [5 empty] | 467.7841
Perimeter (ft) | 200
Total floor area (ft²) | 2500.92
Floors | 1
Height (ft) | 10

## Equipment
Equipment - RestaurantFastFood
Space Type | Plug Load Power Density (W/ft²) | ReachIn Refrigerator and ReachInFreezer Power (W) - 24/7 | Refrigerator Power Density (W/ft²) | Gas Power Density (Btu/hr-ft²) | Source
Dining Area (Cafeteria/Fast Food) | 0.5 |  | 0.25 |  | Others inputs: T24 2025 - Appendix 5.4A: "2022 SpaceFuncData-Input"
Kitchen/Food Preparation Area | 1.5 | 590 | 1.12 | 35.08 | - ReachIn Refrigerator and ReachInFreezer load : [PNNL ASHRAE 90.1 2022 Fast Food prototype] - Other inputs: T24 2025 - Appendix 5.4A: "2022 SpaceFuncData-Input" Plug load density is confirmed by the findings Plug load and schedules project with CEC, 2025
Attic
*ReachIn Refrigerator and ReachInFreezer Power is based on PNNL model. It doesn’t exist in the CEC prototype model.
* Gas load is very low compared to PNNL model (237.4 Btu/hr-ft2 for Kitchen)
Refrigerator load will be simulated as equipment load

## Schedules
Schedules - RestaurantFastFood
Zone | Schedule Category | Schedule | Source | Type | Hour
[5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Dining | Restaurant | Occupancy | PNNL,ASHRAE 90.1, 2022 Fast Food Restaurant prototype (It has higher occupancy rate during morning compared to T24 2022 - Appendix 5.4B) | Weekday | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.4 | 0.4 | 0.4 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.8 | 0.8 | 0.8 | 0.5 | 0.35 | 0.2
|  |  |  | Saturday | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.4 | 0.2 | 0.45 | 0.5 | 0.5 | 0.35 | 0.3 | 0.3 | 0.3 | 0.7 | 0.9 | 0.7 | 0.65 | 0.55 | 0.35
|  |  |  | Sunday | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.3 | 0.2 | 0.25 | 0.35 | 0.55 | 0.65 | 0.7 | 0.35 | 0.2 | 0.2
Dining | Restaurant | Lights | T24 2022 - Appendix 5.4B, [Restaurant] Updated based on the equipment schedule from the plug load and schedule project with CEC | Weekday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.3 | 0.67 | 0.73 | 0.75 | 0.85 | 0.85 | 0.85 | 0.83 | 0.72 | 0.65 | 0.67 | 0.75 | 0.85 | 0.85 | 0.85 | 0.75 | 0.57 | 0.3
|  |  |  | Saturday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.3 | 0.67 | 0.73 | 0.75 | 0.85 | 0.85 | 0.85 | 0.83 | 0.72 | 0.65 | 0.67 | 0.75 | 0.85 | 0.85 | 0.85 | 0.75 | 0.57 | 0.3
|  |  |  | Sunday | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.67 | 0.73 | 0.75 | 0.85 | 0.85 | 0.85 | 0.83 | 0.72 | 0.65 | 0.67 | 0.75 | 0.85 | 0.85 | 0.85 | 0.75 | 0.57 | 0.3
Dining | Restaurant | ElecEquipment | Plug load and schedules project with CEC, 2025 | Weekday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.3 | 0.72 | 0.78 | 0.8 | 0.9 | 0.9 | 0.9 | 0.88 | 0.77 | 0.7 | 0.72 | 0.8 | 0.9 | 0.9 | 0.9 | 0.8 | 0.62 | 0.3
|  |  |  | Saturday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.3 | 0.72 | 0.78 | 0.8 | 0.9 | 0.9 | 0.9 | 0.88 | 0.77 | 0.7 | 0.72 | 0.8 | 0.9 | 0.9 | 0.9 | 0.8 | 0.62 | 0.3
|  |  |  | Sunday | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.72 | 0.78 | 0.8 | 0.9 | 0.9 | 0.9 | 0.88 | 0.77 | 0.7 | 0.72 | 0.8 | 0.9 | 0.9 | 0.9 | 0.8 | 0.62 | 0.3
Dining | Restaurant | HVACAvail | T24 2022 - Appendix 5.4B , [Restaurant] Updated based on the adopted PNNL occupancy | Weekday | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Saturday | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Sunday | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Dining | Restaurant | ServiceHotWater | T24 2022 - Appendix 5.4B, [Restaurant] Updated based on the adopted PNNL occupancy | Weekday | 0.2 | 0 | 0 | 0 | 0 | 0.6 | 0.6 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25
|  |  |  | Saturday | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3
|  |  |  | Sunday | 0.25 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2
Dining | Restaurant | Infiltration | T24 2022 - Appendix 5.4B, [Restaurant] Updated based on the adopted PNNL occupancy | Weekday | 0.25 | 0 | 0 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  |  | Saturday | 0.25 | 0 | 0 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  |  | Sunday | 0.25 | 0 | 0 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Dining | Restaurant | Refrigeration | T24 2022 - Appendix 5.4B, [Restaurant] | Weekday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Saturday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Sunday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
Dining | Restaurant | HtgSetpt | T24 2022 - Appendix 5.4B, [Restaurant] | Weekday | 70 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
|  |  |  | Saturday | 70 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
|  |  |  | Sunday | 70 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
Dining | Restaurant | ClgSetpt | T24 2022 - Appendix 5.4B, [Restaurant] | Weekday | 75 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
|  |  |  | Saturday | 75 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
|  |  |  | Sunday | 75 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
Kitchen
Kitchen | Kitchen | occupancy | PNNL,ASHRAE 90.1, 2022 Fast Food Restaurant prototype (It has higher occupancy rate during morning compared to T24 2022 - Appendix 5.4B) | Weekday | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.4 | 0.4 | 0.4 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.8 | 0.8 | 0.8 | 0.5 | 0.35 | 0.2
|  |  |  | Saturday | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.4 | 0.2 | 0.45 | 0.5 | 0.5 | 0.35 | 0.3 | 0.3 | 0.3 | 0.7 | 0.9 | 0.7 | 0.65 | 0.55 | 0.35
|  |  |  | Sunday | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.3 | 0.2 | 0.25 | 0.35 | 0.55 | 0.65 | 0.7 | 0.35 | 0.2 | 0.2
Kitchen | Kitchen | Lights | T24 2022 - Appendix 5.4B, [Restaurant] Updated based on the equipment schedule from the plug load and schedule project with CEC | Weekday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.3 | 0.67 | 0.73 | 0.75 | 0.85 | 0.85 | 0.85 | 0.83 | 0.72 | 0.65 | 0.67 | 0.75 | 0.85 | 0.85 | 0.85 | 0.75 | 0.57 | 0.3
|  |  |  | Saturday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.3 | 0.67 | 0.73 | 0.75 | 0.85 | 0.85 | 0.85 | 0.83 | 0.72 | 0.65 | 0.67 | 0.75 | 0.85 | 0.85 | 0.85 | 0.75 | 0.57 | 0.3
|  |  |  | Sunday | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.67 | 0.73 | 0.75 | 0.85 | 0.85 | 0.85 | 0.83 | 0.72 | 0.65 | 0.67 | 0.75 | 0.85 | 0.85 | 0.85 | 0.75 | 0.57 | 0.3
Kitchen | Kitchen | ElecEquipment | Plug load and schedules project with CEC, 2025 | Weekday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.3 | 0.72 | 0.78 | 0.8 | 0.9 | 0.9 | 0.9 | 0.88 | 0.77 | 0.7 | 0.72 | 0.8 | 0.9 | 0.9 | 0.9 | 0.8 | 0.62 | 0.3
|  |  |  | Saturday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.3 | 0.72 | 0.78 | 0.8 | 0.9 | 0.9 | 0.9 | 0.88 | 0.77 | 0.7 | 0.72 | 0.8 | 0.9 | 0.9 | 0.9 | 0.8 | 0.62 | 0.3
|  |  |  | Sunday | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.72 | 0.78 | 0.8 | 0.9 | 0.9 | 0.9 | 0.88 | 0.77 | 0.7 | 0.72 | 0.8 | 0.9 | 0.9 | 0.9 | 0.8 | 0.62 | 0.3
Kitchen | Kitchen | HVACAvail | T24 2022 - Appendix 5.4B , [Restaurant] Updated based on the adopted PNNL occupancy | Weekday | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Saturday | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Sunday | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Kitchen | Kitchen | ServiceHotWater | T24 2022 - Appendix 5.4B, [Restaurant] Updated based on the adopted PNNL occupancy | Weekday | 0.2 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0.3 | 0.3 | 0.3 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.2
|  |  |  | Saturday | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0.3 | 0.3 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.2
|  |  |  | Sunday | 0.25 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0.3 | 0.3 | 0.3 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2
Kitchen | Kitchen | Infiltration | T24 2022 - Appendix 5.4B, [Restaurant] Updated based on the adopted PNNL occupancy | Weekday | 0.25 | 0 | 0 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  |  | Saturday | 0.25 | 0 | 0 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  |  | Sunday | 0.25 | 0 | 0 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Kitchen | Kitchen | ExhaustHoodEqualOrLessThan5000cfm | T24 2022 - Appendix 5.4B, [Restaurant] Updated based on the adopted PNNL occupancy | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
Kitchen | Kitchen | ExhaustHoodGreaterThan 5000cfm | T24 2022 - Appendix 5.4B, [Restaurant] Updated based on the adopted PNNL occupancy | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 0.5 | 1 | 0.5 | 1 | 0.5 | 1 | 0.5 | 1 | 0.5 | 1 | 0.5 | 1 | 0.5 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 0.5 | 1 | 0.5 | 1 | 0.5 | 1 | 0.5 | 1 | 0.5 | 1 | 0.5 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 0.5 | 1 | 0.5 | 1 | 0.5 | 1 | 0.5 | 1 | 0.5 | 1 | 0.5 | 0 | 0 | 0 | 0 | 0
Kitchen | Kitchen | Refrigeration | T24 2022 - Appendix 5.4B, [Restaurant] | Weekday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Saturday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Sunday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
Kitchen | Kitchen | GasEquipment | T24 2022 - Appendix 5.4B, [Restaurant] Updated based on the equipment schedule from the plug load and schedule project with CEC | Weekday | 0.5 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.75 | 0.75 | 0.75 | 0.9 | 0.9 | 0.9 | 0.9 | 0.75 | 0.5 | 0.5
|  |  |  | Saturday | 0.5 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.75 | 0.75 | 0.75 | 0.9 | 0.9 | 0.9 | 0.9 | 0.75 | 0.75 | 0.5
|  |  |  | Sunday | 0.5 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.75 | 0.75 | 0.75 | 0.9 | 0.9 | 0.9 | 0.9 | 0.75 | 0.5 | 0.5
Kitchen | Kitchen | HtgSetpt | Thermostat Setpoints of PNNL 09.1, 2022 Restaurant prototype and HVAC availability schedule of CEC Restaurant prototype | Weekday | 66 | 60 | 60 | 60 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66
|  |  |  | Saturday | 66 | 60 | 60 | 60 | 60 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66
|  |  |  | Sunday | 66 | 60 | 60 | 60 | 60 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66
Kitchen | Kitchen | ClgSetpt | Thermostat Setpoints of PNNL 09.1, 2022 Restaurant prototype and HVAC availability schedule of CEC Restaurant prototype | Weekday | 79 | 86 | 86 | 86 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79
|  |  |  | Saturday | 79 | 86 | 86 | 86 | 86 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79
|  |  |  | Sunday | 79 | 86 | 86 | 86 | 86 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79
Other
| Building | ExtLightingNonMotionCtrl |  | Weekday | bar: Hour 1 to Hour 24
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
| Building | ExtLightingMotionCtrl |  | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Dining | Building | DiningAreaPeopleActivityLevel | Based on Activity level schedules in CEC Prototypes and assumed spaces for Basement | Weekday | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2
|  |  |  | Saturday | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2
|  |  |  | Sunday | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2
Kitchen | Building | KitchenPeopleActivityLevel | Based on Activity level schedules in CEC Prototypes and assumed spaces for Basement | Weekday | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8
|  |  |  | Saturday | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8
|  |  |  | Sunday | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8
;

## Energy Usage (hidden)
CalBEM Energy Consumption - RestaurantFastFood | [7 empty] | National Average (EnergyStar Portfolio Manager) |  |  |  | CEUS Energy Consumption - Restaurant
Prototype | CZ | CalBEM Electricity EUI (KBTU/ft²) | CalBEM Gas EUI (KBTU/ft²) | CalBEM Total EUI (KBTU/ft²) | New Construction Electricity EUI (KBTU/ft²) | New Construction Gas EUI (KBTU/ft²) | New Construction Total EUI (KBTU/ft²) | National Average | Acceptable Range (25% Higher) | Acceptable Range (25% Lower) | National Average Acceptable EUI Range | Prototype | CZ | Total Floorspace (Thousand of ft²) | CEUS 2022 Electricity EUI (kBtu/ft²) | CEUS 2022 Gas EUI (kBtu/ft²) | CEUS 2022 Total EUI (kBtu/ft²) | Acceptable Range (25% Higher) | Acceptable Range (25% Lower) | CEUS 2022 Acceptable EUI Range
RetailStripMall | 1 | [6 empty] | 442.6 | 553.25 | 331.95 | 221.3 | Restaurant | 1 | 2670.248 | 140.2134 | 188.3968 | 328.6101 | 410.7627 | 246.4576 | 164.3051
| 2 | [6 empty] | 442.6 | 553.25 | 331.95 | 221.3 |  | 2 | 4962.8202 | 115.4344 | 178.5959 | 294.0304 | 367.5379 | 220.5228 | 147.0152
| 3 | [6 empty] | 442.6 | 553.25 | 331.95 | 221.3 |  | 3 | 23016.1888 | 121.6825 | 177.6653 | 299.3479 | 374.1848 | 224.5109 | 149.6739
| 4 | [6 empty] | 442.6 | 553.25 | 331.95 | 221.3 |  | 4 | 11906.9501 | 121.6795 | 177.2298 | 298.9093 | 373.6366 | 224.1819 | 149.4546
| 5 | [6 empty] | 442.6 | 553.25 | 331.95 | 221.3 |  | 5 | 2232.1752 | 116.8971 | 182.68 | 299.577 | 374.4713 | 224.6828 | 149.7885
| 6 | [6 empty] | 442.6 | 553.25 | 331.95 | 221.3 |  | 6 | 19264.5577 | 114.3076 | 210.8626 | 325.1702 | 406.4628 | 243.8777 | 162.5851
| 7 | [6 empty] | 442.6 | 553.25 | 331.95 | 221.3 |  | 7 | 11474.8437 | 139.927 | 228.2706 | 368.1976 | 460.247 | 276.1482 | 184.0988
| 8 | [6 empty] | 442.6 | 553.25 | 331.95 | 221.3 |  | 8 | 29165.6468 | 124.0973 | 226.014 | 350.1113 | 437.6392 | 262.5835 | 175.0557
| 9 | [6 empty] | 442.6 | 553.25 | 331.95 | 221.3 |  | 9 | 44906.6072 | 111.9489 | 217.8953 | 329.8442 | 412.3052 | 247.3831 | 164.9221
| 10 | [6 empty] | 442.6 | 553.25 | 331.95 | 221.3 |  | 10 | 24025.7033 | 129.0838 | 231.9237 | 361.0075 | 451.2594 | 270.7557 | 180.5038
| 11 | [6 empty] | 442.6 | 553.25 | 331.95 | 221.3 |  | 11 | 8514.5666 | 141.1332 | 172.3969 | 313.53 | 391.9126 | 235.1475 | 156.765
| 12 | [6 empty] | 442.6 | 553.25 | 331.95 | 221.3 |  | 12 | 37639.2204 | 145.5245 | 191.7377 | 337.2622 | 421.5777 | 252.9466 | 168.6311
| 13 | [6 empty] | 442.6 | 553.25 | 331.95 | 221.3 |  | 13 | 12120.1215 | 147.9323 | 194.185 | 342.1173 | 427.6467 | 256.588 | 171.0587
| 14 | [6 empty] | 442.6 | 553.25 | 331.95 | 221.3 |  | 14 | 6251.7396 | 119.7658 | 215.3254 | 335.0912 | 418.864 | 251.3184 | 167.5456
| 15 | [6 empty] | 442.6 | 553.25 | 331.95 | 221.3 |  | 15 | 12622.5049 | 139.1963 | 260.7922 | 399.9885 | 499.9857 | 299.9914 | 199.9943
| 16 | [6 empty] | 442.6 | 553.25 | 331.95 | 221.3 |  | 16 | 23693.2853 | 127.4641 | 198.8373 | 326.3014 | 407.8767 | 244.726 | 163.1507
Ref: CEUS 2022 Report
And converted FZ level data to CZ level
Restaurants have only one category in CEUS data.
Background Data [To be deleted prior to publication]
| Screenshot of assumption for the national average in the EnergyStar Portfolio Manager website | [10 empty] | EIA 2018: | U.S. Energy Information Administration - EIA - Independent Statistics and Analysis
ENERGY STAR Portfolio Manager Upgrade

## Weights (hidden)
% of Floor Area per CZ and Vintage Bin - Restaurant | [7 empty] | % of Floor Area per CZ and Vintage Bin - Restaurant
Prototype | CZ | Vintage Bin | [5 empty] | Prototype | Vintage Bin | CZ
|  | Pre-1978 | 1978-1997 | 1998-2007 | 2008-2018 | Not available |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
Restaurant | 1 | [5 empty] | 0% | Restaurant | Pre-1978 | [16 empty] | 0%
| 2 | [5 empty] | 0% |  | 1978-1997 | [16 empty] | 0%
| 3 | [5 empty] | 0% |  | 1998-2007 | [16 empty] | 0%
| 4 | [5 empty] | 0% |  | 2008-2018 | [16 empty] | 0%
| 5 | [5 empty] | 0% |  | Not available | [16 empty] | 0%
| 6 | [5 empty] | 0% |  | Total | [16 empty] | 0%
| 7 | [5 empty] | 0%
| 8 | [5 empty] | 0%
| 9 | [5 empty] | 0%
| 10 | [5 empty] | 0%
| 11 | [5 empty] | 0%
| 12 | [5 empty] | 0%
| 13 | [5 empty] | 0%
| 14 | [5 empty] | 0%
| 15 | [5 empty] | 0%
| 16 | [5 empty] | 0%
| Statewide | [5 empty] | 0%
Ref: CEUS 2022 dataset
And converted FZ level data to CZ level
Restaurants have only one category in CEUS data.
Background Data [To be deleted prior to publication]

## EV Charger (hidden)
EV Charger - RestaurantFastFood
TBD

## PV (hidden)
PV - RestaurantFastFood
TBD

## Data (hidden)
Space Function | Electric Equipment Load Intensity | Electric Equipment Load Intensity | LPD
Aging Eye/Low-vision (Corridor Area) |  |  | 2013 | 2016 | 2019 | 2025
Aging Eye/Low-vision (Dining)
Aging Eye/Low-vision (Lobby, Main Entry)
Aging Eye/Low-vision (Lounge/Waiting Area)
Aging Eye/Low-vision (Multipurpose Room)
Aging Eye/Low-vision (Religious Worship Area)
Aging Eye/Low-vision (Restroom)
Aging Eye/Low-vision (Stairwell)
Audience Seating Area
Auditorium Area
Auto Repair / Maintenance Area
Barber, Beauty Salon, Spa Area
Civic Meeting Place Area
Classroom, Lecture, Training, Vocational Areas
Concourse and Atria Area
Convention, Conference, Multipurpose and Meeting Area
Copy Room
Corridor Area
Dining Area (Bar/Lounge and Fine Dining)
Dining Area (Cafeteria/Fast Food)
Dining Area (Family and Leisure)
Electrical, Mechanical, Telephone Rooms
Exercise/Fitness Center and Gymnasium Areas
Financial Transaction Area
Healthcare Facility and Hospitals (Exam/Treatment Room)
Healthcare Facility and Hospitals (Imaging Room)
Healthcare Facility and Hospitals (Medical Supply Room)
Healthcare Facility and Hospitals (Nursery)
Healthcare Facility and Hospitals (Nurse's Station)
Healthcare Facility and Hospitals (Operating Room)
Healthcare Facility and Hospitals (Patient Room)
Healthcare Facility and Hospitals (Physical Therapy Room)
Healthcare Facility and Hospitals (Recovery Room)
Hotel Function Area
Kitchen/Food Preparation Area
Kitchenette or Residential Kitchen
Laboratory, Scientific
Laundry Area
Library (Reading Area)
Library (Stacks Area)
Lobby, Main Entry
Locker Room
Lounge, Breakroom, or Waiting Area
Manufacturing, Commercial & Industrial Work Area (Low Bay)
Manufacturing, Commercial & Industrial Work Area (High Bay)
Manufacturing, Commercial & Industrial Work Area (Precision)
Museum Area (Exhibition/Display)
Museum Area (Restoration Room)
Office Area (>250 square feet)
Office Area (<250 square feet)
Parking Garage Area (Parking Zone and Ramps)
Parking Garage Area (Daylight Adaptation Zones)
Pharmacy Area
Retail Sales Area (Grocery Sales)
Retail Sales Area (Retail Merchandise Sales)
Retail Sales Area (Fitting Room)
Religious Worship Area
Restrooms
Stairwell
Storage, Commercial/Industrial (Warehouse)
Storage, Commercial/Industrial (Refrigerated)
Storage, Commercial/Industrial (Shipping & Handling)
Storage (General)
Sports Arena - Playing Area (> 5,000 Spectators)
Sports Arena - Playing Area (2,000 - 5,000 Spectators)
Sports Arena - Playing Area (< 2,000 Spectators)
Sports Arena - Playing Area (Recreational)
Theater Area (Motion Picture)
Theater Area (Performance)
Transportation Function (Baggage Area)
Transportation Function (Ticketing Area)
Videoconferencing Studio
High-Rise Residential Living Spaces
Hotel/Motel Guest Room
All other
Attic
Reception Area
Elevator
Plenum
IT Room (EPD 12)
Computer Room (EPD 20)
Server Room (EPD 45)