## Notes
Data Sources
Dataset | Dodge 2023
| Commercial End-Use Survey (CEUS) 2022 | https://www.energy.ca.gov/publications/2023/2022-california-commercial-end-use-survey-ceus-final-report
| Comstock 2023 | https://data.openei.org/s3_viewer?bucket=oedi-data-lake&prefix=nrel-pds-building-stock%2Fend-use-load-profiles-for-us-building-stock%2F2023%2Fcomstock_amy2018_release_2%2Fmetadata_and_annual_results%2Fby_state%2Fstate%3DCA%2F
Prototype | CEC Assembly prototype (CBECC 2022.3.1) | https://bees.noresco.com/software2022.html
Codes | Title 24, part 6, referred to as T24 (1984, 1992,1998, 2001, 2005, 2008, 2013, 2016,2019, 2022, 2025) | https://www.energy.ca.gov/publications/2025/2025-building-energy-efficiency-standards-residential-and-nonresidential | 2025
|  | https://codes.iccsafe.org/codes/united-states/california | 2010+
| American Society of Heating, Refrigerating and Air-Conditioning Engineers (ASHRAE) 90.1 (2022) | https://www.ashrae.org/technical-resources/standards-and-guidelines/read-only-versions-of-ashrae-standards
CFR Title 10 (2008, 2010, 2025)
ACM 2022
| T24 2022 - Appendix 5.4A and Appendix 5.4B | https://www.energy.ca.gov/publications/2022/2022-nonresidential-and-multifamily-alternative-calculation-method-reference
Other | 2022 Reduced infiltration CASE report | https://title24stakeholders.com/wp-content/uploads/2020/10/2022-T24-Final-CASE-Report_Reduce-Infiltration.pdf
| 2019 Outdoor Lighting CASE Report | https://title24stakeholders.com/wp-content/uploads/2016/10/T24-2019-CASE-Study-Results-Report-Outdoor-Sources_Final_with-Attachments.pdf
| 2019 High Efficiency Fume Hoods in Laboratory Spaces CASE Report | https://title24stakeholders.com/wp-content/uploads/2017/09/2019-T24-CASE-Report_Fume-Hoods_Final_September-2017.pdf?
| PNNL 20405, 2011 | file:///N:/Prj_SUS/2023/S23668%20SCE%20CA%20Prototypes%20Development/Technical/NR/0_Input%20data/Lighting/PNNL-20405.pdf
| Air leakage Memo, NORESCO, 2025 | Infiltration_rate_report_14May2025-Short-Version.docx
| Yousefi, F., Athalye, R., (2025), "Determining Vintage Bins for Prototype Development: An Analysis of California Commercial Buildings," ASHRAE Annual Conference | https://www.thefreelibrary.com/Determining+Vintage+Bins+for+Prototype+Development%3a+An+Analysis+of...-a0879271125
| ENERGY STAR certified commercial water heaters | https://www.energystar.gov/productfinder/product/certified-commercial-water-heaters/results?fuel_filter=Gas&markets_filter=United+States
| Grainger gas tank water heaters (sizes below commercial, e.g. 30–75 kBtu/h) | https://www.grainger.com/category/plumbing/water-heaters/gas-tank-water-heaters
| Grainger electric tank water heaters | https://www.grainger.com/category/plumbing/water-heaters/electric-tank-water-heaters
Construction Rate
Notes
2025 T24 | Assembly Building is a building with meeting halls in which people gather for civic, social, or recreational activities. These include civic centers, convention centers and auditoriums.

## Prototype
NORESCO, Updated September 2026
Assembly
Characteristic | Value | Data Sources
Building Type | Assembly
Building Category | Nonresidential
Version | v2-0
Vintages | 4 Vintages: Pre-1978, 1978-1997,1998-2007, 2008-2018 New Construction (2019+) | Based on the vintage bin analysis. A summary of the findings is presented in the following paper, with a link provided in the Notes tab: Yousefi, F., Athalye, R. (2025). “Determining Vintage Bins for Prototype Development: An Analysis of California Commercial Buildings.” ASHRAE Annual Conference.
Shape | #VALUE! | The analysis uses prototype geometry originally developed by CEC.
Total Floor Area (ft²) | 315352 | Same as CEC
Aspect Ratio | It varies for different buildings. | Same as CEC
Number of Floors | 1 | Same as CEC
Roof type | Flat | Same as CEC
WWR | 14.5% | Same as CEC
Shading Geometry | No Shades | Same as CEC
Floor to floor height (feet) | Library and Exhibit & Events=13 ft, Religious=50 ft, Sports & Rec and Terminal=25 ft | Same as CEC
Floor to ceiling height (feet) | Library and Exhibit & Events=13 ft, Religious=50 ft, Sports & Rec and Terminal=25 ft | Same as CEC
Glazing sill height (feet) | It varies for different buildings. | Same as CEC
Above grade wall area (ft²) | 415619.76
Gross wall area (ft²) | 415619.76
Roof area (ft²) | 315369.42
Underground Gross Wall Area (ft²) | 0

## Zones
Proposed Layout - Assembly
Building | Space/Thermal Zone | Space Type [Primarily from: T24, 2022 Appendix 5.4A] - See Notes column | HVAC System Name/AHU Name | Schedule Category | Conditioned (Y/N) | Area Fraction | Area (ft²) W/O Multiplier | Area (ft²) | Volume (ft³) | Multipliers | Number of People W/O Multiplier | Number of People | People (Persons/1,000 ft²) [T24, 2025,Table 120.1-A] | Notes
Exhibits and events | Exhibits and events_Conference Room | Convention, Conference, Multipurpose and Meeting Area | AHU-1 | Assembly | Yes | 10.16% | 2669 | 32028 | 416316 | 12 | 88.077 | 1056.924 | 33 |  | 0.033
Exhibits and events | Exhibits and events_Theater Area | Theater Area (Motion Picture) | AHU-1 | Assembly | Yes | 8.467% | 2225 | 26700 | 347172 | 12 | 157.975 | 1895.7 | 71 |  | 0.071
Exhibits and events | Exhibits and events_Auditorium Area | Auditorium Area | AHU-1 | Assembly | Yes | 8.455% | 2222 | 26664 | 346596 | 12 | 157.762 | 1893.144 | 71 |  | 0.071
Exhibits and events | Exhibits and events_Museum Area Exhibition Display | Museum Area (Exhibition/Display) | AHU-1 | Assembly | Yes | 6.762% | 1777 | 21324 | 277140 | 12 | 30.209 | 362.508 | 17 |  | 0.017
Library | Library_Conference Room | Convention, Conference, Multipurpose and Meeting Area | AHU-2 | Assembly | Yes | 0.4122% | 650 | 1300 | 16894 | 2 | 21.45 | 42.9 | 33 |  | 0.033
Library | Library_Reading Area | Library (Reading Area) | AHU-2 | Assembly | Yes | 2.473% | 3899 | 7798 | 101368 | 2 | 38.99 | 77.98 | 10 |  | 0.01
Library | Library_Stacks Area | Library (Stacks Area) | AHU-2 | Assembly | Yes | 4.946% | 7798 | 15596 | 202738 | 2 | 77.98 | 155.96 | 10 |  | 0.01
Library | Library_Lobby Main Entry | Lobby, Main Entry | AHU-2 | Assembly | Yes | 0.4122% | 650 | 1300 | 16894 | 2 | 21.45 | 42.9 | 33 |  | 0.033
religious | Religious_Conference Room | Convention, Conference, Multipurpose and Meeting Area | AHU-3 | Assembly | Yes | 1.966% | 689 | 6201 | 310005 | 9 | 22.737 | 204.633 | 33 |  | 0.033
religious | Religious_General Office | Office Area (>250 square feet) | AHU-3 | Office | Yes | 1.966% | 689 | 6201 | 310005 | 9 | 3.445 | 31.005 | 5 |  | 0.005
religious | Religious_Worship Area | Religious Worship Area | AHU-3 | Assembly | Yes | 15.73% | 5511 | 49599 | 2480040 | 9 | 391.281 | 3521.529 | 71 |  | 0.071
Sports | Sports and recreation_GYM | Exercise/Fitness Center and Gymnasium Areas | AHU-4 | Assembly | Yes | 25.7% | 2795 | 81055 | 2026694 | 29 | 27.95 | 810.55 | 10 |  | 0.01
Sports | Sports and recreation_Locker Room | Locker Room | AHU-4 | Assembly | Yes | 4.81% | 523 | 15167 | 379001 | 29 | 10.46 | 303.34 | 20 |  | 0.02
Sports | Sports and recreation_Restroom | Restrooms | AHU-4 | Assembly | Yes | 1.609% | 175 | 5075 | 126614 | 29 | 1.75 | 50.75 | 10 |  | 0.01
Terminal | Terminals_Concourse | Concourse and Atria Area | AHU-5 | Assembly | Yes | 5.523% | 5806 | 17418 | 435426 | 3 | 98.702 | 296.106 | 17 | Occupancy load is based on T24, 2025, Appendix 5.4A, [For CSV - 2022 SpcFuncData] tab | 0.017
Terminal | Terminals_Baggage | Transportation Function (Baggage Area) | AHU-5 | Assembly | Yes | 0.3054% | 321 | 963 | 24090 | 3 | 10.593 | 31.779 | 33 |  | 0.033
Terminal | Terminals_Ticket | Transportation Function (Ticketing Area) | AHU-5 | Assembly | Yes | 0.3054% | 321 | 963 | 24090 | 3 | 10.593 | 31.779 | 33 |  | 0.033
Total (4 Building) | Total (17 spaces) | Total (15 Space types) | Total ( 5 HVAC Zones) |  | Total (17 Conditioned zones) |  | 38720 | 315352 |  |  | 1171.404 | 10809.487
Background Data [To be deleted prior to publication]
N

## Envelope
Envelope - Assembly
Element | Prototype | Assembly Type | Construction | Thermal properties | Vintage | Selected T24 | Notes | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
External Wall | Assembly | Metal Framed Wall | Metal frame + insulation + Gypsum board | U-value IP | Pre 1978 | N/A | ASHRAE 90.1, 2022 Table A3.1-2, 4", R-0, 135 lb/ft3 Density | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352
[5 empty] | 1978-1997 | 1986 | Similar to High-rise office: Package A/ Heat Capacity was considered ~10 (BTU/F/ft²) | 0.213 | 0.227 | 0.227 | 0.217 | 0.256 | 0.256 | 0.256 | 0.256 | 0.256 | 0.256 | 0.238 | 0.238 | 0.238 | 0.208 | 0.208 | 0.213
[5 empty] | 1998-2007 | 2001 | Table 1-H | 0.182 | 0.182 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.098 | 0.062 | 0.082 | 0.062 | 0.062 | 0.098 | 0.098 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.06 | 0.055 | 0.071 | 0.055 | 0.055 | 0.06 | 0.06 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055
Roof | Assembly | Metal Decking Roof | Built-up Roof roof membrane+roof insulation+metal decking | U-value IP | Pre 1978 | N/A | Considering 30 years for roof/ insulation replacement. | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 1978-1997 | 1992 |  | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 1998-2007 | 2001 | Table 1-H | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.049 | 0.039 | 0.039 | 0.039 | 0.049 | 0.075 | 0.067 | 0.067 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038
Windows | Assembly | Fixed Window | Single pane | U-value IP | Pre 1978 | N/A | ASHRAE Handbook of Fundamentals (Table 4-Ch15) for single pane & T24, 2013 for double pane (33%-67%)* | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108
[5 empty] | 1978-1997 | N/A |  | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108
|  |  | Double pane |  | 1998-2007 | 2001 | Table 1-H | 0.49 | 0.49 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.34 | 0.36 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.36
| Assembly | Fixed Window | Single pane | SHGC | Pre 1978 | N/A | ASHRAE Handbook of Fundamentals (Table 10-Ch15) for single pane & T24, 2013 for double pane (33%-67%)* | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282
[5 empty] | 1978-1997 | N/A |  | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282
|  |  | Double pane |  | 1998-2007 | 2001 | Table 1-H - WWR:31-40% / SHGC non-north | 0.43 | 0.36 | 0.41 | 0.41 | 0.41 | 0.34 | 0.34 | 0.34 | 0.34 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.43
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.22 | 0.25 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.25
Infiltration
|  |  | Building | Zones | Vintage | I_75 6-sdied Inifltration rate @ 75 pa | Note | I-design (cfm/ft²) (4-sided Infiltration rate at normal presure) (Design flow rate approach and Flow/Exterior Wall Area calulation method)
|  | Infiltration | Assembly |  | Pre 1978 | 1.1 | 2022 CASE report (Table 38) | 0.3102
[5 empty] | 1978-1997 | 1.1 | 2022 CASE report (Table 38) | 0.3102
[5 empty] | 1998-2007 | 1.1 | 2022 CASE report (Table 38) | 0.3102
[5 empty] | 2008-2018 | 1 | 2022 CASE report (Table 38) & T24, 2008-2016 (Table 140.3-B)--Air barrier is required in CZ 10-16 | 0.2838
[5 empty] | 2019+ | 0.6 | 2022 CASE report (Table 38) & T24, 2025 (Table 140.3-B)--Air barrier is required in all CZs | 0.1692
Source: T24 air barrier requirements (all editions) and the standardized infiltration rate reported in the 2022 CASE report and Dodge 2023 data
|  |  |  | Air Lekage Memo: |  | Infiltration_rate_report_14May2025-Short-Version.docx

## HVAC System
HVAC system - Assembly
Vintage | Zones | Heating | Cooling | Air Distribution | Source | Note
Exisiting | All Space Types | Hot water heating (Central Gas Boiler) | Cilled water cooling (central Water-Cooled Chiller) | MZ VAV+Hydronic Reheat | Engineering Judgement | System 6 – VAV
New Construction | Library | Hot water heating (AWHP) | Cilled water cooling (central Water-Cooled Chiller) | MZ VAV+Hydronic Reheat | T24 2025 ACM 2025, Table 2 and 3 | System 15 – VAVAWHP
| Exhibit/Sport Arena/Religious building/Terminal | Hot water heating (Central Gas Boiler) | Cilled water cooling (central Water-Cooled Chiller) | MZ VAV+Hydronic Reheat |  | System 6 – VAV
Efficiency of HVAC System (Efficiency is capacity-dependent. The following table provides a general estimate of system efficiency based on preliminary simulations in one climate zone, or assuming cooling load based on rule of thumb)
Vintage | Upgrade/Installed year | Water Cooled Chiller | Gas Boiler | Heat Rejection (Cooling Tower) | Sources | Note
Pre 1978 | 2008 | Water Cooled, Electrically Operated, Centrifugal--≥ 300 tons - 6.10 COP 6.40 IPLV | 82% Ec | Axial fan Open-circuit cooling tower--95°F entering water 85°F leaving water 75°F entering air wb--≥ 38.2 gpm/hp | 2008 Title 20 Appliance Efficiency Regulations, 2005 T24 Standards, Tables 112-A, 112-B
1978-1997
1998-2007
2008-2018 | 2013 | Water Cooled, Electrically Operated, Centrifugal--≥ 600 tons --≤ 0.570 kW/ton (6.2 COP) ≤ 0.539 IPLV (Path A) | 82% Ec | Axial fan Open-circuit cooling tower--95°F entering water 85°F leaving water 75°F entering air wb--≥ 42.1 gpm/hp | 2013 Title 20 Appliance Efficiency Regulations, 2013 T24 Tables 112-A, 112-B
New Construction | 2025 | Water Cooled, Electrically Operated, Centrifugal--≥ 600 tons ≤ 0.560 kW/ton (6.28 COP) ≤ 0.500 IPLV (Path A) | Gas-Fired Boiler > 10,000,000 Btu/h-- 82% Ec | Axial fan Open-circuit cooling tower--95°F entering water 85°F leaving water 75°F entering air wb--≥ 42.1 gpm/hp | Title 20 Appliance Efficiency Regulations, T24, 2025, Tables 110.2-A, 110.2-B
|  | * Et = Combustion efficiency | * Et = Thermal efficiency
Fan power
Vintage | Approach | System | Total Static Pressure (TSP) (in w.c.) | Fan Efficiency [ACM 2025] | Motor Efficiency | Fan Power Index (W/cfm) | Data Source | Note
Existing | PNNL 90.1-2011, TSP | VAV (System 6), > 4,648 cfm | 5.58 | 0.65 | ASHRAE 90.1, 2004, Table 10.8 * |  | Fan power formula: PNNL 20405, 2010, section 5.2.2.5 TSP and fan efficiency: PNNL 20405, 2010, Table 5.11, 90.1-04ac values Motor efficiency: ASHRAE 90.1, 2004, Table 10.8
Brake horsepower (bhp) = (Supply cfm × TSP in w.c.) / (6356 × fan efficiency)
Fan power (w/cfm) = (bhp × 746) / ( supply cfm × motor efficiency )
New Construction | ACM 2025 | PVAVAWHP (System 15), library, >10,000 cfm | TSP = fan power × motor efficiency × fan efficiency × 6356 / 746 | 0.65 | 2025 ACM Table 12 ** | 0.964 | Fan power index: [ACM 2025, Table 13] Motor efficiency: [ACM 2025, Table 12]
|  | VAV (System 6), all other zones, >10,000 cfm | TSP = fan power × motor efficiency × fan efficiency × 6356 / 746 |  |  | 0.946
* According to PNNL 20405 section 5.2.2.5, the full-load efficiency of the motor serving the fan is taken from ASHRAE 90.1, 2004, Table 10.8, based on motor nameplate and assuming enclosed motors operating at 1,800 rotations per minute (rpm) Motor nameplate size (bhp) = brake horsepower (bhp) × 1.1 ( using a 10% oversizing factor)
** The full‑load efficiency of the motor serving the fan is taken from ACM 2025 Table 12 based on the cfm of the fan. Brake horsepower (bhp) = (Supply cfm from sizing run × fan power in W/cfm) / 746. Note: Library is System 15 PVAVAWHP (ACM Table 13 >10,000 cfm = 0.964; 5,000–10,000 cfm = 1.022). Parallel fan-powered box fans, where used, are a separate 0.3 W/cfm. All other zones are System 6 (0.946, same as Hospital).
Background Data [To be deleted prior to publication]

## Thermostat
Thermostat Setpoints - Assembly
Setpoint | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16 | Source
Assembly Heating Setpoint (F) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | T24 2022 - Appendix 5.4B
Assembly Heating Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Assembly Cooling Setpoint (F) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
Assembly Cooling Setback (F) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85

## Ventilation
Outdoor Airflow Rate
Space | Number of People | Floor Area (ft²) | cfm/person [T24, 2025, Equation 120.1-F and Table 120.1-A] | cfm/ft² [T24, 2025, Equation 120.1-F and Table 120.1-A] | Required exhaust rate-CFM/ft²- [T24, 2025, Table 120.1-B – minimum exhaust rates] | Total cfm driven by people | Total cfm driven by area | Total cfm driven by exhaust | Total cfm | Notes
Exhibits and events_Conference Room | 1056.924 | 32028 | 15 | 0.15 |  | 15853.86 | 4804.2 | 0 | 15853.86
Exhibits and events_Theater Area | 1895.7 | 26700 | 15 | 0.15 |  | 28435.5 | 4005 | 0 | 28435.5
Exhibits and events_Auditorium Area | 1893.144 | 26664 | 15 | 0.15 |  | 28397.16 | 3999.6 | 0 | 28397.16
Exhibits and events_Museum Area Exhibition Display | 362.508 | 21324 | 15 | 0.15 |  | 5437.62 | 3198.6 | 0 | 5437.62
Library_Conference Room | 42.9 | 1300 | 15 | 0.15 |  | 643.5 | 195 | 0 | 643.5
Library_Reading Area | 77.98 | 7798 | 15 | 0.15 |  | 1169.7 | 1169.7 | 0 | 1169.7
Library_Stacks Area | 155.96 | 15596 | 15 | 0.15 |  | 2339.4 | 2339.4 | 0 | 2339.4
Library_Lobby Main Entry | 42.9 | 1300 | 15 | 0.15 |  | 643.5 | 195 | 0 | 643.5
Religious_Conference Room | 204.633 | 6201 | 15 | 0.15 |  | 3069.495 | 930.15 | 0 | 3069.495
Religious_General Office | 31.005 | 6201 | 15 | 0.15 |  | 465.075 | 930.15 | 0 | 930.15
Religious_Worship Area | 3521.529 | 49599 | 15 | 0.15 |  | 52822.935 | 7439.85 | 0 | 52822.935
Sports and recreation_GYM | 810.55 | 81055 | 15 | 0.15 |  | 12158.25 | 12158.25 | 0 | 12158.25
Sports and recreation_Locker Room | 303.34 | 15167 | 15 | 0.15 | 0.5 | 4550.1 | 2275.05 | 7583.5 | 7583.5
Sports and recreation_Restroom | 50.75 | 5075 | 0 | 0 | 50 Per Unit or ~0.5 cfm/ft2 | 0 | 0 | 300 | 300 | Restrooms in California per 2025 T24 require mechanical exhaust ventilation, but they do not require additional dedicated outdoor air (OA) beyond that local exhaust. Bathroom exhaust and exhaust fan energy will be captured in the models. We will assume make-up air is drawn from adjacent spaces.
Terminals_Concourse | 296.106 | 17418 | 15 | 0.15 |  | 4441.59 | 2612.7 | 0 | 4441.59
Terminals_Baggage | 31.779 | 963 | 15 | 0.15 |  | 476.685 | 144.45 | 0 | 476.685
Terminals_Ticket | 31.779 | 963 | 15 | 0.15 |  | 476.685 | 144.45 | 0 | 476.685

## Water Heater
Water Heater - Laboratory
Vintage | WH Type | Efficiency | Number of WH | Tank Volume (gal) | Tank Loss | Source
Existing | Gas | 0.8 | 1 | See table below for CZ-specific values: Climate Zone Water Heater Sizing and Loss Coefficients, Storage Volume column (col F) | See table below: Climate Zone Water Heater Sizing and Loss Coefficients, Standby Loss column (col G) | See table below for sources: Climate Zone Water Heater Sizing and Loss Coefficients
New Construction | Gas | 0.8 | 1 | See table below for CZ-specific values: Climate Zone Water Heater Sizing and Loss Coefficients, Storage Volume column (col F) | See table below: Climate Zone Water Heater Sizing and Loss Coefficients, Standby Loss column (col G) | See table below for sources: Climate Zone Water Heater Sizing and Loss Coefficients
Peak Hot Water Consumption
Space Name | Baseline WH Type [CEUS 2022] | Total Area (ft²) | Number of People | Hot Water Usage Specification (gal/hr per person) [T24, 2022, Appendix 5.4A , sheet: "2022 SpaceFuncData-Input"] | Peak Hot Water Usage (gal/hr) | Peak Hot Water Usage (gal/min) | Note
Exhibits and events_Conference Room | Gas | 32028 | 1056.924 | 0.09 | 95.1232 | 1.5854 | For space types marked with an asterisk (the ‘*’ symbol), the water‑heater type is listed as electric in Appendix 5.4A, sheet ‘2022 SpaceFuncData‑Input.’ However, we modified the value based on CEUS data, which indicates that gas is the primary fuel type.
Exhibits and events_Theater Area | Gas | 26700 | 1895.7 | 0.09 | 170.613 | 2.8436
Exhibits and events_Auditorium Area | Gas | 26664 | 1893.144 | 0.09 | 170.383 | 2.8397
Exhibits and events_Museum Area Exhibition Display | Gas | 21324 | 362.508 | 0.09 | 32.6257 | 0.54376
Library_Conference Room | Gas | 1300 | 42.9 | 0.09 | 3.861 | 0.06435
Library_Reading Area | Gas | 7798 | 77.98 | 0.18 | 14.0364 | 0.23394
Library_Stacks Area | Gas | 15596 | 155.96 | 0.18 | 28.0728 | 0.46788
Library_Lobby Main Entry | Gas | 1300 | 42.9 | 0.09 | 3.861 | 0.06435
Religious_Conference Room | Gas | 6201 | 204.633 | 0.09 | 18.417 | 0.30695
Religious_General Office | Gas | 6201 | 31.005 | 0.18 | 5.5809 | 0.093015
Religious_Worship Area | Gas | 49599 | 3521.529 | 0.09 | 316.9376 | 5.2823
Sports and recreation_GYM | Gas | 81055 | 810.55 | 0.18 | 145.899 | 2.4316
Sports and recreation_Locker Room | Gas | 15167 | 303.34 | 0.578 | 175.3305 | 2.9222
Sports and recreation_Restroom | Gas | 5075 | 50.75 | 0 | 0 | 0
Terminals_Concourse | Gas | 17418 | 296.106 | 0.18 | 53.2991 | 0.88832
Terminals_Baggage | Gas | 963 | 31.779 | 0.18 | 5.7202 | 0.095337
Terminals_Ticket | Gas | 963 | 31.779 | 0.18 | 5.7202 | 0.095337
Total | Gas storage |  |  |  | 1245.4806 |  | Minimum peak hot water usage is 75 gal according to ACM 2025
Total | Electric resistance |  |  |  | 0
Number of identical water heaters | 4
Design supply temperature (°F) | 135 | CEC-400-2022-009-CMF-REV2-AP5.4B
WH system factor | 0.6 | 2025 ACM §5.9.2 Rated Capacity
Water mass conversion (lb/gal) | 8.2877 | 2025 ACM §5.9.2 Rated Capacity
Reheat multiplier | 0.4 | 2025 ACM §5.9.2 Storage Volume
Climate Zone Water Heater Sizing and Loss Coefficients
Climate Zone | Minimum Monthly Mains Temp (°F) [T24 2022 - Appendix 5.4B] | Heat Output (Btu/hr) [ACM, 2025, 5.9.2: Rated capacity section] | WH Capacity (Btu/hr) [ACM, 2025, 5.9.2: Rated capacity section] | Required Energy Input (Btu/hr) | Storage Volume (gal) | Standby Loss [Title 20, §1605.1 Table F-4; Appendix B: Water Heating Calculation Method] |  | Off/On Cycle Loss Coefficient to Ambient Temp |  | Source/Note
CZ01 | 47.9 | 224765.2351 | 134859.1411 | 175000 | 125 | 1448.5874 | Btu/hr | 20.6941 | Btu/h·°F | Required Energy Input: vendor/available catalog size (Market data table). Storage Volume: standard/available catalog tank size (Market data table).
CZ02 | 50.8 | 217281.6624 | 130368.9975 | 175000 | 125 | 1448.5874 | Btu/hr | 20.6941 | Btu/h·°F
CZ03 | 52.2 | 213668.9032 | 128201.3419 | 175000 | 125 | 1448.5874 | Btu/hr | 20.6941 | Btu/h·°F
CZ04 | 52.7 | 212378.6321 | 127427.1792 | 160000 | 125 | 1429.8374 | Btu/hr | 20.4262 | Btu/h·°F
CZ05 | 51.6 | 215217.2286 | 129130.3372 | 175000 | 125 | 1448.5874 | Btu/hr | 20.6941 | Btu/h·°F
CZ06 | 56.8 | 201798.4086 | 121079.0452 | 156000 | 125 | 1424.8374 | Btu/hr | 20.3548 | Btu/h·°F
CZ07 | 58.4 | 197669.5409 | 118601.7245 | 150000 | 125 | 1417.3374 | Btu/hr | 20.2477 | Btu/h·°F
CZ08 | 58.4 | 197669.5409 | 118601.7245 | 150000 | 125 | 1417.3374 | Btu/hr | 20.2477 | Btu/h·°F
CZ09 | 57.6 | 199733.9747 | 119840.3848 | 150000 | 125 | 1417.3374 | Btu/hr | 20.2477 | Btu/h·°F
CZ10 | 57.1 | 201024.2459 | 120614.5475 | 156000 | 125 | 1424.8374 | Btu/hr | 20.3548 | Btu/h·°F
CZ11 | 50.5 | 218055.8251 | 130833.4951 | 175000 | 125 | 1448.5874 | Btu/hr | 20.6941 | Btu/h·°F
CZ12 | 51.4 | 215733.3371 | 129440.0022 | 175000 | 125 | 1448.5874 | Btu/hr | 20.6941 | Btu/h·°F
CZ13 | 51.7 | 214959.1744 | 128975.5046 | 175000 | 125 | 1448.5874 | Btu/hr | 20.6941 | Btu/h·°F
CZ14 | 50.1 | 219088.0421 | 131452.8252 | 175000 | 125 | 1448.5874 | Btu/hr | 20.6941 | Btu/h·°F
CZ15 | 63.2 | 185282.9378 | 111169.7627 | 145000 | 125 | 1411.0874 | Btu/hr | 20.1584 | Btu/h·°F
CZ16 | 41.4 | 241538.7601 | 144923.2561 | 199000 | 125 | 1478.5874 | Btu/hr | 21.1227 | Btu/h·°F
Market data
Catalog gas input (Btu/h) | Input source | Elec resistance tank (kW) | Elec resistance (Btu/h) | Catalog gas tank (gal) | Tank source | Elec tank (gal) | Elec tank source | Sources and links → Note tab
60000 | Grainger | 1.5 | 5118 | 34 | ENERGY STAR | 6 | Grainger
75100 | Grainger | 2 | 6824 | 35 | Grainger | 10 | Grainger
76000 | Both | 3 | 10236 | 48 | Grainger | 15 | Grainger
80000 | Grainger | 4.5 | 15355 | 50 | Both | 20 | Grainger
99900 | ENERGY STAR | 6 | 20473 | 55 | ENERGY STAR | 28 | Grainger
100000 | Both | 8 | 27297 | 60 | ENERGY STAR | 30 | Grainger
120000 | ENERGY STAR | 9 | 30709 | 65 | Both | 36 | Grainger
125000 | Both | 10 | 34121 | 72 | Grainger | 40 | Grainger
130000 | Both | 12 | 40946 | 75 | Both | 47
145000 | ENERGY STAR | 12.1 | 41287 | 76 | Grainger | 50
150000 | ENERGY STAR | 18 | 61419 | 80 | Both | 65
156000 | Grainger | 24 | 81891 | 82 | Grainger | 80
160000 | Both | 27 | 92128 | 85 | Grainger | 85
175000 | ENERGY STAR | 36 | 122837 | 90 | Both | 105
180000 | Grainger | 54 | 184256 | 91 | Grainger | 120
199000 | ENERGY STAR |  |  | 100 | Both
199900 | Both |  |  | 110 | ENERGY STAR
200000 | ENERGY STAR |  |  | 119 | Both
250000 | Both |  |  | 125 | ENERGY STAR
251000 | ENERGY STAR
270000 | Grainger
285000 | ENERGY STAR
300000 | Both
320000 | ENERGY STAR
360000 | Grainger
398000 | ENERGY STAR
399000 | ENERGY STAR
399900 | Both
499900 | Grainger
550000 | Grainger
715000 | Grainger

## Interior Lights
Interior Lighting - Assembly
Space Type | New Construction |  |  | Existing
| Lighting density (W/ft²) | Additional lighting power for porTable lighting (W/ft²) | Source | LPD (W/ft²) | Additional LPD for PorTable Lighting (W/ft²) | Source
Convention, Conference, Multipurpose and Meeting Area | 0.75 | 0.25 | T24, 2025, Table 140.6 C (Area category method) | 1.2 |  | T24, 2016, Table 140.6 C (Area category method)
Theater Area (Motion Picture) | 0.5 |  |  | 0.9
Auditorium Area | 0.5 |  |  | 1.4
Museum Area (Exhibition/Display) | 0.6 |  |  | 1.8
Library (Reading Area) | 0.8 |  |  | 1.1
Library (Stacks Area) | 1 |  |  | 1.5
Lobby, Main Entry | 0.7 |  |  | 0.95
Office Area (>250 square feet) | 0.6 | 0.1 |  | 0.75
Religious Worship Area | 0.95 |  |  | 1.5
Exercise/Fitness Center and Gymnasium Areas | 0.5 |  |  | 1
Locker Room | 0.45 |  |  | 0.7
Restrooms | 0.65 |  |  | 0.6
Concourse and Atria Area | 0.6 |  |  | 0.95
Transportation Function (Baggage Area) | 0.4 |  |  | 0.5
Transportation Function (Ticketing Area) | 0.45 |  |  | 1

## Ext Lighting
Exterior Lighting - Assembly
Motion Controlled Luminaires (W) | Non-motion Controlled Luminaires (W) | Total (W) | Source
9861.697 | 1957.325 | 11819.022 | T24, 2022 & 2025 2019 Outdoor Lighting CASE report PNNL 90.1-2010 TSD
Exterior Lighting
Items (Assume LZ2) | Assumptions [2019 Outdoor Lighting CASE Report & PNNL 90.1-2010 TS] |  | Unit | Lighting Power Allowance [T24, 2025, Table 140.7-A & 140.7-B] | Unit | Exterior Lighting Power (W)
IWA (Initial Wattage Allowance) |  |  |  | 200 | (W) | 200
Parking area | 400 ft² for every parking space 1 parking space per 830 ft² of gross building area | 504563 | (ft²) | 0.019 | (W/ft²) | 9586.697
Building Entrance | 5 building entrance per PNNL Model | 5 | (count) | 15 | (W/ea) | 75
Hardscape Ornamental Light | 0.1 ft² per 1 ft² of gross building area for hardscape ornamental light | 31535 | (ft²) | 0.007 | (W/ft²) | 220.745
Building façade | 0.1 W per 1 ft² of facade area Façade Area = Perimeter × 0.5 × max ( height and 30) (30 ft is the max height that is lit) * The 0.5 factor assumes that only half of the perimeter walls are lit. -Formula ia developed based on the 2019 Outdoor Lighting CASE report | 17365.8 | (ft²) | 0.1 | (W/ft²) | 1736.58
Motion Controlled Luminaires (W) | [5 empty] | 9861.697
Non-motion-controlled Luminaires | [5 empty] | 1957.325
Total | [5 empty] | 11819.022
Total floor area | 315352
side each buildings (ft) | 114 | 94.3 | 80.3 | 59.1 | 83
max Height that is lit for each buildings (ft) | 13 | 13 | 25 | 25 | 30
Floors
3
Background Data [To be deleted prior to publication]

## Equipment
Equipment - Assembly
Space Type | Plug load Power Density (W/ft²) | Gas Power Density (Btu/hr-ft²) | Refrigeration Power Density (W/ft²) | Source
Convention, Conference, Multipurpose and Meeting Area | 1 | 0 | 0 | T24 2022 - Appendix 5.4A
Theater Area (Motion Picture) | 0.5 | 0 | 0
Auditorium Area | 1 | 0 | 0
Museum Area (Exhibition/Display) | 1.5 | 0 | 0
Library (Reading Area) | 1.5 | 0 | 0
Library (Stacks Area) | 1.5 | 0 | 0
Lobby, Main Entry | 0.5 | 0 | 0
Office Area (>250 square feet) | 0.7 | 0 | 0 | Plug load and schedules project with CEC, 2025
Religious Worship Area | 0.5 | 0 | 0 | T24 2022 - Appendix 5.4A
Exercise/Fitness Center and Gymnasium Areas | 0.5 | 0 | 0
Locker Room | 0.5 | 0 | 0
Restrooms | 0 | 0 | 0
Concourse and Atria Area | 0.5 | 0 | 0
Transportation Function (Baggage Area) | 0.5 | 0 | 0
Transportation Function (Ticketing Area) | 0.5 | 0 | 0
Background Data [To be deleted prior to publication]

## Schedules
Schedules - Assembly
Zone | Schedule Category | Schedule | Source | Type | Hour
[5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
All the Zones except Office | Assembly | Occupancy | T24 2022 - Appendix 5.4B, [Assembly] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0.2 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0.2 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.8 | 0.1 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.2 | 0
All the Zones except Office and Storage | Assembly | Lights | T24 2022 - Appendix 5.4B, [Assembly] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.35 | 0.35 | 0.35 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.25 | 0.05
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.05
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.05 | 0.05
All the Zones except Office | Assembly | ElecEquipment | T24 2022 - Appendix 5.4B, [Assembly] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.4 | 0.4 | 0.4 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.25 | 0.05
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.05
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.05 | 0.05
All the Zones except Office | Assembly | ServiceHotWater | T24 2022 - Appendix 5.4B, [Assembly] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.35 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65 | 0.3 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65 | 0.3 | 0 | 0 | 0
All the Zones except Office | Assembly | GasEquipment | T24 2022 - Appendix 5.4B, [Assembly] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.3 | 0.2 | 0.9 | 0.9 | 0.9 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5 | 0.1 | 0.1 | 0.1 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.3 | 0.2 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0.1 | 0.1 | 0.3 | 0.8 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5 | 0.1 | 0.1 | 0.1 | 0 | 0
All the Zones except Office | Assembly | Refrigeration | T24 2022 - Appendix 5.4B, [Assembly] | Weekday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Saturday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Sunday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
All the Zones except Office | Assembly | HVACAvail | T24 2022 - Appendix 5.4B, [Assembly] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0
All the Zones except Office | Assembly | Infiltration | T24 2022 - Appendix 5.4B, [Assembly] | Weekday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1
|  |  |  | Saturday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1
|  |  |  | Sunday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1
All the Zones except Office | Assembly | HtgSetpt | T24 2022 - Appendix 5.4B, [Assembly] | Weekday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 60
|  |  |  | Saturday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 60
|  |  |  | Sunday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 60
All the Zones except Office | Assembly | ClgSetpt | T24 2022 - Appendix 5.4B, [Assembly] | Weekday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 85
|  |  |  | Saturday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 85
|  |  |  | Sunday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 85
Office |  | Other
Office | Office | Occupancy | T24 2022 - Appendix 5.4B, [Office] Updated base on Plug load and schedules project with CEC, 2025 | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
Office | Office | Lights | T24 2022 - Appendix 5.4B, [Office] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.35 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Office | Office | ElecEquipment | Plug load and schedules project with CEC, 2025 | Weekday | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.74 | 0.87 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.5 | 0.45 | 0.45 | 0.45
|  |  |  | Saturday | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43
|  |  |  | Sunday | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43
Office | Office | HVACAvail | T24 2022 - Appendix 5.4B, [Office] Updated base on Plug load and schedules project with CEC, 202 | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Office | Office | ServiceHotWater | T24 2022 - Appendix 5.4B, [Office] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.12 | 0.14 | 0.07 | 0.07 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05
|  |  |  | Sunday | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04
Office | Office | Infiltration | T24 2022 - Appendix 5.4B, [Office] Updated base on Plug load and schedules project with CEC, 202 | Weekday | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
Office | Office | HtgSetpt | Honeywell-INNCOM e7 Thermostat User Guide & Engineering Judgement | Weekday | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
|  |  |  | Saturday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  |  | Sunday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Office | Office | ClgSetpt | Honeywell-INNCOM e7 Thermostat User Guide & Engineering Judgement | Weekday | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
|  |  |  | Saturday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
|  |  |  | Sunday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
Other
| Building | Elevator | T24 2022 - Appendix 5.4B, [Assembly] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0.22 | 0.64 | 0.74 | 0.68 | 0.68 | 0.71 | 0.72 | 0.72 | 0.73 | 0.68 | 0.68 | 0.58 | 0.54 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.21 | 0.56 | 0.66 | 0.68 | 0.68 | 0.69 | 0.7 | 0.69 | 0.66 | 0.58 | 0.47 | 0.43 | 0.43 | 0.08 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.13 | 0.35 | 0.37 | 0.37 | 0.39 | 0.41 | 0.38 | 0.34 | 0.03 | 0 | 0 | 0 | 0
| Building | ExtLightingNonMotionCtrl |  | Weekday | bar: Hour 1 to Hour 24
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
| Building | ExtLightingMotionCtrl |  | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
Restroom, Museum, and Terminals | Building | CommonAreaPeopleActivityLevel | CEC Assembly Prototype | Weekday | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147
|  |  |  | Saturday | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147
|  |  |  | Sunday | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147
Locker Room | Building | LockerRoomPeopleActivityLevel | CEC Assembly Prototype | Weekday | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9
|  |  |  | Saturday | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9
|  |  |  | Sunday | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9
Gym | Building | GymPeopleActivityLevel | CEC Assembly Prototype | Weekday | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2
|  |  |  | Saturday | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2
|  |  |  | Sunday | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2
Library, Office | Building | FunctionalAreaPeopleActivityLevel | CEC Assembly Prototype | Weekday | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
|  |  |  | Saturday | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
|  |  |  | Sunday | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
Conference | Building | MeetingAreaPeopleActivityLevel | CEC Assembly Prototype | Weekday | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2
|  |  |  | Saturday | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2
|  |  |  | Sunday | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2
Theater, Worship, Auditorium | Building | PerformanceSpcPeopleActivityLevel | CEC Assembly Prototype | Weekday | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6
|  |  |  | Saturday | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6
|  |  |  | Sunday | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6

## Energy Usage (hidden)
CalBEM Energy Consumption - Assembly | [11 empty] | Energy Consumption - Assembly
Prototype | CZ | CalBEM Electricity EUI (KBTU/ft²) | CalBEM Gas EUI (KBTU/ft²) | CalBEM Total EUI (KBTU/ft²) | New Construction Electricity EUI (KBTU/ft²) | New Construction Gas EUI (KBTU/ft²) | New Construction Total EUI (KBTU/ft²) | National Average | Acceptable Range (25% Higher) | Acceptable Range (25% Lower) | National Average Acceptable EUI Range | Prototype | CZ | Total Floorspace (Thousand of ft²) | CEUS 2023 Electricity EUI (kBtu/ft²) | CEUS 2023 Gas EUI (kBtu/ft²) | CEUS 2023 Total EUI (kBtu/ft²) | Acceptable Range (25% Higher) | Acceptable Range (25% Lower) | CEUS 2022 Acceptable EUI Range
Assembly | 1 | [6 empty] | 63.5 | 79.375 | 47.625 | 31.75 | Assembly | 1
| 2 | [6 empty] | 63.5 | 79.375 | 47.625 | 31.75 |  | 2
| 3 | [6 empty] | 63.5 | 79.375 | 47.625 | 31.75 |  | 3
| 4 | [6 empty] | 63.5 | 79.375 | 47.625 | 31.75 |  | 4
| 5 | [6 empty] | 63.5 | 79.375 | 47.625 | 31.75 |  | 5
| 6 | [6 empty] | 63.5 | 79.375 | 47.625 | 31.75 |  | 6
| 7 | [6 empty] | 63.5 | 79.375 | 47.625 | 31.75 |  | 7
| 8 | [6 empty] | 63.5 | 79.375 | 47.625 | 31.75 |  | 8
| 9 | [6 empty] | 63.5 | 79.375 | 47.625 | 31.75 |  | 9
| 10 | [6 empty] | 63.5 | 79.375 | 47.625 | 31.75 |  | 10
| 11 | [6 empty] | 63.5 | 79.375 | 47.625 | 31.75 |  | 11
| 12 | [6 empty] | 63.5 | 79.375 | 47.625 | 31.75 |  | 12
| 13 | [6 empty] | 63.5 | 79.375 | 47.625 | 31.75 |  | 13
| 14 | [6 empty] | 63.5 | 79.375 | 47.625 | 31.75 |  | 14
| 15 | [6 empty] | 63.5 | 79.375 | 47.625 | 31.75 |  | 15
| 16 | [6 empty] | 63.5 | 79.375 | 47.625 | 31.75 |  | 16
Ref: CEUS 2022 Report
And converted FZ level data to CZ level

## Weights (hidden)
% of Floor Area per CZ and Vintage Bin - Assembly | [7 empty] | % of Floor Area per CZ and Vintage Bin - Assembly
Prototype | CZ | Vintage Bin | [5 empty] | Prototype | Vintage Bin | CZ
|  | Pre-1978 | 1978-1997 | 1998-2007 | 2008-2018 | Not available |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
Assembly | 1 | [5 empty] | 0% | Assembly | Pre-1978 | [16 empty] | 0%
| 2 | [5 empty] | 0% |  | 1978-1997 | [16 empty] | 0%
| 3 | [5 empty] | 0% |  | 1998-2007 | [16 empty] | 0%
| 4 | [5 empty] | 0% |  | 2008-2018 | [16 empty] | 0%
| 5 | [5 empty] | 0% |  | Not available | [16 empty] | 0%
| 6 | [5 empty] | 0% |  | Total
| 7 | [5 empty] | 0%
| 8 | [5 empty] | 0%
| 9 | [5 empty] | 0%
| 10 | [5 empty] | 0%
| 11 | [5 empty] | 0%
| 12 | [5 empty] | 0%
| 13 | [5 empty] | 0%
| 14 | [5 empty] | 0%
| 15 | [5 empty] | 0%
| 16 | [5 empty] | 0%
Statewide
Ref: CEUS 2022 dataset

## PV (hidden)
PV - Assembly
TBD

## EV Charger (hidden)
EV Charger - Assembly
TBD
Background Data [To be deleted prior to publication]

## Data (hidden)
Space Function | Electric Equipment Load Intensity | Electric Equipment Load Intensity | LPD
Aging Eye/Low-vision (Corridor Area) |  |  | 2013 | 2016 | 2019 | 2025
Aging Eye/Low-vision (Dining)
Aging Eye/Low-vision (Lobby, Main Entry)
Aging Eye/Low-vision (Lounge/Waiting Area)
Aging Eye/Low-vision (Multipurpose Room)
Aging Eye/Low-vision (Religious Worship Area)
Aging Eye/Low-vision (Restroom)
Aging Eye/Low-vision (Stairwell)
Audience Seating Area
Auditorium Area
Auto Repair / Maintenance Area
Barber, Beauty Salon, Spa Area
Civic Meeting Place Area
Classroom, Lecture, Training, Vocational Areas
Concourse and Atria Area
Convention, Conference, Multipurpose and Meeting Area
Copy Room
Corridor Area
Dining Area (Bar/Lounge and Fine Dining)
Dining Area (Cafeteria/Fast Food)
Dining Area (Family and Leisure)
Electrical, Mechanical, Telephone Rooms
Exercise/Fitness Center and Gymnasium Areas
Financial Transaction Area
Healthcare Facility and Hospitals (Exam/Treatment Room)
Healthcare Facility and Hospitals (Imaging Room)
Healthcare Facility and Hospitals (Medical Supply Room)
Healthcare Facility and Hospitals (Nursery)
Healthcare Facility and Hospitals (Nurse's Station)
Healthcare Facility and Hospitals (Operating Room)
Healthcare Facility and Hospitals (Patient Room)
Healthcare Facility and Hospitals (Physical Therapy Room)
Healthcare Facility and Hospitals (Recovery Room)
Hotel Function Area
Kitchen/Food Preparation Area
Kitchenette or Residential Kitchen
Laboratory, Scientific
Laundry Area
Library (Reading Area)
Library (Stacks Area)
Lobby, Main Entry
Locker Room
Lounge, Breakroom, or Waiting Area
Manufacturing, Commercial & Industrial Work Area (Low Bay)
Manufacturing, Commercial & Industrial Work Area (High Bay)
Manufacturing, Commercial & Industrial Work Area (Precision)
Museum Area (Exhibition/Display)
Museum Area (Restoration Room)
Office Area (>250 square feet)
Office Area (<250 square feet)
Parking Garage Area (Parking Zone and Ramps)
Parking Garage Area (Daylight Adaptation Zones)
Pharmacy Area
Retail Sales Area (Grocery Sales)
Retail Sales Area (Retail Merchandise Sales)
Retail Sales Area (Fitting Room)
Religious Worship Area
Restrooms
Stairwell
Storage, Commercial/Industrial (Warehouse)
Storage, Commercial/Industrial (Refrigerated)
Storage, Commercial/Industrial (Shipping & Handling)
Storage (General)
Sports Arena - Playing Area (> 5,000 Spectators)
Sports Arena - Playing Area (2,000 - 5,000 Spectators)
Sports Arena - Playing Area (< 2,000 Spectators)
Sports Arena - Playing Area (Recreational)
Theater Area (Motion Picture)
Theater Area (Performance)
Transportation Function (Baggage Area)
Transportation Function (Ticketing Area)
Videoconferencing Studio
High-Rise Residential Living Spaces
Hotel/Motel Guest Room
All other
Attic
Reception Area
Elevator
Plenum
IT Room (EPD 12)
Computer Room (EPD 20)
Server Room (EPD 45)