## Notes
Data Sources
Dataset | Dodge 2023
| Commercial End-Use Survey (CEUS) 2022 | https://www.energy.ca.gov/publications/2023/2022-california-commercial-end-use-survey-ceus-final-report
| Commercial Buildings Energy Consumption Survey (CBECS) 2018 | https://www.eia.gov/consumption/commercial/data/2018/
| ComStock 2023 | https://comstock.nlr.gov/page/datasets
ACM | California Energy Commission (CEC) Large Office prototype (CBECC 2022.3.1) | https://bees.noresco.com/software2022.html
| Pacific Northwest National Laboratory (PNNL) Large Office prototype (90.1-2022) | https://www.energycodes.gov/prototype-building-models#Commercial
| Database for Energy Efficient Resources (DEER) Large prototype (June 2023) | https://github.com/sound-data/DEER-Prototypes-EnergyPlus
| Oak Ridge National Laboratory (ORNL) 2019 Large Office prototype zoning | https://www.sciencedirect.com/science/article/abs/pii/S0306261920312186
https://publications.ibpsa.org/proceedings/simbuild/2020/papers/simbuild2020_C064.pdf
| Massachusetts Large Office prototype | https://www.mass.gov/doc/large-office-prototype-basis-of-design-report/download
Codes | Title 24, part 6, referred to as T24 (1984, 2001, 2008, 2010, 2013, 2022, 2025) | https://www.energy.ca.gov/publications/2025/2025-building-energy-efficiency-standards-residential-and-nonresidential |  |  | 2025
|  | https://codes.iccsafe.org/codes/united-states/california |  |  | 2010+
| American Society of Heating, Refrigerating and Air-Conditioning Engineers (ASHRAE) 90.1 (2022) | https://www.ashrae.org/technical-resources/standards-and-guidelines/read-only-versions-of-ashrae-standards
| Code of Federal Regulations (CFR) Title 10 (2010) | https://www.govinfo.gov/content/pkg/FR-2009-03-23/pdf/FR-2009-03-23.pdf
| CFR Title 10 (2024) | https://www.govinfo.gov/content/pkg/CFR-2024-title10-vol3/pdf/CFR-2024-title10-vol3-part431-subpartF.pdf
| Title 20 | https://govt.westlaw.com/calregs/Document/I270DCA634B4011EFA8F7F119BAF97AD6?viewType=FullText&originationContext=documenttoc&transitionType=CategoryPageItem&contextData=(sc.Default)
Others | Alternative Calculation Method (ACM) (2022) | https://www.energy.ca.gov/publications/2022/2022-nonresidential-and-multifamily-alternative-calculation-method-reference
| ACM (2025) | https://www.energy.ca.gov/publications/2025/2025-nonresidential-and-multifamily-alternative-calculation-method-reference
| Nonres ACM 2022, Appendix 5.4A and Appendix 5.4B | https://www.energy.ca.gov/publications/2022/2022-nonresidential-and-multifamily-alternative-calculation-method-reference
| 2022 Reduced infiltration Codes and Standards Enhancement (CASE) report | https://title24stakeholders.com/wp-content/uploads/2020/10/2022-T24-Final-CASE-Report_Reduce-Infiltration.pdf
| 2019 Outdoor Lighting CASE Report | https://title24stakeholders.com/wp-content/uploads/2016/10/T24-2019-CASE-Study-Results-Report-Outdoor-Sources_Final_with-Attachments.pdf
| PNNL 20405, 2011 | https://www.pnnl.gov/main/publications/external/technical_reports/PNNL-20405.pdf
| Air leakage Memo, NORESCO, 2025 | Infiltration_rate_report_14May2025-Short-Version.docx
| Yousefi, F., Athalye, R., (2025), "Determining Vintage Bins for Prototype Development: An Analysis of California Commercial Buildings," ASHRAE Annual Conference | https://www.thefreelibrary.com/Determining+Vintage+Bins+for+Prototype+Development%3a+An+Analysis+of...-a0879271125
| Proposed Updates to Equipment Power Densities and Building Schedules for the 2028 Energy Code, referred to as "Plug load and schedules project with CEC, 2025" (Docket Number =25-BSTD-03 & TN=265693) | https://efiling.energy.ca.gov/GetDocument.aspx?tn=265693&DocumentContentId=102545
| Yousefi, F., Athalye, R. (2026). "Developing a New Set of Prototypical Models for Office Buildings in California," IBPSA-USA Conference | https://publications.ibpsa.org/conference/paper/?id=simbuild2026_1372
| ENERGY STAR certified commercial water heaters | https://www.energystar.gov/productfinder/product/certified-commercial-water-heaters/results?fuel_filter=Gas&markets_filter=United+States
| Grainger gas tank water heaters (sizes below commercial, e.g. 30–75 kBtu/h) | https://www.grainger.com/category/plumbing/water-heaters/gas-tank-water-heaters
| Grainger electric tank water heaters | https://www.grainger.com/category/plumbing/water-heaters/electric-tank-water-heaters
Construction Rate
Total Floor area (thousands of sf)
[6 empty] | Pre-1978 | 1978-1997 | 1998-2007 | 2008-2018 | 2019-2022
[6 empty] | New Construction (2019+) | 248465.9 | 93016.2 | 62305.7 | 27851.1
Source: Dodge Construction Data, 2023 ( NEW large office built after 1967) (STC refers to building types in Dodge terminology).
Notes
OfficeLarge Prototype | Information about the geometry and underlying logic of the office prototypes can be found in this paper: Yousefi, F., Athalye, R. (2026). ‘Developing a New Set of Prototypical Models for Office Buildings in California.’ IBPSA-USA Conference. The link is provided above in the Data Source section. The floor area was slightly modified in some spaces during the geometry‑drawing phase. Footprint (floor area of each story): Supported by Dodge 2023 data and consistent with the existing Large Office prototypes Zone configuration and floor plan layout: Based on the ORNL 2019 project, with modifications informed by engineering and architectural judgment (see the "Zones" tab for more details)
Large office building is defined as any office building with a total area >150,000 sf, by analyzing Dodge 2023 data.
Large office buildings cover approximately 52% of the floor area and 7% of the total number of the CA office buildings (according to the Dodge 2023 datasets).
Only 2% of offices in CA have stories >6 and area <150,000. (according to the Dodge 2023 datasets)
Analysis of the Dodge 2023 dataset (see table and chart below) shows that the median and average number of stories and total floor area (not footprint of each story) are considerably smaller than those represented in the existing prototypes developed by PNNL and CBECC. This suggests that a smaller prototype might better reflect the California building stock. However, we have chosen to continue using the existing prototype floor area and number of stories for the following reasons: '- Developing a smaller prototype would make the CEC prototype different from national Large Office prototype. '- Change would likely have little impact on energy consumption on a per sf basis (kBTU/sf), nor would it result in different HVAC system design .
| Statical Analysis of the CA Large Office Building Stock (STC:7,305,405 & floor area>150 ksf) | No. of Stories | Footprint (sf) | Total Area (sf)
| Median | 6 | 40000 | 250000
| Average | 9 | 35555 | 320000
Source: Dodge 2023 data ( NEW large office buildings built after 1967)
| Existing Large Office Prototype | No. of Stories | Footprint* (sf) | Total Area (sf)
| CBECC (CEC) 2022 | 13 | 38400 | 498000
| PNNL ASHRAE 90.1 2022 | 13 | 38400 | 498000
| DEER (CPUC) 2024 | 10 | 17500 | 175000
Source: Dodge 2023 data ( NEW large office buildings built after 1967)

## Prototype
NORESCO, Updated September 2026
OfficeLarge
Characteristic | Value | Data Sources
Building Type | Large Office
Building Category | Nonresidential
Version | v2-0
Vintages | 4 Vintages: Pre-1978 , 1978-1997 ,1998-2007 , 2008-2018 New Construction (2019+) | Based on the vintage bin analysis. A summary of the findings is presented in the following paper, with a link provided in the Notes tab: Yousefi, F., Athalye, R. (2025). “Determining Vintage Bins for Prototype Development: An Analysis of California Commercial Buildings.” ASHRAE Annual Conference.
Shape |  | Assume number of floors based on the existing Large Office prototypes (PNNL, CEC) Assume rectangular shape; supported by CBECS, CEC, and PNNL The logic behind the geometry of the CalBEM Office prototypes' shell is described in the following paper, with a link provided in the Notes tab: Yousefi, F., & Athalye, R. (2026). "Developing a New Set of Prototypical Models for Office Buildings in California", IBPSA-USA Conference.
Total Floor Area (ft2) | 498,589 (240 ft *160 ft) | Supported by Dodge 2023 data (Same as CEC and PNNL)
Aspect Ratio | 1.5 | Assumption; same as CEC and PNNL Large Office prototype
Number of Floors | 12 Floor + basement | Number of floors: based on the existing Large Office prototypes (PNNL,CEC)
Roof type | Flat | Supported by CBECS 2018 data (Same as CEC and PNNL)
WWR | 40% of the above grade wall
Window dimensions | Even distribution
Shading Geometry | None
Floor to floor height (feet) | 13 | Assumption, standard ceiling height in office buildings; same as CEC and PNNL Large Office prototype.
Floor to ceiling height (feet) | 9 | Assumption; same as CEC and PNNL Large Office prototype
Glazing sill height (feet) | 3 | Assumption; same as CEC and PNNL Large Office prototype

## Zones
Proposed Layout - OfficeLarge
Building | Space/ Thermal Zone | Space Type [Primarily from: T24, 2022 Appendix 5.4A] - See Notes column | HVAC System Name New Construction | HVAC System Name Vintage 1-4 | Schedule Category | Conditioned (Y/N) | Area Fraction | Area (ft²) | Volume (ft³) | Multipliers | Number of People | People (Persons/1,000 ft²) [T24, 2025,Table 120.1-A] | Notes | Total area fraction | Thermal Zone Layout - Each space has its own thermal zone
OfficeLarge | Perimeter_Open_Office_N_Basement | Office Area (>250 square feet) | VAV With Reheat_Basement | VAV_Basement | Office | Yes | 1.688% | 8416.86 | 75751.74 | 1 | 42.0843 | 5 |  | 1.688%
OfficeLarge | Perimeter_Open_Office_S_Basement | Office Area (>250 square feet) | VAV With Reheat_Basement | VAV_Basement | Office | Yes | 0.7345% | 3662.18 | 32959.62 | 1 | 18.3109 | 5 |  | 0.7345% |  | Basement |  |  | First Floor |  |  | Middle/Top Floors
OfficeLarge | Core_Enclosed_Office_Basement | Office Area (>250 square feet) | VAV With Reheat_Basement | VAV_Basement | Office | Yes | 0.7429% | 3703.68 | 33333.12 | 1 | 18.5184 | 5 |  | 0.7429%
OfficeLarge | Server_Room_Basement | Server Room (EPD 45) | CRAH_ServerRoom_Basement | CAV HW Rht | Data | Yes | 1.65% | 8228 | 74052 | 1 | 41.14 | 5 | New space type defined for this prototype. | 1.65%
OfficeLarge | Mech/Elec_Basement | Electrical, Mechanical, Telephone Rooms | VAV With Reheat_Basement | VAV_Basement | Ancillary | Yes | 1.596% | 7958 | 71622 | 1 | 0 | 0 |  | 1.596%
OfficeLarge | Conference_Basement | Convention, Conference, Multipurpose and Meeting Area | VAV With Reheat_Basement | VAV_Basement | Office | Yes | 0.1163% | 579.7 | 5217.3 | 1 | 19.1301 | 33 |  | 0.1163%
OfficeLarge | BreakRoom/FoodPrep_Basement | Lounge, Breakroom, or Waiting Area | VAV With Reheat_Basement | VAV_Basement | Office | Yes | 0.1952% | 973 | 8757 | 1 | 32.109 | 33 |  | 0.1952%
OfficeLarge | Storage_Basement | Storage (General) | VAV With Reheat_Basement | VAV_Basement | Ancillary | Yes | 0.2469% | 1231 | 11079 | 1 | 0 | 0 | Occupant load density for storage is based on Title 24, 2025, Appendix 5.4A. | 0.2469%
OfficeLarge | Restroom_Basement | Restrooms | VAV With Reheat_Basement | VAV_Basement | Office | Yes | 0.1978% | 986 | 8874 | 1 | 0 | 0 |  | 0.1978%
OfficeLarge | Lobby/Lounge_Basement | Lounge, Breakroom, or Waiting Area | VAV With Reheat_Basement | VAV_Basement | Office | Yes | 0.1418% | 707 | 6363 | 1 | 10.605 | 15 | Increased the ASHRAE 62.1 number of people (10) since this area is more of a lounge/lobby space and not main entry lobby. Number of People: 10 according to ASHRAE 62.1 Table 6-1 for main entry lobbies T24: 33 for main Entry lobbies & 5 for reception area | 0.1418%
OfficeLarge | Stair/Elevator_Basement | Stairwell | VAV With Reheat_Basement | VAV_Basement | Ancillary | Yes | 0.1887% | 941 | 8469 | 1 | 0 | 0 |  | 0.1887%
OfficeLarge | Corridor_W_Basement | Corridor Area | VAV With Reheat_Basement | VAV_Basement | Office | Yes | 0.141% | 703 | 6327 | 1 | 3.515 | 5 |  | 0.141%
OfficeLarge | Corridor_E_Basement | Corridor Area | VAV With Reheat_Basement | VAV_Basement | Office | Yes | 0.05273% | 262.9 | 2366.1 | 1 | 1.3145 | 5 |  | 0.05273%
OfficeLarge | Perimeter_Open_Office_N_FloorG | Office Area (>250 square feet) | VAV With Reheat_FloorG | AHU VAV_FloorG | Office | Yes | 1.43% | 7131.29 | 64181.61 | 1 | 35.6564 | 5 |  | 1.43%
OfficeLarge | Perimeter_Open_Office_W_FloorG | Office Area (>250 square feet) | VAV With Reheat_FloorG | AHU VAV_FloorG | Office | Yes | 1.162% | 5795.77 | 52161.93 | 1 | 28.9789 | 5 |  | 1.162%
OfficeLarge | Perimeter_Open_Office_E_FloorG | Office Area (>250 square feet) | VAV With Reheat_FloorG | AHU VAV_FloorG | Office | Yes | 1.178% | 5875.49 | 52879.41 | 1 | 29.3774 | 5 |  | 1.178%
OfficeLarge | Perimeter_Enclosed_Office_NE_FloorG | Office Area (>250 square feet) | VAV With Reheat_FloorG | AHU VAV_FloorG | Office | Yes | 0.184% | 917.38 | 8256.42 | 1 | 4.5869 | 5 |  | 0.184%
OfficeLarge | Perimeter_Enclosed_Office_NW_FloorG | Office Area (>250 square feet) | VAV With Reheat_FloorG | AHU VAV_FloorG | Office | Yes | 0.2269% | 1131.21 | 10180.89 | 1 | 5.6561 | 5 |  | 0.2269% | Basement |  |  |  | First Floor |  |  |  | Middle/Top Floors
OfficeLarge | Core_Enclosed_Office_FloorG | Office Area (>250 square feet) | VAV With Reheat_FloorG | AHU VAV_FloorG | Office | Yes | 0.6644% | 3312.28 | 29810.52 | 1 | 16.5614 | 5 |  | 0.6644% | Area Distribution By Space Type |  |  |  | Area Distribution By Space Type |  |  |  | Area Distribution By Space Type
OfficeLarge | Server_Room_FloorG | Computer Room (EPD 20) | CRAC DX Clg_FloorG | PTAC DX Clg Elec Htg 1 | Data | Yes | 0.08366% | 417.09 | 3753.81 | 1 | 0.62563 | 1.5 | New space type defined for this prototype. | 0.08366% | Space Type | Area (ft2)​ | % of footprint |  | Space Type | Area (ft2)​ | % of footprint |  | Space Type | Area (ft2)​ | % of footprint
OfficeLarge | Mech/Elec_FloorG | Electrical, Mechanical, Telephone Rooms | VAV With Reheat_FloorG | AHU VAV_FloorG | Ancillary | Yes | 0.1703% | 848.96 | 7640.64 | 1 | 0 | 0 |  | 0.1703% | Open office​ | 12079.04 | 31.49% |  | Open office​ | 18802.55 | 49.02% |  | Open office​ | 21287.86 | 55.51%
OfficeLarge | Conference_FloorG | Convention, Conference, Multipurpose and Meeting Area | VAV With Reheat_FloorG | AHU VAV_FloorG | Office | Yes | 0.1584% | 789.81 | 7108.29 | 1 | 26.0637 | 33 |  | 0.1584% | Core Enclosed Office​ | 3703.68 | 9.657% |  | Core Enclosed Office​ | 3312.28 | 8.636% |  | Core Enclosed Office​ | 3233 | 8.43%
OfficeLarge | BreakRoom_FloorG | Lounge, Breakroom, or Waiting Area | VAV With Reheat_FloorG | AHU VAV_FloorG | Office | Yes | 0.124% | 618.23 | 5564.07 | 1 | 20.4016 | 33 |  | 0.124% | Perimeter Enclosed Office​ | _ | _ |  | Perimeter Enclosed Office​ | 2048.59 | 5.341% |  | Perimeter Enclosed Office​ | 4092.56 | 10.67%
OfficeLarge | FoodPrep_FloorG | Kitchen/Food Preparation Area | VAV With Reheat_FloorG | AHU VAV_FloorG | Office | Yes | 0.1879% | 936.94 | 8432.46 | 1 | 2.8108 | 3 |  | 0.1879% | Conference​ | 579.7 | 1.511% |  | Conference​ | 789.81 | 2.059% |  | Conference​ | 2323.24 | 6.058%
OfficeLarge | Storage_FloorG | Storage (General) | VAV With Reheat_FloorG | AHU VAV_FloorG | Ancillary | Yes | 0.1924% | 959.03 | 8631.27 | 1 | 0 | 0 | Occupant load density for storage is based on Title 24, 2025, Appendix 5.4A. | 0.1924% | Break + Food prep​ | 973 | 2.537% |  | Break + Food prep​ | 1555.17 | 4.055% |  | Break + Food prep​ | 910 | 2.373%
OfficeLarge | Locker_FloorG | Locker Room | VAV With Reheat_FloorG | AHU VAV_FloorG | Office | Yes | 0.3541% | 1765.23 | 15887.07 | 1 | 17.6523 | 10 | Based on 2022 CEC AP5 | 0.3541% | Storage​ | 1231 | 3.21% |  | Storage​+locker | 2724.26 | 7.103% |  | Storage​ | 738 | 1.924%
OfficeLarge | Lobby_S_FloorG | Lobby, Main Entry | VAV With Reheat_FloorG | AHU VAV_FloorG | Office | Yes | 0.6741% | 3360.63 | 30245.67 | 1 | 33.6063 | 10 | According to ASHRAE 62.1 Table 6-1 for main entry lobbies | 0.6741% | Mech/Elec​ | 7958 | 20.75% |  | Mech/Elec​ | 848.96 | 2.214% |  | Mech/Elec​ | 1070 | 2.79%
OfficeLarge | Lobby/Lounge_FloorG | Lounge, Breakroom, or Waiting Area | VAV With Reheat_FloorG | AHU VAV_FloorG | Office | Yes | 0.1372% | 683.9 | 6155.1 | 1 | 10.2585 | 15 | Increased the ASHRAE 62.1 number of people (10) since this area is more of a lounge/lobby space and not main entry lobby. | 0.1372% | Server Room​ | 8228 | 21.45% |  | Server Room​ | 417.09 | 1.088% |  | Server Room​ | 418 | 1.09%
OfficeLarge | Restroom_FloorG | Restrooms | VAV With Reheat_FloorG | AHU VAV_FloorG | Office | Yes | 0.2319% | 1156.09 | 10404.81 | 1 | 0 | 0 |  | 0.2319% | Corridor​ | 965.9 | 2.518% |  | Corridor​ | 1804.63 | 4.705% |  | Corridor​ | 1591.24 | 4.149%
OfficeLarge | Stair/Elevator_FloorG | Stairwell | VAV With Reheat_FloorG | AHU VAV_FloorG | Ancillary | Yes | 0.1701% | 848.01 | 7632.09 | 1 | 0 | 0 |  | 0.1701% | Restroom​ | 986 | 2.571% |  | Restroom​ | 1156.09 | 3.014% |  | Restroom​ | 1155 | 3.011%
OfficeLarge | Corridor_W_FloorG | Corridor Area | VAV With Reheat_FloorG | AHU VAV_FloorG | Office | Yes | 0.2018% | 1005.87 | 9052.83 | 1 | 5.0293 | 5 |  | 0.2018% | Lobby​/Lounge | 707 | 1.843% |  | Lobby​/Lounge | 4044.53 | 10.55% |  | Lobby​/Lounge | 684 | 1.783%
OfficeLarge | Corridor_E_FloorG | Corridor Area | VAV With Reheat_FloorG | AHU VAV_FloorG | Office | Yes | 0.1602% | 798.76 | 7188.84 | 1 | 3.9938 | 5 |  | 0.1602% | Stair/Elevator​ | 941 | 2.454% |  | Stair/Elevator​ | 848.01 | 2.211% |  | Stair/Elevator​ | 848 | 2.211%
OfficeLarge | Plenum_FloorG | Plenum | _ | - |  | No |  | 38352.97 | 153411.88 | 1 | 0 | 0 |  | 0% | Plenum​ | 38352.97 | 100% |  | Plenum​ | 38352.97 | 100% |  | Plenum​ | 38,353 ​ | 100%
OfficeLarge | Perimeter_Open_Office_N_FloorM | Office Area (>250 square feet) | VAV With Reheat_FloorM | AHU VAV_FloorM | Office | Yes | 1.43% | 7131.29 | 64181.61 | 10 | 35.6564 | 5 |  | 14.3% | Total | 38353 | 100% |  | Total |  | 100% |  | Total |  | 99.99%
OfficeLarge | Perimeter_Open_Office_S_FloorM | Office Area (>250 square feet) | VAV With Reheat_FloorM | AHU VAV_FloorM | Office | Yes | 1.05% | 5237.37 | 47136.33 | 10 | 26.1868 | 5 |  | 10.5%
OfficeLarge | Perimeter_Open_Office_E_FloorM | Office Area (>250 square feet) | VAV With Reheat_FloorM | AHU VAV_FloorM | Office | Yes | 0.8967% | 4470.44 | 40233.96 | 10 | 22.3522 | 5 |  | 8.967%
OfficeLarge | Perimeter_Open_Office_W_FloorM | Office Area (>250 square feet) | VAV With Reheat_FloorM | AHU VAV_FloorM | Office | Yes | 0.8923% | 4448.76 | 40038.84 | 10 | 22.2438 | 5 |  | 8.923% | Area Distribution By Space Type
OfficeLarge | Perimeter_Enclosed_Office_NE_FloorM | Office Area (>250 square feet) | VAV With Reheat_FloorM | AHU VAV_FloorM | Office | Yes | 0.184% | 917.38 | 8256.42 | 10 | 4.5869 | 5 |  | 1.84% | Space Type |  |  | % Area
OfficeLarge | Perimeter_Enclosed_Office_NW_FloorM | Office Area (>250 square feet) | VAV With Reheat_FloorM | AHU VAV_FloorM | Office | Yes | 0.2269% | 1131.21 | 10180.89 | 10 | 5.6561 | 5 |  | 2.269% | Office Area (>250 square feet) |  |  | 71.14%
OfficeLarge | Perimeter_Enclosed_Office_SW_FloorM | Office Area (>250 square feet) | VAV With Reheat_FloorM | AHU VAV_FloorM | Office | Yes | 0.2027% | 1010.49 | 9094.41 | 10 | 5.0524 | 5 |  | 2.027% | Convention, Conference, Multipurpose and Meeting Area |  |  | 5.401%
OfficeLarge | Perimeter_Enclosed_Office_SE_FloorM | Office Area (>250 square feet) | VAV With Reheat_FloorM | AHU VAV_FloorM | Office | Yes | 0.2073% | 1033.48 | 9301.32 | 10 | 5.1674 | 5 |  | 2.073% | Lobby, Main Entry |  |  | 2.462%
OfficeLarge | Core_Enclosed_Office_FloorM | Office Area (>250 square feet) | VAV With Reheat_FloorM | AHU VAV_FloorM | Office | Yes | 0.6485% | 3233 | 29097 | 10 | 16.165 | 5 |  | 6.485% | Storage (General) |  |  | 2.068%
OfficeLarge | Server_Room_FloorM | Computer Room (EPD 20) | CRAC DX Clg_FloorM | PTAC DX Clg Elec Htg | Data | Yes | 0.08384% | 418 | 3762 | 10 | 0.627 | 1.5 | New space type defined for this prototype. | 0.8384% | Electrical, Mechanical, Telephone Rooms |  |  | 4.127%
OfficeLarge | Mech/Elec_FloorM | Electrical, Mechanical, Telephone Rooms | VAV With Reheat_FloorM | AHU VAV_FloorM | Ancillary | Yes | 0.2146% | 1070 | 9630 | 10 | 0 | 0 |  | 2.146% | Computer Room (EPD 20) |  |  | 2.656%
OfficeLarge | Conference_N_FloorM | Convention, Conference, Multipurpose and Meeting Area | VAV With Reheat_FloorM | AHU VAV_FloorM | Office | Yes | 0.1584% | 789.8 | 7108.2 | 10 | 26.0634 | 33 |  | 1.584% | Restrooms |  |  | 2.978%
OfficeLarge | Conference_W_FloorM | Convention, Conference, Multipurpose and Meeting Area | VAV With Reheat_FloorM | AHU VAV_FloorM | Office | Yes | 0.06748% | 336.44 | 3027.96 | 10 | 11.1025 | 33 |  | 0.6748% | Lounge, Breakroom, or Waiting Area |  |  | 2.327%
OfficeLarge | Conference_S_FloorM | Convention, Conference, Multipurpose and Meeting Area | VAV With Reheat_FloorM | AHU VAV_FloorM | Office | Yes | 0.1532% | 763.8 | 6874.2 | 10 | 25.2054 | 33 |  | 1.532% | Stairwell |  |  | 2.291%
OfficeLarge | Conference_E_FloorM | Convention, Conference, Multipurpose and Meeting Area | VAV With Reheat_FloorM | AHU VAV_FloorM | Office | Yes | 0.08689% | 433.2 | 3898.8 | 10 | 14.2956 | 33 |  | 0.8689% | Corridor Area |  |  | 4.067%
OfficeLarge | Break/FoorPrep_FloorM | Lounge, Breakroom, or Waiting Area | VAV With Reheat_FloorM | AHU VAV_FloorM | Office | Yes | 0.1825% | 910 | 8190 | 10 | 30.03 | 33 |  | 1.825% | Locker Room |  |  | 0.3541%
OfficeLarge | Storage_FloorM | Storage (General) | VAV With Reheat_FloorM | AHU VAV_FloorM | Ancillary | Yes | 0.148% | 738 | 6642 | 10 | 0 | 0 | Occupant load density for storage is based on Title 24, 2025, Appendix 5.4A. | 1.48% | Kitchen/Food Preparation Area |  |  | 0.1879%
OfficeLarge | Lobby/Lounge_FloorM | Lounge, Breakroom, or Waiting Area | VAV With Reheat_FloorM | AHU VAV_FloorM | Office | Yes | 0.1372% | 684 | 6156 | 10 | 10.26 | 15 | Appendix 5.4A assigns 2.5 occupants to kitchenette spaces, but because this room serves as a combined break/kitchenette area—and break rooms assume 33 occupants—we applied a midpoint value. The lounge overlaps functionally with the break area, so its occupant count (33) was reduced to 15 to keep overall loads balanced. | 1.372% | Total
OfficeLarge | Restroom_FloorM | Restrooms | VAV With Reheat_FloorM | AHU VAV_FloorM | Office | Yes | 0.2317% | 1155 | 10395 | 10 | 0 | 0 |  | 2.317%
OfficeLarge | Stair/Elevator_FloorM | Stairwell | VAV With Reheat_FloorM | AHU VAV_FloorM | Ancillary | Yes | 0.1701% | 848 | 7632 | 10 | 0 | 0 |  | 1.701%
OfficeLarge | Corridor_W_FloorM | Corridor Area | VAV With Reheat_FloorM | AHU VAV_FloorM | Office | Yes | 0.2018% | 1005.88 | 9052.92 | 10 | 5.0294 | 5 |  | 2.018%
OfficeLarge | Corridor_E_FloorM | Corridor Area | VAV With Reheat_FloorM | AHU VAV_FloorM | Office | Yes | 0.1174% | 585.36 | 5268.24 | 10 | 2.9268 | 5 |  | 1.174%
OfficeLarge | Plenum_FloorM | Plenum | _ | - |  | No |  | 38352.97 | 153411.88 | 10 | 0 | 0 |  | 0%
OfficeLarge | Perimeter_Open_Office_N_FloorT | Office Area (>250 square feet) | VAV With Reheat_FloorT | AHU VAV_FloorT | Office | Yes | 1.43% | 7131.29 | 64181.61 | 1 | 35.6564 | 5 |  | 1.43%
OfficeLarge | Perimeter_Open_Office_S_FloorT | Office Area (>250 square feet) | VAV With Reheat_FloorT | AHU VAV_FloorT | Office | Yes | 1.05% | 5237.37 | 47136.33 | 1 | 26.1868 | 5 |  | 1.05%
OfficeLarge | Perimeter_Open_Office_E_FloorT | Office Area (>250 square feet) | VAV With Reheat_FloorT | AHU VAV_FloorT | Office | Yes | 0.8967% | 4470.44 | 40233.96 | 1 | 22.3522 | 5 |  | 0.8967%
OfficeLarge | Perimeter_Open_Office_W_FloorT | Office Area (>250 square feet) | VAV With Reheat_FloorT | AHU VAV_FloorT | Office | Yes | 0.8923% | 4448.76 | 40038.84 | 1 | 22.2438 | 5 |  | 0.8923%
OfficeLarge | Perimeter_Enclosed_Office_NE_FloorT | Office Area (>250 square feet) | VAV With Reheat_FloorT | AHU VAV_FloorT | Office | Yes | 0.184% | 917.38 | 8256.42 | 1 | 4.5869 | 5 |  | 0.184%
OfficeLarge | Perimeter_Enclosed_Office_NW_FloorT | Office Area (>250 square feet) | VAV With Reheat_FloorT | AHU VAV_FloorT | Office | Yes | 0.2269% | 1131.21 | 10180.89 | 1 | 5.6561 | 5 |  | 0.2269%
OfficeLarge | Perimeter_Enclosed_Office_SW_FloorT | Office Area (>250 square feet) | VAV With Reheat_FloorT | AHU VAV_FloorT | Office | Yes | 0.2027% | 1010.49 | 9094.41 | 1 | 5.0524 | 5 |  | 0.2027%
OfficeLarge | Perimeter_Enclosed_Office_SE_FloorT | Office Area (>250 square feet) | VAV With Reheat_FloorT | AHU VAV_FloorT | Office | Yes | 0.2073% | 1033.48 | 9301.32 | 1 | 5.1674 | 5 |  | 0.2073%
OfficeLarge | Core_Enclosed_Office_FloorT | Office Area (>250 square feet) | VAV With Reheat_FloorT | AHU VAV_FloorT | Office | Yes | 0.6485% | 3233 | 29097 | 1 | 16.165 | 5 |  | 0.6485%
OfficeLarge | Server_Room_FloorT | Computer Room (EPD 20) | CRAC DX Clg_FloorT | PTAC DX Clg Elec Htg 2 | Data | Yes | 0.08384% | 418 | 3762 | 1 | 0.627 | 1.5 | New space type defined for this prototype. | 0.08384%
OfficeLarge | Mech/Elec_FloorT | Electrical, Mechanical, Telephone Rooms | VAV With Reheat_FloorT | AHU VAV_FloorT | Ancillary | Yes | 0.2146% | 1070 | 9630 | 1 | 0 | 0 |  | 0.2146%
OfficeLarge | Conference_N_FloorT | Convention, Conference, Multipurpose and Meeting Area | VAV With Reheat_FloorT | AHU VAV_FloorT | Office | Yes | 0.1584% | 789.8 | 7108.2 | 1 | 26.0634 | 33 |  | 0.1584%
OfficeLarge | Conference_W_FloorT | Convention, Conference, Multipurpose and Meeting Area | VAV With Reheat_FloorT | AHU VAV_FloorT | Office | Yes | 0.06748% | 336.44 | 3027.96 | 1 | 11.1025 | 33 |  | 0.06748%
OfficeLarge | Conference_S_FloorT | Convention, Conference, Multipurpose and Meeting Area | VAV With Reheat_FloorT | AHU VAV_FloorT | Office | Yes | 0.1532% | 763.8 | 6874.2 | 1 | 25.2054 | 33 |  | 0.1532%
OfficeLarge | Conference_E_FloorT | Convention, Conference, Multipurpose and Meeting Area | VAV With Reheat_FloorT | AHU VAV_FloorT | Office | Yes | 0.08689% | 433.2 | 3898.8 | 1 | 14.2956 | 33 |  | 0.08689%
OfficeLarge | BreakRoom/FoodPrep_FloorT | Lounge, Breakroom, or Waiting Area | VAV With Reheat_FloorT | AHU VAV_FloorT | Office | Yes | 0.1825% | 910 | 8190 | 1 | 30.03 | 33 |  | 0.1825%
OfficeLarge | Storage_FloorT | Storage (General) | VAV With Reheat_FloorT | AHU VAV_FloorT | Ancillary | Yes | 0.148% | 738 | 6642 | 1 | 0 | 0 | Occupant load density for storage is based on Title 24, 2025, Appendix 5.4A. | 0.148%
OfficeLarge | Lobby/Lounge_FloorT | Lounge, Breakroom, or Waiting Area | VAV With Reheat_FloorT | AHU VAV_FloorT | Office | Yes | 0.1372% | 684 | 6156 | 1 | 10.26 | 15 | Increased the ASHRAE 62.1 number of people (10) since this area is more of a lounge/lobby space and not main entry lobby. | 0.1372%
OfficeLarge | Restroom_FloorT | Restrooms | VAV With Reheat_FloorT | AHU VAV_FloorT | Office | Yes | 0.2317% | 1155 | 10395 | 1 | 0 | 0 |  | 0.2317%
OfficeLarge | Stair/Elevator_FloorT | Stairwell | VAV With Reheat_FloorT | AHU VAV_FloorT | Ancillary | Yes | 0.1701% | 848 | 7632 | 1 | 0 | 0 |  | 0.1701%
OfficeLarge | Corridor_W_FloorT | Corridor Area | VAV With Reheat_FloorT | AHU VAV_FloorT | Office | Yes | 0.2018% | 1005.88 | 9052.92 | 1 | 5.0294 | 5 |  | 0.2018%
OfficeLarge | Corridor_E_FloorT | Corridor Area | VAV With Reheat_FloorT | AHU VAV_FloorT | Office | Yes | 0.1174% | 585.36 | 5268.24 | 1 | 2.9268 | 5 |  | 0.1174%
OfficeLarge | Plenum_FloorT | Plenum | _ | - |  | No |  | 38352.97 | 153411.88 | 1 | 0 | 0 |  | 0%
Total ( 1 Building) | Total Zones in E+: 79 Total with multiplier: 286 | Total (13 Space Types) | Total systems in E+: 8 Total with multiplier: 26 | Total systems in E+: 8 Total with multiplier: 27 | Total (1 category) | Total zones in E+: 76 conditioned and 3 unconditioned. Total with multiplier: 274 Conditioned , 12 Unconditioned ) | 100% | 498564.19 | [5 empty] | 0%
N

## Envelope
Envelope
Element | Prototype | Assembly Type | Construction | Thermal Properties | Vintage | Selected T24 | Notes | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
External Wall | OfficeLarge | ExtWall_MetalFramed_NonRes | Metal framed wall: Metal frame + insulation + Gypsum board | U-factor IP | Pre 1978 | N/A | ASHRAE 90.1 Table A3.3.3.1, 16" on center, R-0 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352
[5 empty] | 1978-1997 | 1986 | High-rise office: Package A with heat capacity 10.0-14.99 (BTU/F/ft2) | 0.21277 | 0.22727 | 0.22727 | 0.21739 | 0.21739 | 0.25641 | 0.25641 | 0.25641 | 0.25641 | 0.25641 | 0.2381 | 0.2381 | 0.2381 | 0.20833 | 0.20833 | 0.21277
[5 empty] | 1998-2007 | 2001 | TABLE 1-H | 0.182 | 0.182 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182
[5 empty] | 2008-2018 | 2013 | TABLE 140.3-B | 0.098 | 0.062 | 0.082 | 0.062 | 0.062 | 0.098 | 0.098 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062
[5 empty] | 2019+ | 2025 | Table 140.3-B (In Nonres Section) | 0.06 | 0.055 | 0.071 | 0.055 | 0.055 | 0.06 | 0.06 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055
Roof | OfficeLarge | FlatRoof_WoodFramedAndOther_NonRes | Metal deck roof: Metal deck + insulation + Roof membrane | U-factor IP | Pre 1978 | N/A | Considering 30 years for roof/ insulation replacement. | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 1978-1997 | 1992 |  | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 1998-2007 | 2001 | TABLE 1-H | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 2008-2018 | 2013 | TABLE 140.3-B | 0.049 | 0.039 | 0.039 | 0.039 | 0.049 | 0.075 | 0.067 | 0.067 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039
[5 empty] | 2019+ | 2025 | Table 140.3-B (In Nonres Section) | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.047 | 0.047 | 0.047 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028
Windows | OfficeLarge | FixedWindow_NonRes | CBECS 2018 shows that ~50% of large offices that were built before 2000 are single pane | U-factor IP | Pre 1978 | N/A | ASHRAE Handbook of Fundamentals for single pane (Table 4-Ch15) & T24, 2013 for double pane(50%-50%)* | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74
[5 empty] | 1978-1997 | N/A |  | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74
|  |  | Double pane |  | 1998-2007 | 2001 | TABLE 1-H | 0.49 | 0.49 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49
[5 empty] | 2008-2018 | 2013 | TABLE 140.3-B | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36
[5 empty] | 2019+ | 2025 | Table 140.3-B (In Nonres Section) | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.34 | 0.36 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.36
|  | FixedWindow_NonRes | CBECS 2018 shows that ~50% of large offices that were built before 2000 are single pane | SHGC | Pre 1978 | N/A | ASHRAE Handbook of Fundamentals for single pane (Table 10-Ch15) & T24, 2013 for double pane(50%-50%)* | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52
[5 empty] | 1978-1997 | N/A |  | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52
[5 empty] | 1998-2007 | 2001 | WWR:30-40 / SHGC non-north (Non-north SHGC is more stringent than north and is therefore considered for all sides) | 0.43 | 0.31 | 0.41 | 0.41 | 0.41 | 0.34 | 0.34 | 0.34 | 0.34 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.43
[5 empty] | 2008-2018 | 2013 | TABLE 140.3-B | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
[5 empty] | 2019+ | 2025 | Table 140.3-B (In Nonres Section) | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.22 | 0.25 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.25
Infiltration rate at normal pressure (cfm/ft2) (Design flow rate approach and Flow/Exterior Wall Area calculation method)
|  |  | Building | Zones | Vintage | I_75 (cfm/sf) 6-sdied Infiltration rate @ 75 pa | Note | CZ1: I-design (cfm/ft2) (4-sided Infiltration rate at normal pressure) (Design flow rate approach and Flow/Exterior Wall Area calculation method)
|  | Infiltration | OfficeLarge |  | Pre 1978 | 1.1 | 2022 CASE report (Table 38) | CZ1: #REF! | Building 4 sided area (ft2) | #REF!
[5 empty] | 1978-1997 | 1.1 | 2022 CASE report (Table 38) | CZ1: #REF! | Building 6 sided area (ft2) | #REF!
[5 empty] | 1998-2007 | 1.1 | 2022 CASE report (Table 38) | CZ1: #REF! | 6 sided /4 sided factor | #REF!
[5 empty] | 2008-2018 | 1 | 2022 CASE report (Table 38) & Title 24, part 6, 2008-2016 (Table 140.3-B) | CZ1: #REF! | Floor or roof area (ft2) | 38352.9692
[5 empty] | 2019+ | 0.6 | 2022 CASE report (Table 38) & Title 24, part 6, 2025 (Table 140.3-B) | CZ1: #REF!
Source: Title 24 air barrier requirements (all editions) and the standardized infiltration rate reported in the 2022 CASE report and Dodge 2023 data
|  |  |  | Air Leakage Memo: |  | Infiltration_rate_report_14May2025-Short-Version.docx
*Note for windows properties in vintage 1 &2 :
We’ve considered a 50% single-pane and 50% double-pane mix (based on the 2013 requirements) for the window properties in Vintage 1 & 2 (pre-1998 buildings).
We don't have California-specific data, and the decision was based on the CBECS 2018 data, which indicates:
- 30% of large offices built before 1978 have mixed windows, while only 16% of large offices from the second vintage (1978-1997) have mixed glass.
- Pre-1980: Among those with either single or double-pane windows, 70% have single-pane windows, and 30% have double-pane windows.
- 1980-1999: Among those with either single or double-pane windows, 43% have single-pane windows, and 57% have double-pane windows.
- Pre-2000: Among those with either single or double-pane windows, 49% has single pane windows.
Considering the Pre-2000 percentage, we've decided to apply the 50%-50% mix to the window properties of the first two vintages.

## HVAC System
HVAC system - OfficeLarge | [7 empty] | Existing HVAC System Layout _ Each floor is served by one HVAC system
Vintage | Zones | Heating | Cooling | Air Distribution | Other Systems | Source |  | Basement | First Floor | Middle/Top Floors
Existing | Server Room_B | - | built up CRAH with chilled water coils (Computer Room Air Handling unit) | CAV | Fluid Economizer for vintage 4 | Engineering Judgement
| Server_Room_G Server_Room_M Server_Room_T | - | DX Computer Room Air Conditioner (CRAC) | CAV | _ | Engineering Judgement
| All other conditioned zones | Gas Boiler | Chiller (it also serves the Server_Room_B zone) | VAV with hydronic reheat | OA mixing through air handler Economizer for Vintage 2, 3 and 4 DCV for Vintage 4 (for qualifying high density rooms) | CEUS 2022
New Construction | Server Room_B | - | built up CRAH with chilled water coils (Computer Room Air Handling unit) | CAV | Fluid Economizer | T24 2025
| Server_Room_G Server_Room_M Server_Room_T | - | DX Computer Room Air Conditioner (CRAC) | CAV | _ | T24 2025
| All other conditioned zones | Gas Boiler | Chiller (it also serves the Server_Room_B zone) | VAV with hydronic reheat | OA mixing through air handler ERV Economizer DCV for qualifying high density rooms | T24 2025
Efficiency of HVAC System (Efficiency is capacity-dependent. The following table provides a general estimate of system efficiency based on preliminary simulations in one climate zone, or assuming cooling load based on rule of thumb)
| Upgrade/Installed year | DX Computer Room Air Conditioner Server_Room_G/M/T (CRAC) | Chiller | Gas Boiler | Heat Rejection (Cooling Tower) | Sources | Note
Pre 1978 | 2008 | 11 EER for <65 kBtu/h 10.4 EER for 65-135 kBtu/h 10.2 EER for 135-240 kBtu/h | Water Cooled, Electrically Operated, Centrifugal--≥ 300 tons 6.10 COP 6.40 IPLV | 80% Ec | Axial fan Open-circuit cooling tower--95°F entering water 85°F leaving water 75°F entering air wb--≥ 38.2 gpm/hp | CRAC: California Title 20 Appliance Efficiency Regulations, §1605.3(c)(2), Tables C-9 (2008) T24, Table 112-D (for chiller COP)(2008) California Title 20 Appliance Efficiency Regulations, Table E-3 for Boiler Efficiency (2008) T24, Table 112-G (Performance Requirements for Heat Rejection Equipment) (2008) | Two centrifugal chillers (Total cooling plant load > 600 tons) Two atmospheric boilers (no combustion air fans)
1978-1997
1998-2007
2008-2018 | 2013 This system will be used for the Collapsed version | SCOP= 2.44 for <65 kBtu/h 2.34 for 65-240 kBtu/h 2.24 for >240 kBtu/h | Water Cooled, Electrically Operated, Centrifugal--≥ 300 tons and < 600 tons ≤ 0.600 kW/ton (Path B) ≤ 0.400 IPLV (Path B) | Gas-Fired Boiler > 300,000 Btu/h and ≤2,500,000 Btu/h-- 80% Et Gas-Fired Boiler > 2,500,000 Btu/h -- 82% Ec < 300,000 Btu/h 82% AFUE | Axial fan Open-circuit cooling tower--95°F entering water 85°F leaving water 75°F entering air wb--≥ 42.1 gpm/hp | CRAC: 10 CFR §431.97(f)(1), Table 7 (2013) T24, Table 110.2-D (for chiller COP) (2013) T24, Table 110.2-K (for Boiler thermal efficiency) (2013) T24, Table 110.2-G (Performance Requirements for Heat Rejection Equipment) (2013) | water-cooled centrifugal chillers Two Boilers each with capacity between 300-2,500 KBTU/hr
New Construction | 2025 | NSenCOP= 2.09 for <65 kBtu/h 1.99 for 65-240 kBtu/h 1,81 for >240 kBtu/h | Water Cooled, Electrically Operated, Positive displacement--≥ 300 tons and < 600 ton ≤ 0.625 kW/ton (Path B) ≤ 0.410 IPLV (Path B) | Gas-Fired Boiler > 300,000 Btu/h and ≤2,500,000 Btu/h-- 80% Et Gas-Fired Boiler > 2,500,000 Btu/h -- 82% Ec | Axial fan Open-circuit cooling tower--95°F entering water 85°F leaving water 75°F entering air wb--≥ 42.1 gpm/hp | CRAC: 10 CFR § 431.97, Table 13 (2025) T24, Table 110.2-D (for chiller COP)(2025) 10 CFR 431.86 , section § 431.87 Table 1 (for Boiler thermal efficiency)(2025) T24, Table 110.2-E (Performance Requirements for Heat Rejection Equipment)(2025) | Two water-cooled screw chillers (Each between 300-600 ton), Path B, Positive displacement chiller with design leaving fluid temperature ≤ 32°F Two Boilers each with capacity between 300-2,500 KBTU/hr
Background Data [To be deleted prior to publication]
Existing prototypes:
| Space | System No. | System Type | Fan Control | Cooling Type | Heating Type
CBECC 2025 | All Space |  |  | VAV | Chilled water | Hot-water fossil fuel boiler
CPUC 2024 | All Space |  |  | VAV | Chiller water | Gas Boiler
PNNL ASHRAE 90.1- 2022 San Diego | data center room | 14. WSHP (CRAC) | Water source heat pump (Computer room air conditioning unit) | Constant volume | Fluid cooler | Hot-water fossil fuel boiler
| Basement (Except data center) | 12. SZ-CV-HW | Single-zone system | Constant volume | Chilled water | Hot-water fossil fuel boiler
| Other spaces | 7. VAV with reheat | VAV with reheat | VAV | Chilled water | Hot-water fossil fuel boiler
Basement system in PNNL model is :SZ-CV-HW (Single zone system: CV fan control & Chilled water cooling & Hot-water fossil fuel boiler heating)
Other floors system in PNNL model is: VAV Reheat ( VAV with Reheat: VA fan control & Chilled water cooling & Hot-water fossil fuel boiler heating )
Dat center zone has its won system in PNNL model: WSHP (CRAC): Water source heat pump (Computer room air conditioning unit) system: CV fan control & Fluid cooler & Hot-water fossil fuel boiler heating
CEUS 2022 data:
Heating System
Calculation method | Building Type | Fan Coil / Unit Ventilator | Dual Duct Constant Air Volume | Dual Duct Variable Air Volume |  | Single Duct Constant Air Volume | Single Duct Variable Air Volume
Floorspace-Based | Office, Large |  | 3% | 15% |  | 43% | 21%
Sites-Based | Office, Large | 13% | 2% | 7% |  | 66% | 12%
Chiller System
Calculation method | Building Type | Boiler/ Hydronic | Package System / Heat Pump | Split-System / Heat Pump |  | Ductless Mini-Split Heat Pump | Room Heating
Floorspace-Based | Office, Large | 59% | 35% | 5% |  | 0% | 0%
Sites-Based | Office, Large | 34% | 58% | 7% |  | 0% | 0%
Heating Fuel Type
Calculation method | Building Type | Gas Share | Electric Share
Floorspace-Based | Office, Large | 86% | 13%
Sites-Based | Office, Large | 79% | 20%
Fuel Share Large office (area >3,000 sf)
CZ | Heating system |  |  | Water heater
| Saturation (Electric) | Saturation (Gas) | Saturation (Other Fuels) | Saturation (Electric) | Saturation (Gas) | Saturation (Other Fuels)
1 | 3% | 97% | 0% | 17% | 83% | 0%
2 | 7% | 93% | 0% | 30% | 70% | 0%
3 | 2% | 94% | 4% | 36% | 64% | 4%
4 | 1% | 94% | 4% | 35% | 65% | 4%
5 | 4% | 95% | 2% | 74% | 26% | 2%
6 | 21% | 79% | 0% | 38% | 62% | 0%
7 | 11% | 87% | 2% | 30% | 70% | 1%
8 | 23% | 77% | 0% | 37% | 63% | 0%
9 | 16% | 83% | 0% | 33% | 67% | 0%
10 | 16% | 83% | 1% | 49% | 51% | 0%
11 | 10% | 89% | 1% | 42% | 58% | 1%
12 | 10% | 88% | 2% | 38% | 62% | 3%
13 | 4% | 96% | 0% | 16% | 84% | 0%
14 | 31% | 69% | 0% | 43% | 57% | 0%
15 | 9% | 89% | 2% | 82% | 18% | 0%
16 | 20% | 80% | 0% | 35% | 65% | 0%
Fan power
Vintage | Approach | System | Total Static Pressure (TSP) (in w.c.) | Fan Efficiency [ACM 2025] | Motor Efficiency | Fan Power Index (W/cfm) | Data Source | Note
Existing | PNNL 90.1-2011, TSP | CAV System <7,437 cfm | 2.5 | 0.65 | ASHRAE 90.1, 2004, Table 10.8 * |  | Fan power formula: PNNL 20405, 2010, section 5.2.2.5 TSP and fan efficiency: PNNL 20405, 2010, Table 5.11, 90.1-04ac values Motor and drive efficiency: ASHRAE 90.1, 2004, Table 10.8
|  | CAV System >7,437 cfm | 4.09
|  | VAV System > 4,648 cfm | 5.58
Brake horsepower (bhp) = (Supply cfm × TSP in w.c.) / (6356 × fan efficiency)
Fan power (w/cfm) = (bhp × 746) / ( supply cfm × motor efficiency )
New Construction | ACM 2025 | VAV with hydronic reheat (System 6), >10,000 cfm | TSP = fan power × motor efficiency × fan efficiency × 6356 / 746 | 0.65 | 2025 ACM Table 12 ** | 0.947 | Fan power index: [ACM 2025, Table 13] Motor efficiency: [ACM 2025, Table 12]
* According to PNNL 20405 section 5.2.2.5, the full-load efficiency of the motor serving the fan is taken from ASHRAE 90.1, 2004, Table 10.8, based on motor nameplate and assuming enclosed motors operating at 1,800 rotations per minute (rpm) Motor nameplate size (bhp) = brake horsepower (bhp) × 1.1 ( using a 10% oversizing factor)
** The full‑load efficiency of the motor serving the fan is taken from ACM 2025 Table 12 based on the cfm of the fan. Brake horsepower (bhp) = (Supply cfm from sizing run × fan power in W/cfm) / 746. Note: ACM System 6 VAV >10,000 cfm. Server-room CRAH/CRAC fans are not in this row.
〖𝐹𝑎𝑛 𝑝𝑜𝑤𝑒𝑟〗_(𝑤/𝑐𝑓𝑚)=(〖𝑇𝑆𝑃〗_(𝑖𝑛 𝑤.𝑐)∗746)/(6356∗𝜇_𝑓𝑎𝑛∗𝜇_𝑚𝑜𝑡𝑜𝑟 )
𝑏ℎ𝑝=(𝑐𝑓𝑚∗〖𝑇𝑆𝑃〗_(𝑖𝑛 𝑤.𝑐.))/〖6356∗𝜇〗_𝑓𝑎𝑛
〖𝐹𝑎𝑛 𝑝𝑜𝑤𝑒𝑟〗_(𝑤/𝑐𝑓𝑚)=(𝑏ℎ𝑝∗746)/(𝑐𝑓𝑚∗𝜇_𝑚𝑜𝑡𝑜𝑟 )
𝑏ℎ𝑝=(〖𝐹𝑎𝑛 𝑝𝑜𝑤𝑒𝑟〗_(𝑤/𝑐𝑓𝑚)∗𝑐𝑓𝑚∗𝜇_𝑚𝑜𝑡𝑜𝑟)/746
N

## Thermostat
Thermostat Setpoints - OfficeLarge
Spaces/Zones | Setpoint | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16 | Source
All conditioned zones except server rooms | Heating Setpoint (F) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | T24 2022 - Appendix 5.4B
| Heating Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
| Cooling Setpoint (F) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
| Cooling Setback (F) | 85* | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
Server rooms | Cooling Setpoint (F) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | Title 24, Part 6, 2025, section 140.9 (a) and PNNL ASHRAE 90.1 2022 Large Office prototype
| Heating Setpoint (F) | CZ1: The Server room with 20 W/ft2 load would likely don't require heating system as the equipment constantly generate enough heat. **
Storage, Stairway, and Mechanical_Electrical | Heating Setpoint (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | Engineering Judgment (Semi‑conditioned space)
| Heating Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
| Cooling Setpoint (F) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
| Cooling Setback (F) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
*PNNL has considered 80 F for cooling setback of Large Office prototype (same as Medium Office). However cooling setback is 85 F in Small Office prototype !
**PNNL has set the heating system temperature to 65°F for all of their data center zones.
Background Data [To be deleted prior to publication] | bar: CZ3 to CZ5
Heating/ CoolingSetpointsSchedules (existing prototypes extracted from the idf files (presented below)
| Heating | CZ9: Cooling
| CEC-2022 | CZ4: PNNL-2022; CZ9: CEC-2022; CZ13: PNNL-2022
| CEC-Weekday | CEC-Saturday | CEC-Sunday |  | PNNL-Weekday | PNNL-Saturday | PNNL-Sunday |  |  | CEC-Weekday | CEC-Saturday | CEC-Sunday |  | PNNL-Weekday | PNNL-Saturday | PNNL-Sunday
1 | 60 | 60 | 60 |  | 60.08 | 60.08 | 60.08 |  |  | 85 | 85 | 85 |  | 80.06 | 80.06 | 80.06
2 | 60 | 60 | 60 |  | 60.08 | 60.08 | 60.08 |  |  | 85 | 85 | 85 |  | 80.06 | 80.06 | 80.06
3 | 60 | 60 | 60 |  | 60.08 | 60.08 | 60.08 |  |  | 85 | 85 | 85 |  | 80.06 | 80.06 | 80.06
4 | 60 | 60 | 60 |  | 60.08 | 60.08 | 60.08 |  |  | 85 | 85 | 85 |  | 80.06 | 80.06 | 80.06
5 | 60 | 60 | 60 |  | 60.08 | 60.08 | 60.08 |  |  | 85 | 85 | 85 |  | 80.06 | 80.06 | 80.06
6 | 70 | 70 | 60 |  | 64.04 | 64.04 | 60.08 |  |  | 75 | 75 | 85 |  | 78.08 | 78.26 | 80.06
7 | 70 | 70 | 60 |  | 68 | 68 | 60.08 |  |  | 75 | 75 | 85 |  | 77 | 77 | 80.06
8 | 70 | 70 | 60 |  | 69.8 | 69.8 | 60.08 |  |  | 75 | 75 | 85 |  | 75.2 | 75.2 | 80.06
9 | 70 | 70 | 60 |  | 69.8 | 69.8 | 60.08 |  |  | 75 | 75 | 85 |  | 75.2 | 75.2 | 80.06
10 | 70 | 70 | 60 |  | 69.8 | 69.8 | 60.08 |  |  | 75 | 75 | 85 |  | 75.2 | 75.2 | 80.06
11 | 70 | 70 | 60 |  | 69.8 | 69.8 | 60.08 |  |  | 75 | 75 | 85 |  | 75.2 | 75.2 | 80.06
12 | 70 | 70 | 60 |  | 69.8 | 69.8 | 60.08 |  |  | 75 | 75 | 85 |  | 75.2 | 75.2 | 80.06
13 | 70 | 70 | 60 |  | 69.8 | 69.8 | 60.08 |  |  | 75 | 75 | 85 |  | 75.2 | 75.2 | 80.06
14 | 70 | 70 | 60 |  | 69.8 | 69.8 | 60.08 |  |  | 75 | 75 | 85 |  | 75.2 | 75.2 | 80.06
15 | 70 | 70 | 60 |  | 69.8 | 69.8 | 60.08 |  |  | 75 | 75 | 85 |  | 75.2 | 75.2 | 80.06
16 | 70 | 70 | 60 |  | 69.8 | 69.8 | 60.08 |  |  | 75 | 75 | 85 |  | 75.2 | 75.2 | 80.06
17 | 70 | 70 | 60 |  | 69.8 | 69.8 | 60.08 |  |  | 75 | 75 | 85 |  | 75.2 | 75.2 | 80.06
18 | 70 | 70 | 60 |  | 69.8 | 60.08 | 60.08 |  |  | 75 | 75 | 85 |  | 75.2 | 80.06 | 80.06
19 | 70 | 70 | 60 |  | 69.8 | 60.08 | 60.08 |  |  | 75 | 75 | 85 |  | 75.2 | 80.06 | 80.06
20 | 70 | 60 | 60 |  | 69.8 | 60.08 | 60.08 |  |  | 75 | 85 | 85 |  | 75.2 | 80.06 | 80.06
21 | 70 | 60 | 60 |  | 69.8 | 60.08 | 60.08 |  |  | 75 | 85 | 85 |  | 75.2 | 80.06 | 80.06
22 | 70 | 60 | 60 |  | 69.8 | 60.08 | 60.08 |  |  | 75 | 85 | 85 |  | 75.2 | 80.06 | 80.06
23 | 70 | 60 | 60 |  | 60.08 | 60.08 | 60.08 |  |  | 75 | 85 | 85 |  | 80.06 | 80.06 | 80.06
24 | 70 | 60 | 60 |  | 60.08 | 60.08 | 60.08 |  |  | 75 | 85 | 85 |  | 80.06 | 80.06 | 80.06

## Ventilation
Outdoor Airflow Rate - OfficeLarge
Space Name | Number of People | Floor Area (ft²) | cfm/person (T24, 2025, Equation 120.1-F and Table 120.1-A) | cfm/ft² (T24, 2025, Equation 120.1-F and Table 120.1-A) | Required Exhaust Rate (T24, 2025, Table 120.1-B – Minimum Exhaust Rates) | Total cfm Driven by People | Total cfm Driven by Area | Total cfm Driven by Exhaust | Total cfm | Note
Perimeter_Open_Office_N_Basement | 42.0843 | 8416.86 | 15 | 0.15 |  | 631.2645 | 1262.529 |  | 1262.529 | Office space/Occupancy Category - Office Buildings
Perimeter_Open_Office_S_Basement | 18.3109 | 3662.18 | 15 | 0.15 |  | 274.6635 | 549.327 |  | 549.327 | Office space/Occupancy Category - Office Buildings
Core_Enclosed_Office_Basement | 18.5184 | 3703.68 | 15 | 0.15 |  | 277.776 | 555.552 |  | 555.552 | Office space/Occupancy Category - Office Buildings
Server_Room_Basement | 41.14 | 8228 | 15 | 0.15 |  | 617.1 | 1234.2 |  | 1234.2 | Telephone/data entry/Occupancy Category - Office Buildings
Mech/Elec_Basement | 0 | 7958 | 15 | 0.15 |  | 0 | 1193.7 |  | 1193.7 | All Other
Conference_Basement | 19.1301 | 579.7 | 15 | 0.15 |  | 286.9515 | 86.955 |  | 286.9515 | Conference/meeting/Occupancy Category - General
BreakRoom/FoodPrep_Basement | 32.109 | 973 | 15 | 0.15 |  | 481.635 | 145.95 |  | 481.635 | Breakrooms/Occupancy Category - Office Buildings
Storage_Basement | 0 | 1231 | 15 | 0.15 |  | 0 | 184.65 |  | 184.65 | Occupiable storage rooms for dry materials/Occupancy Category - Office Buildings
Restroom_Basement | 0 | 986 | 15 | 0.15 | 5* 50/70 (cfm/unit) | 0 | 147.9 | 250 | 250 | Almost 1 unit per 30 occupant for exhaust fan
Lobby/Lounge_Basement | 10.605 | 707 | 15 | 0.15 |  | 159.075 | 106.05 |  | 159.075 | Breakrooms/Occupancy Category - Office Buildings
Stair/Elevator_Basement | 0 | 941 | 15 | 0.15 |  | 0 | 141.15 |  | 141.15 | All Other
Corridor_W_Basement | 3.515 | 703 | 15 | 0.15 |  | 52.725 | 105.45 |  | 105.45 | Corridors /Occupancy Category - General
Corridor_E_Basement | 1.3145 | 262.9 | 15 | 0.15 |  | 19.7175 | 39.435 |  | 39.435 | Corridors /Occupancy Category - General
Perimeter_Open_Office_N_FloorG | 35.6564 | 7131.29 | 15 | 0.15 |  | 534.8468 | 1069.6935 |  | 1069.6935 | Office space/Occupancy Category - Office Buildings
Perimeter_Open_Office_W_FloorG | 28.9789 | 5795.77 | 15 | 0.15 |  | 434.6827 | 869.3655 |  | 869.3655 | Office space/Occupancy Category - Office Buildings
Perimeter_Open_Office_E_FloorG | 29.3774 | 5875.49 | 15 | 0.15 |  | 440.6617 | 881.3235 |  | 881.3235 | Office space/Occupancy Category - Office Buildings
Perimeter_Enclosed_Office_NE_FloorG | 4.5869 | 917.38 | 15 | 0.15 |  | 68.8035 | 137.607 |  | 137.607 | Office space/Occupancy Category - Office Buildings
Perimeter_Enclosed_Office_NW_FloorG | 5.6561 | 1131.21 | 15 | 0.15 |  | 84.8408 | 169.6815 |  | 169.6815 | Office space/Occupancy Category - Office Buildings
Core_Enclosed_Office_FloorG | 16.5614 | 3312.28 | 15 | 0.15 |  | 248.421 | 496.842 |  | 496.842 | Office space/Occupancy Category - Office Buildings
Server_Room_FloorG | 0.62563 | 417.09 | 15 | 0.15 |  | 9.3845 | 62.5635 |  | 62.5635 | Telephone/data entry/Occupancy Category - Office Buildings
Mech/Elec_FloorG | 0 | 848.96 | 15 | 0.15 |  | 0 | 127.344 |  | 127.344 | All Other
Conference_FloorG | 26.0637 | 789.81 | 15 | 0.15 |  | 390.9559 | 118.4715 |  | 390.9559 | Conference/meeting/Occupancy Category - General
BreakRoom_FloorG | 20.4016 | 618.23 | 15 | 0.15 |  | 306.0238 | 92.7345 |  | 306.0238 | Breakrooms/Occupancy Category - Office Buildings
FoodPrep_FloorG | 2.8108 | 936.94 | 15 | 0.15 |  | 42.1623 | 140.541 |  | 140.541 | Kitchen (cooking)/Occupancy Category - Food and Beverage Service
Storage_FloorG | 0 | 959.03 | 15 | 0.15 |  | 0 | 143.8545 |  | 143.8545 | Occupiable storage rooms for dry materials/Occupancy Category - Office Buildings
Locker_FloorG | 17.6523 | 1765.23 | 15 | 0.15 | 0.25 (cfm/sf) | 264.7845 | 264.7845 | 441.3075 | 441.3075 | All Other
Lobby_S_FloorG | 33.6063 | 3360.63 | 15 | 0.15 |  | 504.0945 | 504.0945 |  | 504.0945 | Main entry lobbies/Occupancy Category - Office Buildings
Lobby/Lounge_FloorG | 10.2585 | 683.9 | 15 | 0.15 |  | 153.8775 | 102.585 |  | 153.8775 | Main entry lobbies/Occupancy Category - Office Buildings
Restroom_FloorG | 0 | 1156.09 | 15 | 0.15 | 8* 50/70 (cfm/unit) | 0 | 173.4135 | 400 | 400 | All Other
Stair/Elevator_FloorG | 0 | 848.01 | 15 | 0.15 |  | 0 | 127.2015 |  | 127.2015 | All Other
Corridor_W_FloorG | 5.0293 | 1005.87 | 15 | 0.15 |  | 75.4403 | 150.8805 |  | 150.8805 | Corridors /Occupancy Category - General
Corridor_E_FloorG | 3.9938 | 798.76 | 15 | 0.15 |  | 59.907 | 119.814 |  | 119.814 | Corridors /Occupancy Category - General
Plenum_FloorG | 0 | 38352.97 |  |  |  | 0 | 0 |  | 0 | -
Perimeter_Open_Office_N_FloorM | 35.6564 | 7131.29 | 15 | 0.15 |  | 534.8468 | 1069.6935 |  | 1069.6935 | Office space/Occupancy Category - Office Buildings
Perimeter_Open_Office_S_FloorM | 26.1868 | 5237.37 | 15 | 0.15 |  | 392.8028 | 785.6055 |  | 785.6055 | Office space/Occupancy Category - Office Buildings
Perimeter_Open_Office_E_FloorM | 22.3522 | 4470.44 | 15 | 0.15 |  | 335.283 | 670.566 |  | 670.566 | Office space/Occupancy Category - Office Buildings
Perimeter_Open_Office_W_FloorM | 22.2438 | 4448.76 | 15 | 0.15 |  | 333.657 | 667.314 |  | 667.314 | Office space/Occupancy Category - Office Buildings
Perimeter_Enclosed_Office_NE_FloorM | 4.5869 | 917.38 | 15 | 0.15 |  | 68.8035 | 137.607 |  | 137.607 | Office space/Occupancy Category - Office Buildings
Perimeter_Enclosed_Office_NW_FloorM | 5.6561 | 1131.21 | 15 | 0.15 |  | 84.8408 | 169.6815 |  | 169.6815 | Office space/Occupancy Category - Office Buildings
Perimeter_Enclosed_Office_SW_FloorM | 5.0524 | 1010.49 | 15 | 0.15 |  | 75.7867 | 151.5735 |  | 151.5735 | Office space/Occupancy Category - Office Buildings
Perimeter_Enclosed_Office_SE_FloorM | 5.1674 | 1033.48 | 15 | 0.15 |  | 77.511 | 155.022 |  | 155.022 | Office space/Occupancy Category - Office Buildings
Core_Enclosed_Office_FloorM | 16.165 | 3233 | 15 | 0.15 |  | 242.475 | 484.95 |  | 484.95 | Office space/Occupancy Category - Office Buildings
Server_Room_FloorM | 0.627 | 418 | 15 | 0.15 |  | 9.405 | 62.7 |  | 62.7 | Telephone/data entry/Occupancy Category - Office Buildings
Mech/Elec_FloorM | 0 | 1070 | 15 | 0.15 |  | 0 | 160.5 |  | 160.5 | All Other
Conference_N_FloorM | 26.0634 | 789.8 | 15 | 0.15 |  | 390.951 | 118.47 |  | 390.951 | Conference/meeting/Occupancy Category - General
Conference_W_FloorM | 11.1025 | 336.44 | 15 | 0.15 |  | 166.5378 | 50.466 |  | 166.5378 | Conference/meeting/Occupancy Category - General
Conference_S_FloorM | 25.2054 | 763.8 | 15 | 0.15 |  | 378.081 | 114.57 |  | 378.081 | Conference/meeting/Occupancy Category - General
Conference_E_FloorM | 14.2956 | 433.2 | 15 | 0.15 |  | 214.434 | 64.98 |  | 214.434 | Conference/meeting/Occupancy Category - General
Break/FoorPrep_FloorM | 30.03 | 910 | 15 | 0.15 |  | 450.45 | 136.5 |  | 450.45 | Breakrooms/Occupancy Category - Office Buildings
Storage_FloorM | 0 | 738 | 15 | 0.15 |  | 0 | 110.7 |  | 110.7 | Occupiable storage rooms for dry materials/Occupancy Category - Office Buildings
Lobby/Lounge_FloorM | 10.26 | 684 | 15 | 0.15 |  | 153.9 | 102.6 |  | 153.9 | Breakrooms/Occupancy Category - Office Buildings
Restroom_FloorM | 0 | 1155 | 15 | 0.15 | 9* 50/70 (cfm/unit) | 0 | 173.25 | 450 | 450 | All Other
Stair/Elevator_FloorM | 0 | 848 | 15 | 0.15 |  | 0 | 127.2 |  | 127.2 | All Other
Corridor_W_FloorM | 5.0294 | 1005.88 | 15 | 0.15 |  | 75.441 | 150.882 |  | 150.882 | Corridors /Occupancy Category - General
Corridor_E_FloorM | 2.9268 | 585.36 | 15 | 0.15 |  | 43.902 | 87.804 |  | 87.804 | Corridors /Occupancy Category - General
Plenum_FloorM | 0 | 38352.97 |  |  |  | 0 | 0 |  | 0 | -
Perimeter_Open_Office_N_FloorT | 35.6564 | 7131.29 | 15 | 0.15 |  | 534.8468 | 1069.6935 |  | 1069.6935 | Office space/Occupancy Category - Office Buildings
Perimeter_Open_Office_S_FloorT | 26.1868 | 5237.37 | 15 | 0.15 |  | 392.8028 | 785.6055 |  | 785.6055 | Office space/Occupancy Category - Office Buildings
Perimeter_Open_Office_E_FloorT | 22.3522 | 4470.44 | 15 | 0.15 |  | 335.283 | 670.566 |  | 670.566 | Office space/Occupancy Category - Office Buildings
Perimeter_Open_Office_W_FloorT | 22.2438 | 4448.76 | 15 | 0.15 |  | 333.657 | 667.314 |  | 667.314 | Office space/Occupancy Category - Office Buildings
Perimeter_Enclosed_Office_NE_FloorT | 4.5869 | 917.38 | 15 | 0.15 |  | 68.8035 | 137.607 |  | 137.607 | Office space/Occupancy Category - Office Buildings
Perimeter_Enclosed_Office_NW_FloorT | 5.6561 | 1131.21 | 15 | 0.15 |  | 84.8408 | 169.6815 |  | 169.6815 | Office space/Occupancy Category - Office Buildings
Perimeter_Enclosed_Office_SW_FloorT | 5.0524 | 1010.49 | 15 | 0.15 |  | 75.7867 | 151.5735 |  | 151.5735 | Office space/Occupancy Category - Office Buildings
Perimeter_Enclosed_Office_SE_FloorT | 5.1674 | 1033.48 | 15 | 0.15 |  | 77.511 | 155.022 |  | 155.022 | Office space/Occupancy Category - Office Buildings
Core_Enclosed_Office_FloorT | 16.165 | 3233 | 15 | 0.15 |  | 242.475 | 484.95 |  | 484.95 | Office space/Occupancy Category - Office Buildings
Server_Room_FloorT | 0.627 | 418 | 15 | 0.15 |  | 9.405 | 62.7 |  | 62.7 | Telephone/data entry/Occupancy Category - Office Buildings
Mech/Elec_FloorT | 0 | 1070 | 15 | 0.15 |  | 0 | 160.5 |  | 160.5 | All Other
Conference_N_FloorT | 26.0634 | 789.8 | 15 | 0.15 |  | 390.951 | 118.47 |  | 390.951 | Conference/meeting/Occupancy Category - General
Conference_W_FloorT | 11.1025 | 336.44 | 15 | 0.15 |  | 166.5378 | 50.466 |  | 166.5378 | Conference/meeting/Occupancy Category - General
Conference_S_FloorT | 25.2054 | 763.8 | 15 | 0.15 |  | 378.081 | 114.57 |  | 378.081 | Conference/meeting/Occupancy Category - General
Conference_E_FloorT | 14.2956 | 433.2 | 15 | 0.15 |  | 214.434 | 64.98 |  | 214.434 | Conference/meeting/Occupancy Category - General
BreakRoom/FoodPrep_FloorT | 30.03 | 910 | 15 | 0.15 |  | 450.45 | 136.5 |  | 450.45 | Breakrooms/Occupancy Category - Office Buildings
Storage_FloorT | 0 | 738 | 15 | 0.15 |  | 0 | 110.7 |  | 110.7 | Occupiable storage rooms for dry materials/Occupancy Category - Office Buildings
Lobby/Lounge_FloorT | 10.26 | 684 | 15 | 0.15 |  | 153.9 | 102.6 |  | 153.9 | Breakrooms/Occupancy Category - Office Buildings
Restroom_FloorT | 0 | 1155 | 15 | 0.15 | 9* 50/70 (cfm/unit) | 0 | 173.25 | 450 | 450 | All Other
Stair/Elevator_FloorT | 0 | 848 | 15 | 0.15 |  | 0 | 127.2 |  | 127.2 | All Other
Corridor_W_FloorT | 5.0294 | 1005.88 | 15 | 0.15 |  | 75.441 | 150.882 |  | 150.882 | Corridors /Occupancy Category - General
Corridor_E_FloorT | 2.9268 | 585.36 | 15 | 0.15 |  | 43.902 | 87.804 |  | 87.804 | Corridors /Occupancy Category - General
Plenum_FloorT | 0 | 38352.97 | 15 |  |  | 0 | 0 |  | 0 | -
Background Data [To be deleted prior to publication]

## Water Heater
Water Heater - OfficeLarge
Vintage | WH Type | Efficiency | Number of WH | Tank Volume (gal) | Tank Loss | Source
Existing | Gas | 0.8 | 2 | See table below for each WH: col F is storage volume EACH of N identical heaters (N in B91). Plant total volume = col L. | See table below for each WH: col G is standby EACH of N identical heaters. Plant total UA = col N. | See table below for sources: Climate Zone Water Heater Sizing and Loss Coefficients
New Construction | Gas | 0.8 | 2 | See table below for each WH: col F is storage volume EACH of N identical heaters (N in B91). Plant total volume = col L. | See table below for each WH: col G is standby EACH of N identical heaters. Plant total UA = col N. | See table below for sources: Climate Zone Water Heater Sizing and Loss Coefficients
Peak Hot Water Consumption
Space Name | Baseline WH Type [T24, 2022, Appendix 5.4A , sheet: "2022 SpaceFuncData-Input"] | Total Area (ft²) | Number of People | Hot Water Usage Specification (gal/hr per person) [T24, 2022, Appendix 5.4A , sheet: "2022 SpaceFuncData-Input"] | Peak Hot Water Usage (gal/hr) | Peak Hot Water Usage (gal/min) | Note
Perimeter_Open_Office_N_Basement | Gas* | 8416.86 | 42.0843 | 0.18 | 7.5752 | 0.12625 | For space types marked with an asterisk (the ‘*’ symbol), the water‑heater type is listed as electric in Appendix 5.4A, sheet ‘2022 SpaceFuncData‑Input.’ However, we modified the value based on CEUS data, which indicates that gas is the primary fuel type.
Perimeter_Open_Office_S_Basement | Gas* | 3662.18 | 18.3109 | 0.18 | 3.296 | 0.054933
Core_Enclosed_Office_Basement | Gas* | 3703.68 | 18.5184 | 0.18 | 3.3333 | 0.055555
Server_Room_Basement | Gas* | 8228 | 41.14 | 0.18 | 7.4052 | 0.12342
Mech/Elec_Basement | Gas* | 7958 | 0 | 0.18 | 0 | 0
Conference_Basement | Gas* | 579.7 | 19.1301 | 0.09 | 1.7217 | 0.028695
BreakRoom/FoodPrep_Basement | Gas* | 973 | 32.109 | 0.09 | 2.8898 | 0.048164
Storage_Basement | Gas* | 1231 | 0 | 0 | 0 | 0
Restroom_Basement | Gas | 986 | 0 | 0 | 0 | 0
Lobby/Lounge_Basement | Gas | 707 | 10.605 | 0.09 | 0.95445 | 0.015908
Stair/Elevator_Basement | Gas* | 941 | 0 | 0 | 0 | 0
Corridor_W_Basement | Gas* | 703 | 3.515 | 0 | 0 | 0
Corridor_E_Basement | Gas* | 262.9 | 1.3145 | 0 | 0 | 0
Perimeter_Open_Office_N_FloorG | Gas* | 7131.29 | 35.6564 | 0.18 | 6.4182 | 0.10697
Perimeter_Open_Office_W_FloorG | Gas* | 5795.77 | 28.9789 | 0.18 | 5.2162 | 0.086937
Perimeter_Open_Office_E_FloorG | Gas* | 5875.49 | 29.3774 | 0.18 | 5.2879 | 0.088132
Perimeter_Enclosed_Office_NE_FloorG | Gas* | 917.38 | 4.5869 | 0.18 | 0.82564 | 0.013761
Perimeter_Enclosed_Office_NW_FloorG | Gas* | 1131.21 | 5.6561 | 0.18 | 1.0181 | 0.016968
Core_Enclosed_Office_FloorG | Gas* | 3312.28 | 16.5614 | 0.18 | 2.9811 | 0.049684
Server_Room_FloorG | Gas* | 417.09 | 0.62563 | 0.18 | 0.11261 | 0.0018769
Mech/Elec_FloorG | Gas* | 848.96 | 0 | 0.18 | 0 | 0
Conference_FloorG | Gas* | 789.81 | 26.0637 | 0.09 | 2.3457 | 0.039096
BreakRoom_FloorG | Gas* | 618.23 | 20.4016 | 0.09 | 1.8361 | 0.030602
FoodPrep_FloorG | Gas | 936.94 | 2.8108 | 0.578 | 1.6247 | 0.027078
Storage_FloorG | Gas | 959.03 | 0 | 0 | 0 | 0
Locker_FloorG | Gas | 1765.23 | 17.6523 | 0.578 | 10.203 | 0.17005
Lobby_S_FloorG | Gas* | 3360.63 | 33.6063 | 0.09 | 3.0246 | 0.050409
Lobby/Lounge_FloorG | Gas | 683.9 | 10.2585 | 0.09 | 0.92326 | 0.015388
Restroom_FloorG | Gas | 1156.09 | 0 | 0 | 0 | 0
Stair/Elevator_FloorG | Gas* | 848.01 | 0 | 0 | 0 | 0
Corridor_W_FloorG | Gas* | 1005.87 | 5.0293 | 0 | 0 | 0
Corridor_E_FloorG | Gas* | 798.76 | 3.9938 | 0 | 0 | 0
Plenum_FloorG |  | 38352.97 | 0 | 0 | 0 | 0
Perimeter_Open_Office_N_FloorM | Gas* | 71312.9 | 356.5645 | 0.18 | 64.1816 | 1.0697
Perimeter_Open_Office_S_FloorM | Gas* | 52373.7 | 261.8685 | 0.18 | 47.1363 | 0.78561
Perimeter_Open_Office_E_FloorM | Gas* | 44704.4 | 223.522 | 0.18 | 40.234 | 0.67057
Perimeter_Open_Office_W_FloorM | Gas* | 44487.6 | 222.438 | 0.18 | 40.0388 | 0.66731
Perimeter_Enclosed_Office_NE_FloorM | Gas* | 9173.8 | 45.869 | 0.18 | 8.2564 | 0.13761
Perimeter_Enclosed_Office_NW_FloorM | Gas* | 11312.1 | 56.5605 | 0.18 | 10.1809 | 0.16968
Perimeter_Enclosed_Office_SW_FloorM | Gas* | 10104.9 | 50.5245 | 0.18 | 9.0944 | 0.15157
Perimeter_Enclosed_Office_SE_FloorM | Gas* | 10334.8 | 51.674 | 0.18 | 9.3013 | 0.15502
Core_Enclosed_Office_FloorM | Gas* | 32330 | 161.65 | 0.18 | 29.097 | 0.48495
Server_Room_FloorM | Gas* | 4180 | 6.27 | 0.18 | 1.1286 | 0.01881
Mech/Elec_FloorM | Gas* | 10700 | 0 | 0.18 | 0 | 0
Conference_N_FloorM | Gas* | 7898 | 260.634 | 0.09 | 23.4571 | 0.39095
Conference_W_FloorM | Gas* | 3364.4 | 111.0252 | 0.09 | 9.9923 | 0.16654
Conference_S_FloorM | Gas* | 7638 | 252.054 | 0.09 | 22.6849 | 0.37808
Conference_E_FloorM | Gas* | 4332 | 142.956 | 0.09 | 12.866 | 0.21443
Break/FoorPrep_FloorM | Gas* | 9100 | 300.3 | 0.09 | 27.027 | 0.45045
Storage_FloorM | Gas* | 7380 | 0 | 0 | 0 | 0
Lobby/Lounge_FloorM | Gas | 6840 | 102.6 | 0.09 | 9.234 | 0.1539
Restroom_FloorM | Gas | 11550 | 0 | 0 | 0 | 0
Stair/Elevator_FloorM | Gas* | 8480 | 0 | 0 | 0 | 0
Corridor_W_FloorM | Gas* | 10058.8 | 50.294 | 0 | 0 | 0
Corridor_E_FloorM | Gas* | 5853.6 | 29.268 | 0 | 0 | 0
Plenum_FloorM |  | 383529.7 | 0 | 0 | 0 | 0
Perimeter_Open_Office_N_FloorT | Gas* | 7131.29 | 35.6564 | 0.18 | 6.4182 | 0.10697
Perimeter_Open_Office_S_FloorT | Gas* | 5237.37 | 26.1868 | 0.18 | 4.7136 | 0.078561
Perimeter_Open_Office_E_FloorT | Gas* | 4470.44 | 22.3522 | 0.18 | 4.0234 | 0.067057
Perimeter_Open_Office_W_FloorT | Gas* | 4448.76 | 22.2438 | 0.18 | 4.0039 | 0.066731
Perimeter_Enclosed_Office_NE_FloorT | Gas* | 917.38 | 4.5869 | 0.18 | 0.82564 | 0.013761
Perimeter_Enclosed_Office_NW_FloorT | Gas* | 1131.21 | 5.6561 | 0.18 | 1.0181 | 0.016968
Perimeter_Enclosed_Office_SW_FloorT | Gas* | 1010.49 | 5.0524 | 0.18 | 0.90944 | 0.015157
Perimeter_Enclosed_Office_SE_FloorT | Gas* | 1033.48 | 5.1674 | 0.18 | 0.93013 | 0.015502
Core_Enclosed_Office_FloorT | Gas* | 3233 | 16.165 | 0.18 | 2.9097 | 0.048495
Server_Room_FloorT | Gas* | 418 | 0.627 | 0.18 | 0.11286 | 0.001881
Mech/Elec_FloorT | Gas* | 1070 | 0 | 0.18 | 0 | 0
Conference_N_FloorT | Gas* | 789.8 | 26.0634 | 0.09 | 2.3457 | 0.039095
Conference_W_FloorT | Gas* | 336.44 | 11.1025 | 0.09 | 0.99923 | 0.016654
Conference_S_FloorT | Gas* | 763.8 | 25.2054 | 0.09 | 2.2685 | 0.037808
Conference_E_FloorT | Gas* | 433.2 | 14.2956 | 0.09 | 1.2866 | 0.021443
BreakRoom/FoodPrep_FloorT | Gas* | 910 | 30.03 | 0.58 | 17.4174 | 0.29029
Storage_FloorT | Gas* | 738 | 0 | 0 | 0 | 0
Lobby/Lounge_FloorT | Gas | 684 | 10.26 | 0.09 | 0.9234 | 0.01539
Restroom_FloorT | Gas | 1155 | 0 | 0 | 0 | 0
Stair/Elevator_FloorT | Gas* | 848 | 0 | 0 | 0 | 0
Corridor_W_FloorT | Gas* | 1005.88 | 5.0294 | 0 | 0 | 0
Corridor_E_FloorT | Gas* | 585.36 | 2.9268 | 0 | 0 | 0
Plenum_FloorT |  | 38352.97 | 0 | 0 | 0 | 0
Total | Gas storage |  |  |  | 484.0091 |  | Minimum peak hot water usage is 75 gal according to ACM 2025
Total | Electric resistance |  |  |  | 0
Number of identical gas storage WH | 2 | Since the total WH storage volume is more than the maximum size of the standard commercial gas storage WH listed in ENERGY STAR (193.7 gal > 125 gal). Therefore, two identical WH units were designed.
Total WH storage volume (gal) | 193.6036 | 2025 ACM §5.9.2
Maximum size of the standard commercial gas storage WH (gal) | 125 | ENERGY STAR commercial gas storage. The link is provided at the Notes tab.
Design supply temperature (°F) | 135 | Title 24 2022 Reference Appendices, Appendix 5.4B
WH system factor | 0.6 | 2025 ACM §5.9.2 Rated Capacity
Water mass conversion (lb/gal) | 8.2877 | 2025 ACM §5.9.2 Rated Capacity
Reheat multiplier | 0.4 | 2025 ACM §5.9.2 Storage Volume
Climate Zone Water Heater Sizing and Loss Coefficients (Individual WH)
Water Heater Name | Climate Zone | Minimum Monthly Mains Temp (°F) [T24 2022 - Appendix 5.4B] | Heat Output (Btu/hr) [ACM, 2025, 5.9.2: Rated capacity section] | WH Capacity (Btu/hr) [ACM, 2025, 5.9.2: Rated capacity section] | Required Energy Input each (Btu/hr) | Storage Volume each (gal) | Standby Loss [Title 20, §1605.1 Table F-4; Appendix B: Water Heating Calculation Method] |  | Off/On Cycle Loss Coefficient to Ambient Temp |  | Source/Note | Plant total volume (gal) | Plant total input (Btu/hr) | Plant total UA (Btu/h·°F)
WH_OfficeLarge | CZ01 | 47.9 | 174693.0726 | 104815.8436 | 145000 | 100 | 1281.25 | Btu/hr | 18.3036 | Btu/h·°F | No listed ~200 gal unitary gas storage WH: ENERGY STAR commercial gas storage and the Grainger tanks in this catalog max out at 125 gal (E139). AO Smith 140–2500 gal units in that size class are unfired storage tanks, not unitary water heaters, and were not added. ACM §5.9.2 plant volume is ~194 gal, so the scorecard uses N identical catalog heaters (B91). E/F/G/I are per heater. L/M/N are plant totals (N × each). Title 20 Table F-4 G = E/800+110×√F applies per tank. | 200 | 290000 | 36.6071
WH_OfficeLarge | CZ02 | 50.8 | 168876.6557 | 101325.9934 | 130000 | 100 | 1262.5 | Btu/hr | 18.0357 | Btu/h·°F |  | 200 | 260000 | 36.0714
WH_OfficeLarge | CZ03 | 52.2 | 166068.7303 | 99641.2382 | 125000 | 100 | 1256.25 | Btu/hr | 17.9464 | Btu/h·°F |  | 200 | 250000 | 35.8929
WH_OfficeLarge | CZ04 | 52.7 | 165065.8998 | 99039.5399 | 125000 | 100 | 1256.25 | Btu/hr | 17.9464 | Btu/h·°F |  | 200 | 250000 | 35.8929
WH_OfficeLarge | CZ05 | 51.6 | 167272.1269 | 100363.2761 | 130000 | 100 | 1262.5 | Btu/hr | 18.0357 | Btu/h·°F |  | 200 | 260000 | 36.0714
WH_OfficeLarge | CZ06 | 56.8 | 156842.6897 | 94105.6138 | 120000 | 100 | 1250 | Btu/hr | 17.8571 | Btu/h·°F |  | 200 | 240000 | 35.7143
WH_OfficeLarge | CZ07 | 58.4 | 153633.6321 | 92180.1793 | 120000 | 100 | 1250 | Btu/hr | 17.8571 | Btu/h·°F |  | 200 | 240000 | 35.7143
WH_OfficeLarge | CZ08 | 58.4 | 153633.6321 | 92180.1793 | 120000 | 100 | 1250 | Btu/hr | 17.8571 | Btu/h·°F |  | 200 | 240000 | 35.7143
WH_OfficeLarge | CZ09 | 57.6 | 155238.1609 | 93142.8966 | 120000 | 100 | 1250 | Btu/hr | 17.8571 | Btu/h·°F |  | 200 | 240000 | 35.7143
WH_OfficeLarge | CZ10 | 57.1 | 156240.9914 | 93744.5949 | 120000 | 100 | 1250 | Btu/hr | 17.8571 | Btu/h·°F |  | 200 | 240000 | 35.7143
WH_OfficeLarge | CZ11 | 50.5 | 169478.354 | 101687.0124 | 130000 | 100 | 1262.5 | Btu/hr | 18.0357 | Btu/h·°F |  | 200 | 260000 | 36.0714
WH_OfficeLarge | CZ12 | 51.4 | 167673.2591 | 100603.9555 | 130000 | 100 | 1262.5 | Btu/hr | 18.0357 | Btu/h·°F |  | 200 | 260000 | 36.0714
WH_OfficeLarge | CZ13 | 51.7 | 167071.5608 | 100242.9365 | 130000 | 100 | 1262.5 | Btu/hr | 18.0357 | Btu/h·°F |  | 200 | 260000 | 36.0714
WH_OfficeLarge | CZ14 | 50.1 | 170280.6184 | 102168.371 | 130000 | 100 | 1262.5 | Btu/hr | 18.0357 | Btu/h·°F |  | 200 | 260000 | 36.0714
WH_OfficeLarge | CZ15 | 63.2 | 144006.4594 | 86403.8756 | 120000 | 100 | 1250 | Btu/hr | 17.8571 | Btu/h·°F |  | 200 | 240000 | 35.7143
WH_OfficeLarge | CZ16 | 41.4 | 187729.869 | 112637.9214 | 145000 | 100 | 1281.25 | Btu/hr | 18.3036 | Btu/h·°F |  | 200 | 290000 | 36.6071
Market data
Catalog gas input (Btu/h) | Input source | Elec resistance tank (kW) | Elec resistance (Btu/h) | Catalog gas tank (gal) | Tank source | Elec tank (gal) | Elec tank source | Sources and links → Note tab
60000 | Grainger | 1.5 | 5118 | 34 | ENERGY STAR | 6 | Grainger
75100 | Grainger | 2 | 6824 | 35 | Grainger | 10 | Grainger
76000 | Both | 3 | 10236 | 48 | Grainger | 15 | Grainger
80000 | Grainger | 4.5 | 15355 | 50 | Both | 20 | Grainger
99900 | ENERGY STAR | 6 | 20473 | 55 | ENERGY STAR | 28 | Grainger
100000 | Both | 8 | 27297 | 60 | ENERGY STAR | 30 | Grainger
120000 | ENERGY STAR | 9 | 30709 | 65 | Both | 36 | Grainger
125000 | Both | 10 | 34121 | 72 | Grainger | 40 | Grainger
130000 | Both | 12 | 40946 | 75 | Both | 47 | Grainger
145000 | ENERGY STAR | 12.1 | 41287 | 76 | Grainger | 50 | Grainger
150000 | ENERGY STAR | 18 | 61419 | 80 | Both | 65 | Grainger
156000 | Grainger | 24 | 81891 | 82 | Grainger | 80 | Grainger
160000 | Both | 27 | 92128 | 85 | Grainger | 85 | Grainger
175000 | ENERGY STAR | 36 | 122837 | 90 | Both | 105 | Grainger
180000 | Grainger | 54 | 184256 | 91 | Grainger | 120 | Grainger
199000 | ENERGY STAR |  |  | 100 | Both
199900 | Both |  |  | 110 | ENERGY STAR
200000 | ENERGY STAR |  |  | 119 | Both
250000 | Both |  |  | 125 | ENERGY STAR
251000 | ENERGY STAR
270000 | Grainger
285000 | ENERGY STAR
300000 | Both
320000 | ENERGY STAR
360000 | Grainger
398000 | ENERGY STAR
399000 | ENERGY STAR
399900 | Both
499900 | Grainger
550000 | Grainger
715000 | Grainger

## Interior Lights
Interior Lighting - OfficeLarge
Space Type | New Construction |  |  | Existing |  |  | Note
| LPD (W/ft²) | Additional LPD for Portable Lighting (W/ft²) | Source | LPD (W/ft²) | Additional LPD for Portable Lighting (W/ft²) | Source
Office Area (>250 square feet) | 0.6 | 0.1 | T24, part 6, 2025, Table 140.6 C IT Room Source: ASHRAE 90.1 2022, Table 9.5.2.1-1, computer room space type | 0.75 | - | T24, part 6, 2013, Table 140.6 C IT Room Source: ASHRAE 90.1 2013, TABLE9.6.1, computer room space type | It is assumed that 50% of the additional allowance lighting is in use.
Convention, Conference, Multipurpose and Meeting Area | 0.75 |  |  | 1.4
Lobby, Main Entry | 0.7 | 0.25 |  | 1.5 | 0.5
Locker Room | 0.45 |  |  | 0.8
Storage (General) | 0.4 |  |  | 0.6
Electrical, Mechanical, Telephone Rooms | 0.4 |  |  | 0.7
Server Room (EPD 45) | 1.1 |  |  | 1.1
Computer Room (EPD 20) | 0.75 |  |  | 1.71
Restrooms | 0.65 |  |  | 0.65
Lounge, Breakroom, or Waiting Area | 0.55 | 0.125 |  | 1,1 | 0.25 |  | It is assumed that 50% of the additional allowance lighting is in use.
Kitchen/Food Preparation Area | 0.95 |  |  | 1.6
Stairwell | 0.6 |  |  | 0.6
Corridor Area | 0.4 |  |  | 0.6
Plenum
Whole Building method
| 2025 | 2013
LPD for Office Building ((W/ft²) | 0.6 | 0.8 | Ref: T24, Table 140.6 B
Background Data [To be deleted prior to publication]

## Ext Lighting
Exterior Lighting - OfficeLarge
Motion Controlled Luminaires (W) | Non-motion Controlled Luminaires (W) | Total (W) | Source
15580.7514 | 1548.9949 | 17129.7463 | Title 24, 2022
Exterior Lighting
Items (Assume LZ2) | Assumptions [2019 Outdoor Lighting CASE Report & PNNL 90.1-2010 TSD] |  | Unit | Lighting Power Allowance [T24, 2025, Table 140.7-A & 140.7-B] | Unit | Exterior Lighting Power (W)
IWA (Initial Wage Allowance) |  |  |  | 200 | (W) | 200
Parking area | 400 ft² for every parking space [2019 Lighting CASE report, Appendix H] 1 parking space per 250 ft² of gross building area [2019 Lighting CASE report, Table 38] | 797702.704 | (ft²) | 0.019 | (W/ft²) | 15156.3514
Building Entrance | 4 building entrance (1 per 10,000 ft² footprint) | 4 | (count) | 15 | (W/ea) | 60
Hardscape Ornamental Light | 0.1 ft² per 1 ft² of gross building area [2019 Lighting CASE report, Table 36] | 49856.419 | (ft²) | 0.007 | (W/ft²) | 348.9949
Building façade | 0.1 W per ft² of facade area Façade Area* = Perimeter × 0.5 × 30 ft (30 ft is the max height that is lit) The 0.5 factor assumes that only half of the perimeter walls are lit. -Formula is developed based on the 2019 Outdoor Lighting CASE report | 12000 | (ft²) | 0.1 | (W/ft²) | 1200
Non-sales canopy | According to the geometry (dimensions bellow) | 1200 | (ft²) | 0.137 | (W/ft²) | 164.4
Motion controlled Luminaires | [5 empty] | 15580.7514
Non-motion-controlled Luminaires | [5 empty] | 1548.9949
Total | [5 empty] | 17129.7463
*Developed based on 2019 Outdoor Lighting CASE Report
|  | Canopy | Size | Area
Perimeter (ft) | 800 | Lobby_S_FloorG | 40 ft × 15 ft | 600 ft²
Total floor area (ft²) | 498564.19 | Conference_FloorG | 30 ft × 12 ft | 360 ft²
Floors (above ground) | 12 | FoodPrep south | 15 ft × 8 ft | 120 ft²
Floors (all) | 13 | FoodPrep east | 15 ft × 8 ft | 120 ft²
|  | Total |  | 1,200 ft²

## Equipment
Equipment - OfficeLarge
Space Type | Plug load Power Density (W/ft²) | Gas Power Density (Btu/hr-ft²) | Refrigeration Power Density (W/ft²) | Source
Office Area (>250 square feet) | 0.7 |  |  | "Proposed Updates to Equipment Power Densities and Schedules in the 2028 Energy Code Nonresidential and Multifamily Alternative Calculation Method (NRMFACM) Reference Manual", August 7, 2025
Server Room (EPD 45) | 45 |  |  | PNNL ASHRAE 90.1 2022
Computer Room (EPD 20) | 20 |  |  | Based on PNNL ASHRAE 90.1 2022 assumptions and minimum load for computer room
Electrical, Mechanical, Telephone Rooms | 0.5 |  |  | T24 2022 - Appendix 5.4A
Lounge, Breakroom, or Waiting Area | 1
Convention, Conference, Multipurpose and Meeting Area | 1
Storage (General) | 0.2
Locker Room | 0.5
Kitchen/Food Preparation Area | 1.5
Lobby, Main Entry | 0.5
Restrooms | 0
Stairwell | 0
Corridor Area | 0
Plenum | 0
OfficeLarge prototype is assumed to have a transformer, and its losses will be explicitly modeled.
Elevator
Vintage | Class | Number of elevators (ne) | Cab Lighting Power Limit (W/ft2) | Fan Power Limit (W/CFM) | Cab Ventilation Fan & Lighting Shutoff | Design Motor Load (W) | Fan Load (W) | Lighting Load (W) | Total (W) | Note
Existing | F/G | 12 | 1.14 | 0.33 | When stopped and unoccupied with doors closed for over 15 minutes, cab interior lighting and ventilation shall be de-energized until required for operation. | 109218.18 | 990 | 409.03 | 110617.21 | Design load is calculated according to ISO 25745-2 method using Class F/G. Cab lighting and fan requirements are based on ASHRAE 90.1 2013.
New Construction | E | 12 | 0.6 | 0.33 | When the elevator cab is stopped and unoccupied with doors closed for over 15 minutes, the cab interior lighting and ventilation fans shall be switched off until elevator cab operation resumes. | 67919.52 | 990 | 215.28 | 69124.8 | Design load is calculated according to ISO 25745-2 method using Class E. Cab lighting and fan requirements are based on T24 2025 §120.6 (f).
Large Office Elevator Calculations
Symbol | Definition | Value | Units | Source
E | Annual energy consumption of the elevator - Existing | 541612.96 | kWh/year | Calculated
| Annual energy consumption of the elevator - New Construction | 336812.92 | kWh/year | Calculated
C1 | Running-energy coefficient | 3.65 for Class E; 5.47 for Class F | Coefficient | ISO 25745-2 Table 7
C2 | Idle/standby coefficient | 800 for Class E; 1,600 for Class F | Coefficient | ISO 25745-2 Table 7
Q | Rated load of elevator | 1361 | kg | Assumed for all prototypes
Elevator Size | Cab floor area | 29.9 | ft^2 | W=6.781 ft, L=4.406 ft; assumed based on representative manufacturer
CFM | Cab fan airflow | 250 | cfm | Assumed for multifamily and commercial prototypes
cat | Usage category | 4 | - | ISO 25745-2 Table A.1
d | Operating days per year | 260 | days/year | ISO 25745-2 Table A.1
nf | Number of floors | 13 | floors | Prototype assumptions
h | Floor-to-floor height | 3.96 | m | Prototype assumptions
v | Elevator lift speed | 2.5 | m/s | ISO 25745-2 Table A.1
nd | Number of trips per day | 750 | trips/day | ISO 25745-2 Table A.1
S_pct | Percent of average travel distance | 0.44 | % | ISO 25745-2 Table 2
a | Acceleration | 1 | m/s^2 | Annex B of ISO 25745-2
j | Jerk | 1.25 | m/s^3 | Annex B of ISO 25745-2
td | Door time | 8 | seconds | Annex B of ISO 25745-2
S_av | Average distance traveled per trip | 22.65 | m/trip | Calculated (nf * h * S_pct)
t_av | Average trip time | 20.36 | seconds/trip | Calculated (S_av/v + v/a + a/j + td)
t_nr | Time not running per day | 19.76 | hours/day | Calculated (24 - nd * t_av)
Standby Hours | Annual standby hours | 7657.14 | hours/year | Calculated (24*(365-d)+t_nr*d)
Total light level | Total light level | 40 | lm/ft2 | PNNL Prototypes
EFLH | Equivalent full load hours | 4959 | hours | Calculated using the elevator schedule

## Schedules
Schedules - OfficeLarge
Zone | Schedule Category | Schedule | Source | Type | Hour
[5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
All zones except for Server Rooms, Storage, Stairway, and Mechanical_Electrical | Office | Occupancy | T24 2022 - Appendix 5.4B, [Office] Updated base on Plug load and schedules project with CEC, 2025 | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
All zones except for Server Rooms, Storage, Stairway, and Mechanical_Electrical | Office | Lights | T24 2022 - Appendix 5.4B, [Office] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.35 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
All zones except for Server Rooms, Storage, Stairway, and Mechanical_Electrical | Office | ElecEquipment | Plug load and schedules project with CEC, 2025 | Weekday | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.74 | 0.87 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.5 | 0.45 | 0.45 | 0.45
|  |  |  | Saturday | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43
|  |  |  | Sunday | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43
All zones except for Server Rooms, Storage, Stairway, and Mechanical_Electrical | Office | HVACAvail | T24 2022 - Appendix 5.4B, [Office] Updated base on Plug load and schedules project with CEC, 2025 | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
All zones except for Server Rooms, Storage, Stairway, and Mechanical_Electrical | Office | ServiceHotWater | T24 2022 - Appendix 5.4B, [Office] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05
|  |  |  | Saturday | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04
|  |  |  | Sunday | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04
All zones except for Server Rooms, Storage, Stairway, and Mechanical_Electrical | Office | Infiltration | T24 2022 - Appendix 5.4B, [Office] Updated base on Plug load and schedules project with CEC, 202 | Weekday | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
All zones except for Server Rooms, Storage, Stairway, and Mechanical_Electrical | Office | HtgSetpt |  | Weekday | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
|  |  |  | Saturday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  |  | Sunday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
All zones except for Server Rooms, Storage, Stairway, and Mechanical_Electrical | Office | ClgSetpt |  | Weekday | 85* | 85* | 85* | 85* | 85* | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
|  |  |  | Saturday | 85* | 85* | 85* | 85* | 85* | 85* | 85* | 85* | 85* | 85* | 85* | 85* | 85* | 85* | 85* | 85* | 85* | 85* | 85* | 85* | 85* | 85* | 85* | 85*
|  |  |  | Sunday | 85* | 85* | 85* | 85* | 85* | 85* | 85* | 85* | 85* | 85* | 85* | 85* | 85* | 85* | 85* | 85* | 85* | 85* | 85* | 85* | 85* | 85* | 85* | 85*
Data
Server rooms | Data | Occupancy | T24 2022 - Appendix 5.4B, [Data] Updated base on office schedule | Weekday | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.25 | 0.65 | 0.65 | 0.65 | 0.65 | 0.6 | 0.6 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.25 | 0.1 | 0.05 | 0.05 | 0.05 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0
Server rooms | Data | Lights | T24 2022 - Appendix 5.4B, [Data] Updated base on office schedule | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.7 | 0.8 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.8 | 0.35 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05
Server rooms | Data | HVACAvail | T24 2022 - Appendix 5.4B, [Data] | Weekday | bar: Hour 1 to Hour 24
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
Server rooms | Data | ServiceHotWater | T24 2022 - Appendix 5.4B, [Data] | Weekday | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.9 | 0.9 | 0.5 | 0.5 | 0.7 | 0.5 | 0.5 | 0.5 | 0.1 | 0.1 | 0.1 | 0.1 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Server rooms | Data | Infiltration | T24 2022 - Appendix 5.4B, [Data] | Weekday | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  |  | Saturday | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  |  | Sunday | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Server rooms | Data | ClgSetpt | Based on Activity level and thermostat setpoint | Weekday | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
|  |  |  | Saturday | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
|  |  |  | Sunday | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
Storage, Stairway, and Mechanical_Electrical
Storage, Stairway, and Mechanical_Electrical | Ancillary | Occupancy | T24 2022 - Appendix 5.4B, [Office] Updated base on office schedule | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
Storage, Stairway, and Mechanical_Electrical | Ancillary | Lights | T24 2022 - Appendix 5.4B, [Office] Updated base on office schedule | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.35 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Storage, Stairway, and Mechanical_Electrical | Ancillary | HVACAvail | T24 2022 - Appendix 5.4B, [Office] Updated base on office schedule | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Storage, Stairway, and Mechanical_Electrical | Ancillary | ServiceHotWater | T24 2022 - Appendix 5.4B, [Office] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05
|  |  |  | Saturday | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04
|  |  |  | Sunday | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04
Storage, Stairway, and Mechanical_Electrical | Ancillary | Infiltration | T24 2022 - Appendix 5.4B, [Office] | Weekday | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
Storage, Stairway, and Mechanical_Electrical | Ancillary | HtgSetpt | Engineering Judgement | Weekday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  |  | Saturday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  |  | Sunday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Storage, Stairway, and Mechanical_Electrical | Ancillary | ClgSetpt | Engineering Judgement | Weekday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
|  |  |  | Saturday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
|  |  |  | Sunday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
Other | [28 empty] | EFLH
| Building | Elevator | T24 2022 - Appendix 5.4B, [Office] Updated base on Plug load and schedules project with CEC, 202 | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 4959
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Building | ExtLightingNonMotionCtrl |  | Weekday | bar: Hour 1 to Hour 24
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
| Building | ExtLightingMotionCtrl |  | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Office | Building | FunctionalAreaPeopleActivityLevel | Based on Activity level schedules in CEC Prototypes | Weekday | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
|  |  |  | Saturday | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
|  |  |  | Sunday | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
Server room | Building | ComputerRoomPeopleActivityLevel | Based on Activity level schedules in CEC Prototypes | Weekday | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
|  |  |  | Saturday | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
|  |  |  | Sunday | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
Conference room | Building | MeetingAreaPeopleActivityLevel | Based on Activity level schedules in CEC Prototypes | Weekday | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2
|  |  |  | Saturday | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2
|  |  |  | Sunday | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2
Corridor, Stair, Lobby, Restroom, Mech, Storage, Break | Building | CommonAreaPeopleActivityLevel | Based on Activity level schedules in CEC Prototypes | Weekday | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5
|  |  |  | Saturday | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5
|  |  |  | Sunday | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5
Kitchen/Food prep | Building | KitchenPeopleActivityLevel | Based on Activity level schedules in CEC Prototypes | Weekday | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8
|  |  |  | Saturday | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8
|  |  |  | Sunday | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8
Locker | Building | LockerRoomPeopleActivityLevel | Based on Activity level schedules in CEC Prototypes | Weekday | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9
|  |  |  | Saturday | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9
|  |  |  | Sunday | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9
Background Data [To be deleted prior to publication]
Operating Schedule
| System Capacity fraction | Developed based on CEC and CEUS |  | Weekday
Saturday
Alternative HVAC System Operating
| Alternative HVAC System Operating | Developed based on CEC schedules and CEUS operating hours |  | Weekday
Saturday
Otherday
Weekday
Saturday
Otherday

## Energy Usage (hidden)
CalBEM Energy Consumption - OfficeLarge | [7 empty] | National Average (EnergyStar Portfolio Manager) |  |  |  |  | CEUS Energy Consumption - OfficeLarge
Prototype | CZ | CalBEM Electricity EUI (KBTU/ft²) | CalBEM Gas EUI (KBTU/ft²) | CalBEM Total EUI (KBTU/ft²) | New Construction Electricity EUI (KBTU/ft²) | New Construction Gas EUI (KBTU/ft²) | New Construction Total EUI (KBTU/ft²) | National Average | Acceptable Range (25% Higher) | Acceptable Range (25% Lower) | National Average Acceptable Range | Zip code | Prototype | CZ | Total Floorspace (Thousand of ft2) | CEUS 2022 Electric Energy Intensity (kWh/ft²) | CEUS 2022 Annual Gas Intensity (kWh/ft²) | CEUS 2022 Total EUI (kBtu/ft²) | Acceptable Range (25% Higher) | Acceptable Range (25% Lower) | CEUS 2022 Acceptable Range
HotelSmall | 1 | [6 empty] | 71.5 | 89.375 | 53.625 | 35.75 | 95521 | Large Office | 1 | 5279 | 16.7 | 5.01 | 74.0745 | 92.5932 | 55.5559 | 37.0373
| 2 | [6 empty] | 77.3 | 96.625 | 57.975 | 38.65 | 95476 |  | 2 | 12449 | 15.2 | 6.24 | 73.1533 | 91.4416 | 54.865 | 36.5766
| 3 | [6 empty] | 74 | 92.5 | 55.5 | 37 | 94612 |  | 3 | 242565 | 14.3 | 4.83 | 65.2716 | 81.5895 | 48.9537 | 32.6358
| 4 | [6 empty] | 79.5 | 99.375 | 59.625 | 39.75 | 93446 |  | 4 | 137610 | 14.4 | 4.76 | 65.3739 | 81.7174 | 49.0304 | 32.687
| 5 | [6 empty] | 71.4 | 89.25 | 53.55 | 35.7 | 93455 |  | 5 | 3834 | 8.6 | 9.32 | 61.143 | 76.4288 | 45.8573 | 30.5715
| 6 | [6 empty] | 80.8 | 101 | 60.6 | 40.4 | 93550 |  | 6 | 109980 | 10.9 | 4.88 | 53.8414 | 67.3017 | 40.381 | 26.9207
| 7 | [6 empty] | 76.7 | 95.875 | 57.525 | 38.35 | 92101 |  | 7 | 76710 | 14.8 | 9.36 | 82.4339 | 103.0424 | 61.8254 | 41.217
| 8 | [6 empty] | 77.6 | 97 | 58.2 | 38.8 | 92831 |  | 8 | 177013 | 10.4 | 4.24 | 49.9517 | 62.4396 | 37.4638 | 24.9758
| 9 | [6 empty] | 77.7 | 97.125 | 58.275 | 38.85 | 91505 |  | 9 | 240000 | 10.9 | 4.38 | 52.1354 | 65.1692 | 39.1015 | 26.0677
| 10 | [6 empty] | 78.1 | 97.625 | 58.575 | 39.05 | 92501 |  | 10 | 65927 | 11.9 | 7.21 | 65.2033 | 81.5041 | 48.9025 | 32.6017
| 11 | [6 empty] | 80.3 | 100.375 | 60.225 | 40.15 | 96080 |  | 11 | 18413 | 11.4 | 4.29 | 53.5343 | 66.9179 | 40.1507 | 26.7671
| 12 | [6 empty] | 79.6 | 99.5 | 59.7 | 39.8 | 95814 |  | 12 | 171620 | 14.4 | 6.12 | 70.0142 | 87.5178 | 52.5107 | 35.0071
| 13 | [6 empty] | 80 | 100 | 60 | 40 | 93721 |  | 13 | 19959 | 15.9 | 3.71 | 66.9093 | 83.6366 | 50.182 | 33.4547
| 14 | [6 empty] | 80.8 | 101 | 60.6 | 40.4 | 93550 |  | 14 | 18934 | 9.8 | 4.4 | 48.4504 | 60.563 | 36.3378 | 24.2252
| 15 | [6 empty] | 79.5 | 99.375 | 59.625 | 39.75 | 92262 |  | 15 | 23127 | 9.7 | 5.14 | 50.6341 | 63.2926 | 37.9756 | 25.317
| 16 | [6 empty] | 82.3 | 102.875 | 61.725 | 41.15 | 95715 |  | 16 | 39406 | 11.6 | 4.42 | 54.6602 | 68.3253 | 40.9952 | 27.3301
Ref: CEUS 2022 Report
And by applying FZ-CZ multipliers for converting FZ data to CZ data
Background Data [To be deleted prior to publication]

## Weights (hidden)
% of floor area per CZ and vintage bin - OfficeLarge
Prototype | CZ | Vintage Bin |  |  |  |  | Floor area distribution of CA office buildings (CEUS 2022)
|  | Pre-1978 | 1978-1997 | 1998-2007 | 2008-2018 |  | Office, Small | Office, Medium | Office, Large
OfficeSmall | 1 |  |  |  |  | 0% | 35.39% | 29.43% | 35.18%
| 2 |  |  |  |  | 0%
| 3 |  |  |  |  | 0%
| 4 |  |  |  |  | 0%
| 5 |  |  |  |  | 0%
| 6 |  |  |  |  | 0%
| 7 |  |  |  |  | 0%
| 8 |  |  |  |  | 0%
| 9 |  |  |  |  | 0%
| 10 |  |  |  |  | 0%
| 11 |  |  |  |  | 0%
| 12 |  |  |  |  | 0%
| 13 |  |  |  |  | 0%
| 14 |  |  |  |  | 0%
| 15 |  |  |  |  | 0%
| 16 |  |  |  |  | 0%
Statewide
Ref: CEUS 2022 dataset
Ref: Dodge 2023

## PV (hidden)
PV - OfficeLarge

## EV Charger (hidden)
EV Charger - OfficeLarge
Background Data [To be deleted prior to publication]

## Data (hidden)
Space Function | Electric Equipment Load Intensity | Electric Equipment Load Intensity | LPD
Aging Eye/Low-vision (Corridor Area) |  |  | 2013 | 2016 | 2019 | 2025
Aging Eye/Low-vision (Dining)
Aging Eye/Low-vision (Lobby, Main Entry)
Aging Eye/Low-vision (Lounge/Waiting Area)
Aging Eye/Low-vision (Multipurpose Room)
Aging Eye/Low-vision (Religious Worship Area)
Aging Eye/Low-vision (Restroom)
Aging Eye/Low-vision (Stairwell)
Audience Seating Area
Auditorium Area
Auto Repair / Maintenance Area
Barber, Beauty Salon, Spa Area
Civic Meeting Place Area
Classroom, Lecture, Training, Vocational Areas
Concourse and Atria Area
Convention, Conference, Multipurpose and Meeting Area
Copy Room
Corridor Area
Dining Area (Bar/Lounge and Fine Dining)
Dining Area (Cafeteria/Fast Food)
Dining Area (Family and Leisure)
Electrical, Mechanical, Telephone Rooms
Exercise/Fitness Center and Gymnasium Areas
Financial Transaction Area
Healthcare Facility and Hospitals (Exam/Treatment Room)
Healthcare Facility and Hospitals (Imaging Room)
Healthcare Facility and Hospitals (Medical Supply Room)
Healthcare Facility and Hospitals (Nursery)
Healthcare Facility and Hospitals (Nurse's Station)
Healthcare Facility and Hospitals (Operating Room)
Healthcare Facility and Hospitals (Patient Room)
Healthcare Facility and Hospitals (Physical Therapy Room)
Healthcare Facility and Hospitals (Recovery Room)
Hotel Function Area
Kitchen/Food Preparation Area
Kitchenette or Residential Kitchen
Laboratory, Scientific
Laundry Area
Library (Reading Area)
Library (Stacks Area)
Lobby, Main Entry
Locker Room
Lounge, Breakroom, or Waiting Area
Manufacturing, Commercial & Industrial Work Area (Low Bay)
Manufacturing, Commercial & Industrial Work Area (High Bay)
Manufacturing, Commercial & Industrial Work Area (Precision)
Museum Area (Exhibition/Display)
Museum Area (Restoration Room)
Office Area (>250 square feet)
Office Area (<250 square feet)
Parking Garage Area (Parking Zone and Ramps)
Parking Garage Area (Daylight Adaptation Zones)
Pharmacy Area
Retail Sales Area (Grocery Sales)
Retail Sales Area (Retail Merchandise Sales)
Retail Sales Area (Fitting Room)
Religious Worship Area
Restrooms
Stairwell
Storage, Commercial/Industrial (Warehouse)
Storage, Commercial/Industrial (Refrigerated)
Storage, Commercial/Industrial (Shipping & Handling)
Storage (General)
Sports Arena - Playing Area (> 5,000 Spectators)
Sports Arena - Playing Area (2,000 - 5,000 Spectators)
Sports Arena - Playing Area (< 2,000 Spectators)
Sports Arena - Playing Area (Recreational)
Theater Area (Motion Picture)
Theater Area (Performance)
Transportation Function (Baggage Area)
Transportation Function (Ticketing Area)
Videoconferencing Studio
High-Rise Residential Living Spaces
Hotel/Motel Guest Room
All other
Attic
Reception Area
Elevator
Plenum
IT Room (EPD 12)
Computer Room (EPD 20)
Server Room (EPD 45)