## Notes
Data Sources
Dataset | Dodge 2023
| Commercial End-Use Survey (CEUS) 2022 | https://www.energy.ca.gov/publications/2023/2022-california-commercial-end-use-survey-ceus-final-report
| Commercial Buildings Energy Consumption Survey (CBECS) 2018 | https://www.eia.gov/consumption/commercial/data/2018/index.php?view=microdata
| Comstock 2023 | https://data.openei.org/s3_viewer?bucket=oedi-data-lake&prefix=nrel-pds-building-stock%2Fend-use-load-profiles-for-us-building-stock%2F2023%2Fcomstock_amy2018_release_2%2Fmetadata_and_annual_results%2Fby_state%2Fstate%3DCA%2F
Prototype | California Energy Commission (CEC) Medium Office prototype (CBECC 2022.3.1) | https://bees.noresco.com/software2022.html
| Pacific Northwest National Laboratory (PNNL) Medium Office prototype (90.1-2022) | https://www.energycodes.gov/prototype-building-models#Commercial
| Database for Energy Efficient Resources (DEER) Large Office prototype (June 2023) | https://github.com/sound-data/DEER-Prototypes-EnergyPlus
| Oak Ridge National Laboratory (ORNL) 2019 Medium Office prototype zoning | https://web.eecs.utk.edu/~jnew1/publications/2019_IBPSA_OpenStudioOffice.pdf
Codes | Title 24, part 6, referred to as T24 (1984, 1992,1998, 2001, 2005, 2008, 2013, 2016,2019, 2022, 2025) | https://www.energy.ca.gov/publications/2025/2025-building-energy-efficiency-standards-residential-and-nonresidential | 2025
|  | https://codes.iccsafe.org/codes/united-states/california | 2010+
| Title 20 | https://govt.westlaw.com/calregs/Document/I270DCA634B4011EFA8F7F119BAF97AD6?viewType=FullText&originationContext=documenttoc&transitionType=CategoryPageItem&contextData=(sc.Default)
| American Society of Heating, Refrigerating and Air-Conditioning Engineers (ASHRAE) 90.1 (2022) | https://www.ashrae.org/technical-resources/standards-and-guidelines/read-only-versions-of-ashrae-standards
| Code of Federal Regulations (CFR) Title 10 ( 2024) | https://www.govinfo.gov/content/pkg/CFR-2024-title10-vol3/pdf/CFR-2024-title10-vol3-part431-subpartF.pdf
| Alternative Calculation Method (ACM) (2022) | https://www.energy.ca.gov/publications/2022/2022-nonresidential-and-multifamily-alternative-calculation-method-reference
| ACM (2025) | https://www.energy.ca.gov/publications/2025/2025-nonresidential-and-multifamily-alternative-calculation-method-reference
| Nonres ACM 2022, Appendix 5.4A and Appendix 5.4B | https://www.energy.ca.gov/publications/2022/2022-nonresidential-and-multifamily-alternative-calculation-method-reference
| 2022 Reduced infiltration Codes and Standards Enhancement (CASE) report | https://title24stakeholders.com/wp-content/uploads/2020/10/2022-T24-Final-CASE-Report_Reduce-Infiltration.pdf
| 2019 Outdoor Lighting CASE Report | https://title24stakeholders.com/wp-content/uploads/2016/10/T24-2019-CASE-Study-Results-Report-Outdoor-Sources_Final_with-Attachments.pdf
| PNNL 20405, 2011 | https://www.pnnl.gov/main/publications/external/technical_reports/PNNL-20405.pdf
| Air leakage Memo, NORESCO, 2025 | Infiltration_rate_report_14May2025-Short-Version.docx
| Yousefi, F., Athalye, R., (2025), "Determining Vintage Bins for Prototype Development: An Analysis of California Commercial Buildings," ASHRAE Annual Conference | https://www.thefreelibrary.com/Determining+Vintage+Bins+for+Prototype+Development%3a+An+Analysis+of...-a0879271125
| Proposed Updates to Equipment Power Densities and Building Schedules for the 2028 Energy Code, referred to as "Plug load and schedules project with CEC, 2025" (Docket Number =25-BSTD-03 & TN=265693) | https://efiling.energy.ca.gov/GetDocument.aspx?tn=265693&DocumentContentId=102545
| Yousefi, F., Athalye, R. (2026). "Developing a New Set of Prototypical Models for Office Buildings in California," IBPSA-USA Conference | https://publications.ibpsa.org/conference/paper/?id=simbuild2026_1372
| ENERGY STAR certified commercial water heaters | https://www.energystar.gov/productfinder/product/certified-commercial-water-heaters/results?fuel_filter=Gas&markets_filter=United+States
| Grainger gas tank water heaters (sizes below commercial, e.g. 30–75 kBtu/h) | https://www.grainger.com/category/plumbing/water-heaters/gas-tank-water-heaters
| Grainger electric tank water heaters | https://www.grainger.com/category/plumbing/water-heaters/electric-tank-water-heaters
Construction Rate
[5 empty] | 1978-84 | 1985-97 | 1992-1997
|  |  |  | Construction rate (Dodge 2023 data for new medium offices) | 46.19% | 53.81% | 12.39%
Source:Dodge Construction Data, 2023 ( NEW medium office built after 1967) (STC refers to building types in Dodge terminology).
Notes
OfficeMedium Prototype | The Medium Office prototype was developed to represent California office buildings between 25,000 and 150,000 ft². Based on California construction data, the existing CEC/PNNL Medium Office geometry was retained because it aligned well with observed building stock characteristics. The prototype is modeled as a three-story building with a total floor area of 53,628 ft². Its zoning layout was updated using ORNL-based layouts, with modifications to better reflect current design practice and simplify the model. These changes included consolidating spaces, reducing the total number of thermal zones, and incorporating elevator space into the vertical circulation area. The resulting Medium Office prototype includes approximately 61.8% office space, 6.2% conference space, 5.5% storage, 9% corridor, 5.9% lobby, 3.6% restroom, 3.7% stair/elevator area, and for other 4.3% (server room, mechanical room, breakroom). The same geometry and zoning layout are applied across vintages and California climate zones. Information about the geometry and underlying logic of the office prototypes can be found in this paper: Yousefi, F., Athalye, R. (2026). ‘Developing a New Set of Prototypical Models for Office Buildings in California.’ IBPSA-USA Conference. The link is provided above in the Data Source section. The floor area was slightly modified in some spaces during the geometry‑drawing phase.
1986 is the representative year for the 1984-1997 vintage bin | Most medium offices in this vintage bin were built after 1984 (more than 54% ) and the CA energy code did not noticeably changed between 1984 to 1992) . Edition 1986 included 6 prescriptive packages per CZ for office buildings compared to 1984 with 3 packages per CZ. Also "Heat Capacity" for external wall is considered between 10.0 to 14.99 (BTU/F/ft2) Package A was selected for the thermal properties Medium office was considered as low rise office
2001 is the representative year for the 1998-2007 vintage bin | Wall and roof prescriptive criteria from 1998 to 2005 remain unchanged except for CZ2 and 6 in 2001 version (the percentage of change is less than 10%). Since the construction rate between 1998-2005 is greater than the 2006-2007 period, the envelope properties of 1998 -2005 were chosen for envelope properties. The windows requirement considerably changed in the 2001 code and makes this year (2001) as the nominated year for this vintage. It should be noticed that, only one Title 24 should be chosen within each vintage bin for building envelope properties since the entire envelope is built at once. We can't choose 1998 for walls and 2001 for windows. Wall and roof prescriptive criteria from 1998 to 2005 remain unchanged except for CZ2 and 6 in 2001 version (the percentage of change is less than 10%).
2013 is the representative year for the 2008-2018 vintage bin | Wall properties remain unchanged from the 2008 code to the 2016 code but the roof did changed. Although the 2016 code introduced improvement for roof in nearly all CZ and for wall in a few CZ, and construction activity surged between 2017 and 2018, the extende period from 2008 to 2016 resulted in a higher construction rate during that time . As a result, it was decided to select the code that was effective during 2008-2016. The 2013 code modified the solar reflectance requirement for low-sloped roof products ( by approximately 15%), and enhanced window properties. Therefore, the 2013 code was chosen as the representative code. Additionally, construction activity from 2014-2018 was higher compared to 2008-2013 period.

## Prototype
NORESCO, Updated September 2026
OfficeMedium
Characteristic | Value | Data Sources
Building Type | Medium Office
Building Category | Nonresidential
Version | v2-0
Vintages | 4 Vintages: Pre-1978 , 1978-1997 ,1998-2007 , 2008-2018 New Construction (2019+) | Based on the vintage bin analysis. A summary of the findings is presented in the following paper, with a link provided in the Notes tab: Yousefi, F., Athalye, R. (2025). “Determining Vintage Bins for Prototype Development: An Analysis of California Commercial Buildings.” ASHRAE Annual Conference.
Shape |  | Assume rectangular shape; supported by CBECS, CEC, and PNNL. The windows have been updated from ribbon style to punched openings. The logic behind the geometry of the CalBEM Office prototypes' shell is described in the following paper, with a link provided in the Notes tab: Yousefi, F., & Athalye, R. (2026). "Developing a New Set of Prototypical Models for Office Buildings in California", IBPSA-USA Conference.
Total Floor Area (ft2) | 53,628 (163.7 ft x 109.2 ft) | Supported by Dodge 2023 data (Same as CEC and PNNL)
Aspect Ratio | 1.5 | Assumption; same as CEC and PNNL Medium Office prototype
Number of Floors | 3 | Supported by Dodge 2023 data (Same as CEC and PNNL) DEER doesn't offer medium office prototype
Roof type | Flat | Supported by CBECS 2018 data (Same as CEC and PNNL)
Window dimensions | 33% | Assumed based on CBECS data; same as CEC and PNNL Medium Office prototype. CBECS: 26-50% Comstock: 26% CEC prototype: 33% same as PNNL DEER: 33% for Large Office prototype | 3 ft from ground, 6*3 feet, 1 ft from ceiling, 2ft from each other.
Shading Geometry | No Shades | Assumption; same as CEC and PNNL Medium Office prototype
Floor to floor height (feet) | 13 | Assumption, standard ceiling height in office buildings; same as CEC and PNNL Medium Office prototype.
Floor to ceiling height (feet) | 9 (4 ft above-ceiling plenum) | Assumption; same as CEC and PNNL Medium Office prototype
Glazing sill height (feet) | 3.35 ft (top of the window is 7.64 ft high with 4.29 ft high glass) | Assumption; same as CEC and PNNL Medium Office prototype

## Zones
Proposed OfficeMedium | [14 empty] | Layout of Spcase (each space has its own thermal zone)
Building | Space/Thermal Zone | Space Type Primarily from [T24, 2022 Appendix 5.4A] - See Notes column | HVAC System Name Vintage 1&2 | HVAC System Name Vintage 3&4 | HVAC System Name New Construction | Schedule Category | Conditioned (Y/N) | Area Fraction | Area (ft²) | Volume (ft³) | Multipliers | Number of People | People (Persons/1,000 ft²) [T24, 2025,Table 120.1-A] | Notes
OfficeMedium | Open_Office_Core_FloorG | Office Area (>250 square feet) | CAV with Reheat_Core | PVAV_FloorG | VRF System_FloorG + DOAS | Office | Yes | 7.986% | 4283 | 38547 | 1 | 21.415 | 5
OfficeMedium | Open_Office_N_FloorG | Office Area (>250 square feet) | CAV with Reheat_North | PVAV_FloorG | VRF System_FloorG + DOAS | Office | Yes | 4.285% | 2297.9873 | 20681.8859 | 1 | 11.4899 | 5
OfficeMedium | Enclosed_Office_W_FloorG | Office Area (>250 square feet) | CAV with Reheat_West | PVAV_FloorG | VRF System_FloorG + DOAS | Office | Yes | 3.054% | 1637.8612 | 14740.7504 | 1 | 8.1893 | 5
OfficeMedium | Enclosed_Office_E_FloorG | Office Area (>250 square feet) | CAV with Reheat_East | PVAV_FloorG | VRF System_FloorG + DOAS | Office | Yes | 3.054% | 1637.8612 | 14740.7504 | 1 | 8.1893 | 5
OfficeMedium | Open_Office_S_FloorG | Office Area (>250 square feet) | CAV with Reheat_South | PVAV_FloorG | VRF System_FloorG + DOAS | Office | Yes | 2.212% | 1186.2075 | 10675.8676 | 1 | 5.931 | 5
OfficeMedium | Conference_FloorG | Convention, Conference, Multipurpose and Meeting Area | CAV with Reheat_South | PVAV_FloorG | VRF System_FloorG + DOAS | Office | Yes | 2.073% | 1111.7798 | 10006.0183 | 1 | 36.6887 | 33 | Persons/1,000 ft²: ORNL: 54, T24:33
OfficeMedium | Lobby_FloorG | Lobby, Main Entry | CAV with Reheat_Core_Service | PVAV_FloorG | VRF System_FloorG + DOAS | Office | Yes | 1.975% | 1059.1755 | 9532.5792 | 1 | 10.5918 | 10 | For entrance lobbies, assumed 10 persons/1000 ft² based on ASHRAE 62.1 Table 6-1 T24 assumed 33 persons/1,000 ft² for main Entry lobbies & 5 persons/1000 ft² for reception area
OfficeMedium | Storage_FloorG | Storage (General) | CAV with Reheat_Core_Service | PVAV_FloorG | VRF System_FloorG + DOAS | Ancillary | Yes | 1.833% | 983.1561 | 8848.405 | 1 | 0 | - | Occupant load density for storage is based on T24, 2025, Appendix 5.4A. Conditioned but with higher cooling setpoint
OfficeMedium | Mechanical/Electrical_FloorG | Electrical, Mechanical, Telephone Rooms | CAV with Reheat_Core_Service | PVAV_FloorG | VRF System_FloorG + DOAS | Ancillary | Yes | 0.6663% | 357.3503 | 3216.1531 | 1 | 0 | - | Conditioned but with higher cooling setpoint
OfficeMedium | IT-Room_FloorG | IT Room (EPD 12) | CAV with Reheat_Core_Service | PVAV_FloorG | VRF System_FloorG + DOAS | Data | Yes | 0.3337% | 178.9373 | 1610.4357 | 1 | 0.26841 | 1.5 | Nonres ACM 2025, Appendix 5.4A
OfficeMedium | Restroom_FloorG | Restrooms | CAV with Reheat_Core_Service | PVAV_FloorG | VRF System_FloorG + DOAS | Office | Yes | 1.2% | 643.5778 | 5792.2004 | 1 | 0 | -
OfficeMedium | BreakRoom/Kitchenette_FloorG | Lounge, Breakroom, or Waiting Area | CAV with Reheat_Core_Service | PVAV_FloorG | VRF System_FloorG + DOAS | Office | Yes | 0.4332% | 232.343 | 2091.0866 | 1 | 7.6673 | 33 | Number of People: T24: 33 for Breakroom
OfficeMedium | Stairway_FloorG | Stairwell | CAV with Reheat_Core_Service | PVAV_FloorG | VRF System_FloorG + DOAS | Ancillary | Yes | 1.233% | 661.3923 | 5952.5303 | 1 | 0 | - | Conditioned but with higher cooling setpoint
OfficeMedium | Corridor_W_FloorG | Corridor Area | CAV with Reheat_West | PVAV_FloorG | VRF System_FloorG + DOAS | Office | Yes | 0.5594% | 300 | 2700 | 1 | 1.5 | 5 |  |  | First Floor |  | Second and Third Floor
OfficeMedium | Corridor_N_FloorG | Corridor Area | CAV with Reheat_North | PVAV_FloorG | VRF System_FloorG + DOAS | Office | Yes | 0.9379% | 502.9724 | 4526.7516 | 1 | 2.5149 | 5
OfficeMedium | Corridor_E_FloorG | Corridor Area | CAV with Reheat_East | PVAV_FloorG | VRF System_FloorG + DOAS | Office | Yes | 0.5579% | 299.2076 | 2692.8684 | 1 | 1.496 | 5
OfficeMedium | Corridor_S_FloorG | Corridor Area | CAV with Reheat_South | PVAV_FloorG | VRF System_FloorG + DOAS | Office | Yes | 0.9379% | 502.9724 | 4526.7516 | 1 | 2.5149 | 5 |  |  | Area Distribution By Space Type
OfficeMedium | Plenum_FloorG | Plenum | - | - | - | Office | No |  | 17875.9325 | 71503.73 | 1 | 0 | - |  |  | Space Type | % Area
OfficeMedium | Open_Office_Core_FloorM | Office Area (>250 square feet) | CAV with Reheat_Core | PVAV_FloorM | VRF System_FloorM + DOAS | Office | Yes | 7.986% | 4283 | 38547 | 1 | 21.415 | 5 |  |  | Office Area (>250 square feet) | 61.77%
OfficeMedium | Open_Office_N_FloorM | Office Area (>250 square feet) | CAV with Reheat_North | PVAV_FloorM | VRF System_FloorM + DOAS | Office | Yes | 4.285% | 2297.9873 | 20681.8859 | 1 | 11.4899 | 5 |  |  | Convention, Conference, Multipurpose and Meeting Area | 6.219%
OfficeMedium | Enclosed_Office_W_FloorM | Office Area (>250 square feet) | CAV with Reheat_West | PVAV_FloorM | VRF System_FloorM + DOAS | Office | Yes | 3.054% | 1637.8612 | 14740.7504 | 1 | 8.1893 | 5 |  |  | Lobby, Main Entry | 5.925%
OfficeMedium | Enclosed_Office_E_FloorM | Office Area (>250 square feet) | CAV with Reheat_East | PVAV_FloorM | VRF System_FloorM + DOAS | Office | Yes | 3.054% | 1637.8612 | 14740.7504 | 1 | 8.1893 | 5 |  |  | Storage (General) | 5.5%
OfficeMedium | Open_Office_S_FloorM | Office Area (>250 square feet) | CAV with Reheat_South | PVAV_FloorM | VRF System_FloorM + DOAS | Office | Yes | 2.212% | 1186.2075 | 10675.8676 | 1 | 5.931 | 5 |  |  | Electrical, Mechanical, Telephone Rooms | 1.999%
OfficeMedium | Conference_FloorM | Convention, Conference, Multipurpose and Meeting Area | CAV with Reheat_South | PVAV_FloorM | VRF System_FloorM + DOAS | Office | Yes | 2.073% | 1111.7798 | 10006.0183 | 1 | 36.6887 | 33 |  |  | IT Room (EPD 12) | 1.001%
OfficeMedium | Lounge_FloorM | Lounge, Breakroom, or Waiting Area | CAV with Reheat_Core_Service | PVAV_FloorM | VRF System_FloorM + DOAS | Office | Yes | 1.975% | 1059.1755 | 9532.5792 | 1 | 15.8876 | 15 | NonRes ACM 2005, Appendix 5.4A assigns 2.5 occupants to kitchenette spaces, but because this room serves as a combined break/kitchenette area—and break rooms assume 33 occupants—we applied a midpoint value. The lounge overlaps functionally with the break area, so its occupant count (33) was reduced to 15 to keep overall loads balanced. |  | Restrooms | 3.6%
OfficeMedium | Storage_FloorM | Storage (General) | CAV with Reheat_Core_Service | PVAV_FloorM | VRF System_FloorM + DOAS | Ancillary | Yes | 1.833% | 983.1561 | 8848.405 | 1 | 0 | - | Conditioned but with higher cooling setpoint |  | Lounge, Breakroom, or Waiting Area | 1.3%
OfficeMedium | Mechanical/Electrical_FloorM | Electrical, Mechanical, Telephone Rooms | CAV with Reheat_Core_Service | PVAV_FloorM | VRF System_FloorM + DOAS | Ancillary | Yes | 0.6663% | 357.3503 | 3216.1531 | 1 | 0 | - | Conditioned but with higher cooling setpoint |  | Stairwell | 3.7%
OfficeMedium | IT-Room_FloorM | IT Room (EPD 12) | CAV with Reheat_Core_Service | PVAV_FloorM | VRF System_FloorM + DOAS | Data | Yes | 0.3337% | 178.9373 | 1610.4357 | 1 | 0.26841 | 1.5 | Nonres ACM 2025, Appendix 5.4A |  | Corridor Area | 8.981%
OfficeMedium | Restroom_FloorM | Restrooms | CAV with Reheat_Core_Service | PVAV_FloorM | VRF System_FloorM + DOAS | Office | Yes | 1.2% | 643.5778 | 5792.2004 | 1 | 0 | - |  |  | Total | 0%
OfficeMedium | BreakRoom/Kitchenette_FloorM | Lounge, Breakroom, or Waiting Area | CAV with Reheat_Core_Service | PVAV_FloorM | VRF System_FloorM + DOAS | Office | Yes | 0.4332% | 232.343 | 2091.0866 | 1 | 7.6673 | 33 | Number of People: T24: 33 for Breakroom
OfficeMedium | Stairway_FloorM | Stairwell | CAV with Reheat_Core_Service | PVAV_FloorM | VRF System_FloorM + DOAS | Ancillary | Yes | 1.233% | 661.3923 | 5952.5303 | 1 | 0 | -
OfficeMedium | Corridor_W_FloorM | Corridor Area | CAV with Reheat_West | PVAV_FloorM | VRF System_FloorM + DOAS | Office | Yes | 0.5594% | 300 | 2700 | 1 | 1.5 | 5
OfficeMedium | Corridor_N_FloorM | Corridor Area | CAV with Reheat_North | PVAV_FloorM | VRF System_FloorM + DOAS | Office | Yes | 0.9379% | 502.9724 | 4526.7516 | 1 | 2.5149 | 5
OfficeMedium | Corridor_E_FloorM | Corridor Area | CAV with Reheat_East | PVAV_FloorM | VRF System_FloorM + DOAS | Office | Yes | 0.5579% | 299.2076 | 2692.8684 | 1 | 1.496 | 5
OfficeMedium | Corridor_S_FloorM | Corridor Area | CAV with Reheat_South | PVAV_FloorM | VRF System_FloorM + DOAS | Office | Yes | 0.9379% | 502.9724 | 4526.7516 | 1 | 2.5149 | 5
OfficeMedium | Plenum_FloorM | Plenum | - | - | - | Office | No |  | 17875.9325 | 71503.73 | 1 | 0 | -
OfficeMedium | Open_Office_Core_FloorT | Office Area (>250 square feet) | CAV with Reheat_Core | PVAV_FloorT | VRF System_FloorT + DOAS | Office | Yes | 7.986% | 4283 | 38547 | 1 | 21.415 | 5
OfficeMedium | Open_Office_N_FloorT | Office Area (>250 square feet) | CAV with Reheat_North | PVAV_FloorT | VRF System_FloorT + DOAS | Office | Yes | 4.285% | 2297.9873 | 20681.8859 | 1 | 11.4899 | 5
OfficeMedium | Enclosed_Office_W_FloorT | Office Area (>250 square feet) | CAV with Reheat_West | PVAV_FloorT | VRF System_FloorT + DOAS | Office | Yes | 3.054% | 1637.8612 | 14740.7504 | 1 | 8.1893 | 5
OfficeMedium | Enclosed_Office_E_FloorT | Office Area (>250 square feet) | CAV with Reheat_East | PVAV_FloorT | VRF System_FloorT + DOAS | Office | Yes | 3.054% | 1637.8612 | 14740.7504 | 1 | 8.1893 | 5
OfficeMedium | Open_Office_S_FloorT | Office Area (>250 square feet) | CAV with Reheat_South | PVAV_FloorT | VRF System_FloorT + DOAS | Office | Yes | 2.212% | 1186.2075 | 10675.8676 | 1 | 5.931 | 5
OfficeMedium | Conference_FloorT | Convention, Conference, Multipurpose and Meeting Area | CAV with Reheat_South | PVAV_FloorT | VRF System_FloorT + DOAS | Office | Yes | 2.073% | 1111.7798 | 10006.0183 | 1 | 36.6887 | 33
OfficeMedium | Lounge_FloorT | Lounge, Breakroom, or Waiting Area | CAV with Reheat_Core_Service | PVAV_FloorT | VRF System_FloorT + DOAS | Office | Yes | 1.975% | 1059.1755 | 9532.5792 | 1 | 15.8876 | 15 | T24, 2025, Appendix 5.4A assigns 2.5 occupants to kitchenette spaces, but because this room serves as a combined break/kitchenette area—and break rooms assume 33 occupants—we applied a midpoint value. The lounge overlaps functionally with the break area, so its occupant count (33) was reduced to 15 to keep overall loads balanced.
OfficeMedium | Storage_FloorT | Storage (General) | CAV with Reheat_Core_Service | PVAV_FloorT | VRF System_FloorT + DOAS | Ancillary | Yes | 1.833% | 983.1561 | 8848.405 | 1 | 0 | - | Conditioned but with higher cooling setpoint
OfficeMedium | Mechanical/Electrical_FloorT | Electrical, Mechanical, Telephone Rooms | CAV with Reheat_Core_Service | PVAV_FloorT | VRF System_FloorT + DOAS | Ancillary | Yes | 0.6663% | 357.3503 | 3216.1531 | 1 | 0 | - | Conditioned but with higher cooling setpoint
OfficeMedium | IT-Room_FloorT | IT Room (EPD 12) | CAV with Reheat_Core_Service | PVAV_FloorT | VRF System_FloorT + DOAS | Data | Yes | 0.3337% | 178.9373 | 1610.4357 | 1 | 0.26841 | 1.5 | Nonres ACM 2025, Appendix 5.4A
OfficeMedium | Restroom_FloorT | Restrooms | CAV with Reheat_Core_Service | PVAV_FloorT | VRF System_FloorT + DOAS | Office | Yes | 1.2% | 643.5778 | 5792.2004 | 1 | 0 | -
OfficeMedium | BreakRoom/Kitchenette_FloorT | Lounge, Breakroom, or Waiting Area | CAV with Reheat_Core_Service | PVAV_FloorT | VRF System_FloorT + DOAS | Office | Yes | 0.4332% | 232.343 | 2091.0866 | 1 | 7.6673 | 33 | Number of People: T24: 33 for Breakroom
OfficeMedium | Stairway_FloorT | Stairwell | CAV with Reheat_Core_Service | PVAV_FloorT | VRF System_FloorT + DOAS | Ancillary | Yes | 1.233% | 661.3923 | 5952.5303 | 1 | 0 | - | Conditioned but with higher cooling setpoint
OfficeMedium | Corridor_W_FloorT | Corridor Area | CAV with Reheat_West | PVAV_FloorT | VRF System_FloorT + DOAS | Office | Yes | 0.5594% | 300 | 2700 | 1 | 1.5 | 5
OfficeMedium | Corridor_N_FloorT | Corridor Area | CAV with Reheat_North | PVAV_FloorT | VRF System_FloorT + DOAS | Office | Yes | 0.9379% | 502.9724 | 4526.7516 | 1 | 2.5149 | 5
OfficeMedium | Corridor_E_FloorT | Corridor Area | CAV with Reheat_East | PVAV_FloorT | VRF System_FloorT + DOAS | Office | Yes | 0.5594% | 300 | 2692.8684 | 1 | 1.5 | 5
OfficeMedium | Corridor_S_FloorT | Corridor Area | CAV with Reheat_South | PVAV_FloorT | VRF System_FloorT + DOAS | Office | Yes | 0.9379% | 502.9724 | 4526.7516 | 1 | 2.5149 | 5
OfficeMedium | Plenum_FloorT | Plenum | - | - | - | Office | No |  | 17875.9325 | 71503.73 | 1 | 0 | -
Total ( 1 Building) | Total (54 Space) | Total (11 Space Type) | Total (6 HVAC Systems/Airloops) | Total (3 HVAC Systems/Airloops) | Total (4 HVAC Systems/Airloops) | Total (1 category) | Total (51 Conditioned zones, 3 unconditioned zones) | 100% | 53628.1373 | 658610.294
Ref: Geometry and zones: ORNL 2019 medium office prototype with modification. Note that to reduce simulation time, the floor areas of similar spaces in the middle section are combined, and the number of zones is minimized as much as possible.
https://web.eecs.utk.edu/~jnew1/publications/2019_IBPSA_OpenStudioOffice.pdf
https://web.eecs.utk.edu/~jnew1/presentations/2019_IBPSA_OpenStudioOffice.pdf
N

## Envelope
Envelope - OfficeMedium
Element | Prototype | Assembly Type | Construction | Thermal Properties | Vintage | Selected T24 | Notes | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
External Wall | OfficeMedium | ExtWall_MetalFramed_NonRes | Metal-frame walls + insulation + Gypsum board | U-factor IP | Pre 1978 | N/A | ASHRAE 90.1, 2022, Table A3.3.3.1, 3.5", R-0 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352
[5 empty] | 1978-1997 | 1986 | Low-rise office: Package A/ Heat Capacity was considered ~10 (BTU/F/ft2) | 0.15083 | 0.15748 | 0.15748 | 0.14368 | 0.14368 | 0.21645 | 0.21645 | 0.21645 | 0.21645 | 0.21645 | 0.18622 | 0.18622 | 0.18622 | 0.15873 | 0.15873 | 0.15083
[5 empty] | 1998-2007 | 2001 | TABLE 1-H | 0.182 | 0.182 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182
[5 empty] | 2008-2018 | 2013 | TABLE 140.3-B | 0.098 | 0.062 | 0.082 | 0.062 | 0.062 | 0.098 | 0.098 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062
[5 empty] | 2019+ | 2025 | Table 140.3-B (In Nonres Section) | 0.06 | 0.055 | 0.071 | 0.055 | 0.055 | 0.06 | 0.06 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055
Roof | OfficeMedium | FlatRoof_WoodFramedAndOther_NonRes | Metal-Deck roof + insulation + Roof membrane | U-factor IP | Pre 1978 | N/A | Considering 30 years for roof/ insultation replacement. | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 1978-1997 | 1992 | Considering 30 years for roof/ insultation replacement. | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 1998-2007 | 2001 | TABLE 1-H | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 2008-2018 | 2013 | TABLE 140.3-B | 0.049 | 0.039 | 0.039 | 0.039 | 0.049 | 0.075 | 0.067 | 0.067 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039
[5 empty] | 2019+ | 2025 | Table 140.3-B (In Nonres Section) | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.047 | 0.047 | 0.047 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028
Windows | OfficeMedium | FixedWindow_NonRes | CBECS 2018 shows that over 50 % of medium offices that were built before 2000 are single pane | U-factor IP | Pre 1978 | N/A | ASHRAE Handbook of Fundamentals for single pane (Table 4-Ch15) & T24, 2013 for double pane(50%-50%)* | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74
[5 empty] | 1978-1997 | N/A |  | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74
|  |  | Double pane |  | 1998-2007 | 2001 | TABLE 1-H | 0.49 | 0.49 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49
[5 empty] | 2008-2018 | 2013 | TABLE 140.3-B | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36
[5 empty] | 2019+ | 2025 | Table 140.3-B (In Nonres Section) | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.34 | 0.36 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.36
| OfficeMedium | FixedWindow_NonRes | CBECS 2018 shows that over 50% of medium offices that were built before 2000 are single pane | SHGC | Pre 1978 | N/A | ASHRAE Handbook of Fundamentals for single pane (Table 10-Ch15), & T24 2013 for double pane(50%-50%)* | 0.61 | 0.55 | 0.6 | 0.6 | 0.6 | 0.565 | 0.565 | 0.565 | 0.565 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.61
[5 empty] | 1978-1997 | N/A |  | 0.61 | 0.55 | 0.6 | 0.6 | 0.6 | 0.565 | 0.565 | 0.565 | 0.565 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.61
|  |  | Double pane |  | 1998-2007 | 2001 | WWR:30-40 / SHGC non-north (Non-north SHGC is more stringent than north and is therefore considered for all sides) | 0.43 | 0.31 | 0.41 | 0.41 | 0.41 | 0.34 | 0.34 | 0.34 | 0.34 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.43
[5 empty] | 2008-2018 | 2013 | TABLE 140.3-B | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
[5 empty] | 2019+ | 2025 | Table 140.3-B (In Nonres Section) | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.22 | 0.25 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.25
Infiltration
|  |  | Building | Zones | Vintage | I_75 (cfm/ft²) 6-sdied Infiltration rate @ 75 pa | Source | I-design (cfm/ft²) (4-sided Infiltration rate at normal pressure) (Design flow rate approach and Flow/Exterior Wall Area calculation method)
|  | Infiltration | OfficeMedium |  | Pre 1978 | 1.1 | 2022 CASE report (Table 38) | #REF! | [15 empty] | Building 6 sided area= | #REF!
[5 empty] | 1978-1997 | 1.1 | 2022 CASE report (Table 38) | #REF! | [15 empty] | Building 4 sided area= | #REF!
[5 empty] | 1998-2007 | 1.1 | 2022 CASE report (Table 38) | #REF! | [15 empty] | 6 sided /4 sided factor= | #REF!
[5 empty] | 2008-2018 | 1.0065* | 2022 CASE report (Table 38) & T24, 2008-2016 (Table 140.3-C) | #REF! | [15 empty] | Floor Area | 17881.5
[5 empty] | 2019+ | 0.6** | 2022 CASE report (Table 38) & T24,140.3(a)9Cii & T24, 2025 (Table 140.3-C) | #REF! | [15 empty] | Wall Area | #REF!
|  |  |  | Infiltration_rate_report_14May2025-Short-Version.docx | [19 empty] | Floor Number | 3
* An air barrier was not required for guest rooms under T24, until the 2019 edition. However, to reflect typical construction practices, we assumed that all exterior walls are equipped with an air barrier where it was required for nonresidential walls.
*** T24 require 0.4 cfm/ft² for tested condition but it also in section 140.3(a)9Cii says that if the air leakage requirements are not met, a visual inspection and diagnostic evaluation shall be completed , all observed leaks shall be sealed where such sealing can be made without destruction of existing building components, and buildings where the tested leakage rate exceeded 0.6 cfm/ft² of building shell area at 75 Pa have been retested to confirm leakage is below 0.6 cfm/ft² of building shell at 75 Pa.
*Note for windows properties in vintage 1 &2 :
We’ve considered a 50% single-pane and 50% double-pane mix (based on the 2013 requirements) for the window properties in Vintage 1 & 2 (pre-1998 buildings).
Since we don't have California-specific data, the decision is based on the CBECS 2018 data, which indicates:
- 40% of medium offices built before 1978 have mixed windows, while only 6% of offices from the second vintage (1978-1997) have mixed glass.
- Pre-1978: Among those with either single or double-pane windows, 80% have single-pane windows, and 20% have double-pane windows.
- 1978-1997: Among those with either single or double-pane windows, 55% have single-pane windows, and 45% have double-pane windows.
- Pre 1999: Among those with either single or double-pane windows, 61% has single pane windows.
Since we don't have California-specific data and CBECS data is for 2018, it's likely that a percentage of pre-1978 buildings have undergone retrofitting in the past 7 years and upgraded their windows. Based on this, we've decided to apply the 50%-50% mix for the window properties.

## HVAC System
HVAC system - OfficeMedium | [7 empty] | HVAC System Layout
Vintage | Space/Thermal Zone | Heating | Cooling | Air Distribution | Other systems | Source
Existing | All Except IT Rooms | Furnace (Gas) | Packaged (DX) | CAV with Reheat for the first two vintages VAV with Reheat for vintage 3 and 4 | OA mix through air handler Economizer for Vintage 3 and 4 DCV for Vintage 4 (for qualifying high density rooms) | CEUS 2022 + Engineering Judgement
| IT Room | - | DX Computer Room Air Conditioner (CRAC) | CAV | _ | Engineering Judgement
New Construction | All Except IT Rooms | VRF | VRF | VRF | DOAS Economizer ERV DCV for qualifying high density rooms | T24, 2025
| IT Room | - | DX Computer Room Air Conditioner (CRAC) | CAV | _ | T24 2025
[8 empty] | First Floor |  | Second and Third Floor
Efficiency of HVAC System (Efficiency is capacity-dependent. The following table provides a general estimate of system efficiency based on preliminary simulations in one climate zone, or assuming cooling load based on rule of thumb)
Vintage | HVAC System Type | Upgrade/Installed year | DX Computer Room Air Conditioner (CRAC) | Heating | Cooling | Source
Pre 1978 | Packaged CAV - DX with Gas Furnace | 2008 | 11 EER for <65 kBtu/h 10.4 EER for 65-135 kBtu/h 10.2 EER for 135-240 kBtu/h | Thermal efficiency (Et) of 80% | 10.1 EER for 65-135 kBtu/h 9.5 EER for 135-240 kBtu/h 9.3 EER & 9.7 IPLV for >240 kBtu/h | T24, Table 112-A (2008) California Title 20 Appliance Efficiency Regulations, Table E-4, Standards for Gas- and Oil-Fired Central Furnaces (2008) CRAC: California Title 20 Appliance Efficiency Regulations, §1605.3(c)(2), Tables C-9 (2008)
1978-1997
1998-2007 | Packaged VAV - DX with Gas Furnace | 2008 | 11 EER for <65 kBtu/h 10.4 EER for 65-135 kBtu/h 10.2 EER for 135-240 kBtu/h | Thermal efficiency (Et) of 80% | 10.1 EER for 65-135 kBtu/h 9.5 EER for 135-240 kBtu/h 9.3 EER & 9.7 IPLV for >240 kBtu/h
2008-2018 | Packaged VAV - DX with Gas Furnace | 2013 | SCOP= 2.44 for <65 kBtu/h 2.34 for 65-240 kBtu/h 2.24 for >240 kBtu/h | Thermal efficiency (Et) of 80% or 78% AFUE | SEER 13 for <65 kBtu/h 11 EER & 11.2 IEER for 65-135 kBtu/h 10.8 EER & 11 IEER for 135-240 kBtu/h 9.8 EER & 9.9 IEER for >240 kBtu/h | T24, Table 110.2-J & Table 110.2-A (2013) CRAC: 10 CFR §431.97(f)(1), Table 7 (2013)
New Construction | VRF | 2025 | NSenCOP= 2.09 for <65 kBtu/h 1.99 for 65-240 kBtu/h 1,81 for >240 kBtu/h | 7.5 HSPF2 for <65 kBtu/h 3.3 COP for 65-135 kBtu/h 3.2 COP for 135-240 kBtu/h 3.2 COP for >240 kBtu/h | 10.1 EER & 14.4 IEER for 65-135 kBtu/h 9.7 EER & 13.7 IEER for 135-240 kBtu/h 8.9 EER & 12.5 IEER for >240 kBtu/h | T24, Table 110.2-G (2025) 10 CFR § 431.97 Table 16 (2025) CRAC: 10 CFR § 431.97, Table 13 (2025)
Fan power
Vintage | Approach | System | Total Static Pressure (TSP) (in w.c.) | Fan Efficiency [ACM 2025] | Motor Efficiency | Fan Power Index (W/cfm) | Data Source | Note
Existing | PNNL 90 1-2011, TSP | CAV System <7,437 cfm | 2.5 | 0.65 | According to PNNL 20405 section 5.2.2.5, the full-load efficiency of the motor serving the fan is taken from ASHRAE 90.1, 2004, Table 10.8, based on motor nameplate and assuming enclosed motors operating at 1,800 rotations per minute (rpm) Motor nameplate size in hp = brake horsepower (bhp) × 1.1 ( using a 10% oversizing factor) Brake horsepower (bhp) = (Supply cfm from sizing run × TSP in w.c.) / (6356 × fan efficiency) | Fan power in W/cfm = (TSP in w.c. × 746) / (6356 × fan efficiency × motor and drive efficiency | Fan power formula: PNNL 20405, 2010, section 5.2.2.5 TSP and fan efficiecncy: PNNL 20405, 2010, Table 5.11, 90.1-04ac values Motor and drive efficiency: ASHRAE 90.1, 2004, Table 10.8 |  | PNNL 20405, 2010, Table 5.11
|  | CAV System >7,437 cfm | 4.09 | 0.65
|  | VAV System > 4,648 cfm | 5.58 | 0.65
Brake horsepower (bhp) = (Supply cfm × TSP in w.c.) / (6356 × fan efficiency)
Fan power (w/cfm) = (bhp × 746) / ( supply cfm × motor efficiency )
New Construction | ACM 2025 | Small indoor fan at zone (for VRF) <1,600 cfm | 1.6573 | 0.65 | The full‑load efficiency of the motor serving the fan is taken from ACM 2025 Table 12 based on the cfm of the fan. Motor horsepower in hp = (Supply cfm from sizing run × fan power in W/cfm) / 746. Considering a maximum airflow of 1,600 cfm for the VRF indoor fan (based on the sizing run), the resulting motor power is less than 1 hp. Therefore, motor efficiency is 85.5% according to ACM 2025 Table 12. In larger fan, motor effiiceny is higher. | 0.35 | Fan power index (0.35 w/cfm): [T24, 2025, Section 140.4(a)3 D] Motot efficiency: [ ACM 2025, Table 12] | 0.35 W/CFM is for the indoor unit fan. For main HVAC system fan (if applicable), the fan power must be determined using the 2025 ACM Table 13.
TSP (E+ input) in w.c. = fan power in W/cfm × motor effciency × fan efficiecny × 6356 / 746
| 𝜇_𝑚𝑜𝑡𝑜𝑟 : Motor and drive efficiency |  |  | (〖Fna power〗_(w/cfm)∗cfm∗μ_motor)/746
〖𝐹𝑎𝑛 𝑝𝑜𝑤𝑒𝑟〗_(𝑤/𝑐𝑓𝑚)=(〖𝑇𝑆𝑃〗_(𝑖𝑛 𝑤.𝑐)∗746)/(6356∗𝜇_𝑓𝑎𝑛∗𝜇_𝑚𝑜𝑡𝑜𝑟 )
𝑏ℎ𝑝=(𝑐𝑓𝑚∗〖𝑇𝑆𝑃〗_(𝑖𝑛 𝑤.𝑐.))/〖6356∗𝜇〗_𝑓𝑎𝑛
〖𝐹𝑎𝑛 𝑝𝑜𝑤𝑒𝑟〗_(𝑤/𝑐𝑓𝑚)=(𝑏ℎ𝑝∗746)/(𝑐𝑓𝑚∗𝜇_𝑚𝑜𝑡𝑜𝑟 )
𝑏ℎ𝑝=(〖𝐹𝑎𝑛 𝑝𝑜𝑤𝑒𝑟〗_(𝑤/𝑐𝑓𝑚)∗𝑐𝑓𝑚∗𝜇_𝑚𝑜𝑡𝑜𝑟)/746

## Thermostat
Thermostat Setpoints: OfficeMedium
Spaces/Zones | Setpoint | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16 | Source
All conditioned zones except server rooms, Storage, Stairway & Mechanical_Electrical | Heating Setpoint (F) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | T24 2022 - Appendix 5.4B
| Heating Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
| Cooling Setpoint (F) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
| Cooling Setback (F) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
Storage, Stairway, and Mechanical_Electrical | Heating Setpoint (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | Enginnering Judgment (Semi‑conditioned space)
| Heating Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
| Cooling Setpoint (F) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
| Cooling Setback (F) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
IT rooms | Cooling Setpoint (F)* | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | Title 24, Part 6, 2025, section 140.9 (a) and PNNL ASHRAE 90.1 2022 Large Office prototype
| Heating Setpoint (F)* | *The IT room with over 12 W/ft2 load doesn't require heating system as the equipment constantly generate enough heat.
Note: The Medium Office prototype by PNNL also uses the same setpoints, except for one of the perimeter zones, which has a heating setpoint of 69 °F and a cooling setpoint of 76 °F during hours of 10:00-11:00, 12:00-13:00, and 14:00-15:00 .

## Ventilation
Outdoor Airflow Rate - OfficeMedium
Space | Number of People | Floor Area (ft²) | cfm/person (T24, 2025, Equation 120.1-F and Table 120.1-A) | cfm/ft² (T24, 2025, Equation 120.1-F and Table 120.1-A) | Required Exhaust Rate (T24, 2025, Table 120.1-B – Minimum Exhaust Rates) | Total cfm Driven by People | Total cfm Driven by Area | Total cfm Driven by Exhaust | Total cfm | Note
Open_Office_Core_FloorG | 21.415 | 4283 | 15 | 0.15 |  | 321.225 | 642.45 | 0 | 642.45 | Office space/Occupancy Category - Office Buildings
Open_Office_N_FloorG | 11.4899 | 2297.9873 | 15 | 0.15 |  | 172.349 | 344.6981 | 0 | 344.6981 | Office space/Occupancy Category - Office Buildings
Enclosed_Office_W_FloorG | 8.1893 | 1637.8612 | 15 | 0.15 |  | 122.8396 | 245.6792 | 0 | 245.6792 | Office space/Occupancy Category - Office Buildings
Enclosed_Office_E_FloorG | 8.1893 | 1637.8612 | 15 | 0.15 |  | 122.8396 | 245.6792 | 0 | 245.6792 | Office space/Occupancy Category - Office Buildings
Open_Office_S_FloorG | 5.931 | 1186.2075 | 15 | 0.15 |  | 88.9656 | 177.9311 | 0 | 177.9311 | Office space/Occupancy Category - Office Buildings
Conference_FloorG | 36.6887 | 1111.7798 | 15 | 0.15 |  | 550.331 | 166.767 | 0 | 550.331 | Conference/meeting/Occupancy Category - General
Lobby_FloorG | 10.5918 | 1059.1755 | 15 | 0.15 |  | 158.8763 | 158.8763 | 0 | 158.8763 | Main entry lobbies/Occupancy Category - Office Buildings
Storage_FloorG | 0 | 983.1561 | 15 | 0.15 |  |  | 147.4734 | 0 | 147.4734 | Occupiable storage rooms for dry materials/Occupancy Category - Office Buildings
Mechanical/Electrical_FloorG | 0 | 357.3503 | 15 | 0.15 |  |  | 53.6026 | 0 | 53.6026 | All Other
IT-Room_FloorG | 0.26841 | 178.9373 | 15 | 0.15 |  |  | 26.8406 | 0 | 26.8406 | Telephone/data entry/Occupancy Category - Office Buildings
Restroom_FloorG | 0 | 643.5778 | 15 | 0.15 | 4*50/70 cfm per unit |  | 96.5367 | 200 | 200 | All Other- Almost 1 unit per 30 occupant for exhaust fan
BreakRoom/Kitchenette_FloorG | 7.6673 | 232.343 | 15 | 0.15 |  | 115.0098 | 34.8514 | 0 | 115.0098 | Breakrooms/Occupancy Category - Office Buildings
Stairway_FloorG | 0 | 661.3923 | 15 | 0.15 |  |  | 99.2088 | 0 | 99.2088 | All Other
Corridor_W_FloorG | 1.5 | 300 | 15 | 0.15 |  | 22.5 | 45 | 0 | 45 | Corridors /Occupancy Category - General
Corridor_N_FloorG | 2.5149 | 502.9724 | 15 | 0.15 |  | 37.7229 | 75.4459 | 0 | 75.4459 | Corridors /Occupancy Category - General
Corridor_E_FloorG | 1.496 | 299.2076 | 15 | 0.15 |  | 22.4406 | 44.8811 | 0 | 44.8811 | Corridors /Occupancy Category - General
Corridor_S_FloorG | 2.5149 | 502.9724 | 15 | 0.15 |  | 37.7229 | 75.4459 | 0 | 75.4459 | Corridors /Occupancy Category - General
Plenum_FloorG | 0 | 17875.9325 |  | - |  |  |  | 0 | 0 | -
Open_Office_Core_FloorM | 21.415 | 4283 | 15 | 0.15 |  | 321.225 | 642.45 | 0 | 642.45 | Office space/Occupancy Category - Office Buildings
Open_Office_N_FloorM | 11.4899 | 2297.9873 | 15 | 0.15 |  | 172.349 | 344.6981 | 0 | 344.6981 | Office space/Occupancy Category - Office Buildings
Enclosed_Office_W_FloorM | 8.1893 | 1637.8612 | 15 | 0.15 |  | 122.8396 | 245.6792 | 0 | 245.6792 | Office space/Occupancy Category - Office Buildings
Enclosed_Office_E_FloorM | 8.1893 | 1637.8612 | 15 | 0.15 |  | 122.8396 | 245.6792 | 0 | 245.6792 | Office space/Occupancy Category - Office Buildings
Open_Office_S_FloorM | 5.931 | 1186.2075 | 15 | 0.15 |  | 88.9656 | 177.9311 | 0 | 177.9311 | Office space/Occupancy Category - Office Buildings
Conference_FloorM | 36.6887 | 1111.7798 | 15 | 0.15 |  | 550.331 | 166.767 | 0 | 550.331 | Conference/meeting/Occupancy Category - General
Lounge_FloorM | 15.8876 | 1059.1755 | 15 | 0.15 |  | 238.3145 | 158.8763 | 0 | 238.3145 | Break rooms /Occupancy Category - Office Buildings
Storage_FloorM | 0 | 983.1561 | 15 | 0.15 |  |  | 147.4734 | 0 | 147.4734 | Occupiable storage rooms for dry materials/Occupancy Category - Office Buildings
Mechanical/Electrical_FloorM | 0 | 357.3503 | 15 | 0.15 |  |  | 53.6026 | 0 | 53.6026 | All Other
IT-Room_FloorM | 0.26841 | 178.9373 | 15 | 0.15 |  |  | 26.8406 | 0 | 26.8406 | Telephone/data entry/Occupancy Category - Office Buildings
Restroom_FloorM | 0 | 643.5778 | 15 | 0.15 | 4*50/70 cfm per unit |  | 96.5367 | 200 | 200 | All Other
BreakRoom/Kitchenette_FloorM | 7.6673 | 232.343 | 15 | 0.15 |  | 115.0098 | 34.8514 | 0 | 115.0098 | Breakrooms/Occupancy Category - Office Buildings
Stairway_FloorM | 0 | 661.3923 | 15 | 0.15 |  |  | 99.2088 | 0 | 99.2088 | All Other
Corridor_W_FloorM | 1.5 | 300 | 15 | 0.15 |  | 22.5 | 45 | 0 | 45 | Corridors /Occupancy Category - General
Corridor_N_FloorM | 2.5149 | 502.9724 | 15 | 0.15 |  | 37.7229 | 75.4459 | 0 | 75.4459 | Corridors /Occupancy Category - General
Corridor_E_FloorM | 1.496 | 299.2076 | 15 | 0.15 |  | 22.4406 | 44.8811 | 0 | 44.8811 | Corridors /Occupancy Category - General
Corridor_S_FloorM | 2.5149 | 502.9724 | 15 | 0.15 |  | 37.7229 | 75.4459 | 0 | 75.4459 | Corridors /Occupancy Category - General
Plenum_FloorM | 0 | 17875.9325 | 0 | - |  |  |  | 0 | 0 | -
Open_Office_Core_FloorT | 21.415 | 4283 | 15 | 0.15 |  | 321.225 | 642.45 | 0 | 642.45 | Office space/Occupancy Category - Office Buildings
Open_Office_N_FloorT | 11.4899 | 2297.9873 | 15 | 0.15 |  | 172.349 | 344.6981 | 0 | 344.6981 | Office space/Occupancy Category - Office Buildings
Enclosed_Office_W_FloorT | 8.1893 | 1637.8612 | 15 | 0.15 |  | 122.8396 | 245.6792 | 0 | 245.6792 | Office space/Occupancy Category - Office Buildings
Enclosed_Office_E_FloorT | 8.1893 | 1637.8612 | 15 | 0.15 |  | 122.8396 | 245.6792 | 0 | 245.6792 | Office space/Occupancy Category - Office Buildings
Open_Office_S_FloorT | 5.931 | 1186.2075 | 15 | 0.15 |  | 88.9656 | 177.9311 | 0 | 177.9311 | Office space/Occupancy Category - Office Buildings
Conference_FloorT | 36.6887 | 1111.7798 | 15 | 0.15 |  | 550.331 | 166.767 | 0 | 550.331 | Conference/meeting/Occupancy Category - General
Lounge_FloorT | 15.8876 | 1059.1755 | 15 | 0.15 |  | 238.3145 | 158.8763 | 0 | 238.3145 | Break rooms /Occupancy Category - Office Buildings
Storage_FloorT | 0 | 983.1561 | 15 | 0.15 |  |  | 147.4734 | 0 | 147.4734 | Occupiable storage rooms for dry materials/Occupancy Category - Office Buildings
Mechanical/Electrical_FloorT | 0 | 357.3503 | 15 | 0.15 |  |  | 53.6026 | 0 | 53.6026 | All Other
IT-Room_FloorT | 0.26841 | 178.9373 | 15 | 0.15 |  |  | 26.8406 | 0 | 26.8406 | Telephone/data entry/Occupancy Category - Office Buildings
Restroom_FloorT | 0 | 643.5778 | 15 | 0.15 | 4* 50/70 cfm per unit |  | 96.5367 | 200 | 200 | All Other
BreakRoom/Kitchenette_FloorT | 7.6673 | 232.343 | 15 | 0.15 |  | 115.0098 | 34.8514 | 0 | 115.0098 | Breakrooms/Occupancy Category - Office Buildings
Stairway_FloorT | 0 | 661.3923 | 15 | 0.15 |  |  | 99.2088 | 0 | 99.2088 | All Other
Corridor_W_FloorT | 1.5 | 300 | 15 | 0.15 |  | 22.5 | 45 | 0 | 45 | Corridors /Occupancy Category - General
Corridor_N_FloorT | 2.5149 | 502.9724 | 15 | 0.15 |  | 37.7229 | 75.4459 | 0 | 75.4459 | Corridors /Occupancy Category - General
Corridor_E_FloorT | 1.5 | 300 | 15 | 0.15 |  | 22.5 | 45 | 0 | 45 | Corridors /Occupancy Category - General
Corridor_S_FloorT | 2.5149 | 502.9724 | 15 | 0.15 |  | 37.7229 | 75.4459 | 0 | 75.4459 | Corridors /Occupancy Category - General
Plenum_FloorT | 0 | 17875.9325 | 0 | - |  |  |  | 0 | 0 | -
CEUS 2022 Data shows that about 50% of the unconditioned floor area belongs to the first vintage bin (Pre-1978)

## Water Heater
Water Heater - OfficeMedium
Vintage | WH Type | Efficiency | Number of WH | Tank Volume (gal) | Tank Loss | Source
Existing | Gas | 0.8 | 1 | See table below for CZ-specific values: Climate Zone Water Heater Sizing and Loss Coefficients, Storage Volume column (col F) | See table below: Climate Zone Water Heater Sizing and Loss Coefficients, Standby Loss column (col G) | See table below for sources: Climate Zone Water Heater Sizing and Loss Coefficients
New Construction | Gas | 0.8 | 1 | See table below for CZ-specific values: Climate Zone Water Heater Sizing and Loss Coefficients, Storage Volume column (col F) | See table below: Climate Zone Water Heater Sizing and Loss Coefficients, Standby Loss column (col G) | See table below for sources: Climate Zone Water Heater Sizing and Loss Coefficients
Peak Hot Water Consumption
Space Name | Baseline WH Type [T24, 2022, Appendix 5.4A , sheet: "2022 SpaceFuncData-Input"] | Total Area (ft²) |  | Number of People | Hot Water Usage Specification (gal/hr per person) [T24, 2022, Appendix 5.4A , sheet: "2022 SpaceFuncData-Input"] | Peak Hot Water Usage (gal/hr) | Peak Hot Water Usage (gal/min) | Note
Open_Office_Core_FloorG | Gas* | 4283 |  | 21.415 | 0.18 | 3.8547 | 0.064245 | For space types marked with an asterisk (the ‘*’ symbol), the water‑heater type is listed as electric in Appendix 5.4A, sheet ‘2022 SpaceFuncData‑Input.’ However, we modified the value based on CEUS data, which indicates that gas is the primary fuel type.
Open_Office_N_FloorG | Gas* | 2297.9873 |  | 11.4899 | 0.18 | 2.0682 | 0.03447
Enclosed_Office_W_FloorG | Gas* | 1637.8612 |  | 8.1893 | 0.18 | 1.4741 | 0.024568
Enclosed_Office_E_FloorG | Gas* | 1637.8612 |  | 8.1893 | 0.18 | 1.4741 | 0.024568
Open_Office_S_FloorG | Gas* | 1186.2075 |  | 5.931 | 0.18 | 1.0676 | 0.017793
Conference_FloorG | Gas* | 1111.7798 |  | 36.6887 | 0.09 | 3.302 | 0.055033
Lobby_FloorG | Gas | 1059.1755 |  | 10.5918 | 0.09 | 0.95326 | 0.015888
Storage_FloorG | Gas* | 983.1561 |  |  | 0 | 0 | 0
Mechanical/Electrical_FloorG | Gas* | 357.3503 |  |  | 0.18 | 0 | 0
IT-Room_FloorG | Gas* | 178.9373 |  |  | 0.18 | 0 | 0
Restroom_FloorG | Gas | 643.5778 |  |  | 0 | 0 | 0
BreakRoom/Kitchenette_FloorG | Gas | 232.343 |  | 7.6673 | 0.578 | 4.4317 | 0.073862
Stairway_FloorG | Gas* | 661.3923 |  |  | 0 | 0 | 0
Corridor_W_FloorG | Gas* | 300 |  | 1.5 | 0 | 0 | 0
Corridor_N_FloorG | Gas* | 502.9724 |  | 2.5149 | 0 | 0 | 0
Corridor_E_FloorG | Gas* | 299.2076 |  | 1.496 | 0 | 0 | 0
Corridor_S_FloorG | Gas* | 502.9724 |  | 2.5149 | 0 | 0 | 0
Plenum_FloorG |  | 17875.9325 |  |  | 0 | 0 | 0
Open_Office_Core_FloorM | Gas* | 4283 |  | 21.415 | 0.18 | 3.8547 | 0.064245
Open_Office_N_FloorM | Gas* | 2297.9873 |  | 11.4899 | 0.18 | 2.0682 | 0.03447
Enclosed_Office_W_FloorM | Gas* | 1637.8612 |  | 8.1893 | 0.18 | 1.4741 | 0.024568
Enclosed_Office_E_FloorM | Gas* | 1637.8612 |  | 8.1893 | 0.18 | 1.4741 | 0.024568
Open_Office_S_FloorM | Gas* | 1186.2075 |  | 5.931 | 0.18 | 1.0676 | 0.017793
Conference_FloorM | Gas* | 1111.7798 |  | 36.6887 | 0.09 | 3.302 | 0.055033
Lounge_FloorM | Gas | 1059.1755 |  | 15.8876 | 0.09 | 1.4299 | 0.023831
Storage_FloorM | - | 983.1561 |  |  | 0 | 0 | 0
Mechanical/Electrical_FloorM | Gas* | 357.3503 |  |  | 0.18 | 0 | 0
IT-Room_FloorM | Gas* | 178.9373 |  |  | 0.18 | 0 | 0
Restroom_FloorM | Gas | 643.5778 |  |  | 0 | 0 | 0
BreakRoom/Kitchenette_FloorM | Gas | 232.343 |  | 7.6673 | 0.578 | 4.4317 | 0.073862
Stairway_FloorM | Gas* | 661.3923 |  |  | 0 | 0 | 0
Corridor_W_FloorM | Gas* | 300 |  | 1.5 | 0 | 0 | 0
Corridor_N_FloorM | Gas* | 502.9724 |  | 2.5149 | 0 | 0 | 0
Corridor_E_FloorM | Gas* | 299.2076 |  | 1.496 | 0 | 0 | 0
Corridor_S_FloorM | Gas* | 502.9724 |  | 2.5149 | 0 | 0 | 0
Plenum_FloorM |  | 17875.9325 |  |  | 0 | 0 | 0
Open_Office_Core_FloorT | Gas* | 4283 |  | 21.415 | 0.18 | 3.8547 | 0.064245
Open_Office_N_FloorT | Gas* | 2297.9873 |  | 11.4899 | 0.18 | 2.0682 | 0.03447
Enclosed_Office_W_FloorT | Gas* | 1637.8612 |  | 8.1893 | 0.18 | 1.4741 | 0.024568
Enclosed_Office_E_FloorT | Gas* | 1637.8612 |  | 8.1893 | 0.18 | 1.4741 | 0.024568
Open_Office_S_FloorT | Gas* | 1186.2075 |  | 5.931 | 0.18 | 1.0676 | 0.017793
Conference_FloorT | Gas* | 1111.7798 |  | 36.6887 | 0.09 | 3.302 | 0.055033
Lounge_FloorT | Gas | 1059.1755 |  | 15.8876 | 0.09 | 1.4299 | 0.023831
Storage_FloorT | Gas* | 983.1561 |  |  | 0 | 0 | 0
Mechanical/Electrical_FloorT | Gas* | 357.3503 |  |  | 0.18 | 0 | 0
IT-Room_FloorT | Gas* | 178.9373 |  |  | 0.18 | 0 | 0
Restroom_FloorT | Gas | 643.5778 |  |  | 0 | 0 | 0
BreakRoom/Kitchenette_FloorT | Gas | 232.343 |  | 7.6673 | 0.578 | 4.4317 | 0.073862
Stairway_FloorT | Gas* | 661.3923 |  |  | 0 | 0 | 0
Corridor_W_FloorT | Gas* | 300 |  | 1.5 | 0 | 0 | 0
Corridor_N_FloorT | Gas* | 502.9724 |  | 2.5149 | 0 | 0 | 0
Corridor_E_FloorT | Gas* | 300 |  | 1.5 | 0 | 0 | 0
Corridor_S_FloorT | Gas* | 502.9724 |  | 2.5149 | 0 | 0 | 0
Plenum_FloorT |  | 17875.9325 |  |  | 0 | 0 | 0
Total | Gas storage |  |  |  |  | 75 |  | Minimum peak hot water usage is 75 gal according to ACM 2025
Total | Electric resistance |  |  |  |  | 0
Design supply temperature (°F) | 135 | Title 24 2022 Reference Appendices, Appendix 5.4B
WH system factor | 0.6 | 2025 ACM §5.9.2 Rated Capacity
Water mass conversion (lb/gal) | 8.2877 | 2025 ACM §5.9.2 Rated Capacity
Reheat multiplier | 0.4 | 2025 ACM §5.9.2 Storage Volume
Climate Zone Water Heater Sizing and Loss Coefficients
Water Heater Name | Climate Zone | Minimum Monthly Mains Temp (°F) [T24 2022 - Appendix 5.4B] | Heat Output (Btu/hr) [ACM, 2025, 5.9.2: Rated capacity section] | WH Capacity (Btu/hr) [ACM, 2025, 5.9.2: Rated capacity section] | Required Energy Input (Btu/hr) | Storage Volume (gal) | Standby Loss [Title 20, §1605.1 Table F-4; Appendix B: Water Heating Calculation Method] |  | Off/On Cycle Loss Coefficient to Ambient Temp |  | Source/Note
WH_OfficeMedium | CZ01 | 47.9 | 54139.4002 | 32483.6401 | 60000 | 34 | 716.4047 | Btu/hr | 10.2344 | Btu/h·°F | Required Energy Input: vendor/available catalog size (Market data table). Storage Volume: standard/available catalog tank size (Market data table).
WH_OfficeMedium | CZ02 | 50.8 | 52336.8255 | 31402.0953 | 60000 | 34 | 716.4047 | Btu/hr | 10.2344 | Btu/h·°F
WH_OfficeMedium | CZ03 | 52.2 | 51466.617 | 30879.9702 | 60000 | 34 | 716.4047 | Btu/hr | 10.2344 | Btu/h·°F
WH_OfficeMedium | CZ04 | 52.7 | 51155.8282 | 30693.4969 | 60000 | 34 | 716.4047 | Btu/hr | 10.2344 | Btu/h·°F
WH_OfficeMedium | CZ05 | 51.6 | 51839.5635 | 31103.7381 | 60000 | 34 | 716.4047 | Btu/hr | 10.2344 | Btu/h·°F
WH_OfficeMedium | CZ06 | 56.8 | 48607.3605 | 29164.4163 | 60000 | 34 | 716.4047 | Btu/hr | 10.2344 | Btu/h·°F
WH_OfficeMedium | CZ07 | 58.4 | 47612.8365 | 28567.7019 | 60000 | 34 | 716.4047 | Btu/hr | 10.2344 | Btu/h·°F
WH_OfficeMedium | CZ08 | 58.4 | 47612.8365 | 28567.7019 | 60000 | 34 | 716.4047 | Btu/hr | 10.2344 | Btu/h·°F
WH_OfficeMedium | CZ09 | 57.6 | 48110.0985 | 28866.0591 | 60000 | 34 | 716.4047 | Btu/hr | 10.2344 | Btu/h·°F
WH_OfficeMedium | CZ10 | 57.1 | 48420.8872 | 29052.5323 | 60000 | 34 | 716.4047 | Btu/hr | 10.2344 | Btu/h·°F
WH_OfficeMedium | CZ11 | 50.5 | 52523.2987 | 31513.9792 | 60000 | 34 | 716.4047 | Btu/hr | 10.2344 | Btu/h·°F
WH_OfficeMedium | CZ12 | 51.4 | 51963.879 | 31178.3274 | 60000 | 34 | 716.4047 | Btu/hr | 10.2344 | Btu/h·°F
WH_OfficeMedium | CZ13 | 51.7 | 51777.4057 | 31066.4434 | 60000 | 34 | 716.4047 | Btu/hr | 10.2344 | Btu/h·°F
WH_OfficeMedium | CZ14 | 50.1 | 52771.9297 | 31663.1578 | 60000 | 34 | 716.4047 | Btu/hr | 10.2344 | Btu/h·°F
WH_OfficeMedium | CZ15 | 63.2 | 44629.2645 | 26777.5587 | 60000 | 34 | 716.4047 | Btu/hr | 10.2344 | Btu/h·°F
WH_OfficeMedium | CZ16 | 41.4 | 58179.654 | 34907.7924 | 60000 | 34 | 716.4047 | Btu/hr | 10.2344 | Btu/h·°F
Market data
Gas WH |  |  |  |  | Elec WH
WH capacity |  | Tank volume |  |  | WH capacity |  | Tank volume
Catalog gas input (Btu/h) | Input source | Catalog gas tank (gal) |  | Tank source | Elec resistance tank (kW) | Elec resistance (Btu/h) | Elec tank (gal) | Elec tank source | Sources and links → Note tab
60000 | Grainger | 34 |  | ENERGY STAR | 1.5 | 5118 | 6 | Grainger
75100 | Grainger | 35 |  | Grainger | 2 | 6824 | 10 | Grainger
76000 | Both | 48 |  | Grainger | 3 | 10236 | 15 | Grainger
80000 | Grainger | 50 |  | Both | 4.5 | 15355 | 20 | Grainger
99900 | ENERGY STAR | 55 |  | ENERGY STAR | 6 | 20473 | 28 | Grainger
100000 | Both | 60 |  | ENERGY STAR | 8 | 27297 | 30 | Grainger
120000 | ENERGY STAR | 65 |  | Both | 9 | 30709 | 36 | Grainger
125000 | Both | 72 |  | Grainger | 10 | 34121 | 40 | Grainger
130000 | Both | 75 |  | Both | 12 | 40946 | 47 | Grainger
145000 | ENERGY STAR | 76 |  | Grainger | 12.1 | 41287 | 50 | Grainger
150000 | ENERGY STAR | 80 |  | Both | 18 | 61419 | 65 | Grainger
156000 | Grainger | 82 |  | Grainger | 24 | 81891 | 80 | Grainger
160000 | Both | 85 |  | Grainger | 27 | 92128 | 85 | Grainger
175000 | ENERGY STAR | 90 |  | Both | 36 | 122837 | 105 | Grainger
180000 | Grainger | 91 |  | Grainger | 54 | 184256 | 120 | Grainger
199000 | ENERGY STAR | 100 |  | Both
199900 | Both | 110 |  | ENERGY STAR
200000 | ENERGY STAR | 119 |  | Both
250000 | Both | 125 |  | ENERGY STAR
251000 | ENERGY STAR
270000 | Grainger
285000 | ENERGY STAR
300000 | Both
320000 | ENERGY STAR
360000 | Grainger
398000 | ENERGY STAR
399000 | ENERGY STAR
399900 | Both
499900 | Grainger
550000 | Grainger
715000 | Grainger
Background Data [To be deleted prior to publication]
Water use: | PNNL (for Core zone) | DEER |  | CEC
peak flow rate (gal/min) | 0.06416 | 0.0322 for N&S ZN - 0.0192 for E&W ZN |  | 0.0242 for Core ZN- 0.0109 for two ZN - 0.0183 for two other ZN | NOR Flow rate schedule follows CEC
Target Temperature | 120 | 135 |  | 135
Sensible Fraction | 0.2 | 0.2 |  | N/A
Latent Fraction | 0.05 | 0.05 |  | N/A
CEUS 2022 data | Water Heater
% of total impacted floor area | 92.96%
Dominated system | Package System / Heat Pump
Fuel and Share | 49.9% Electric and 49.1% Gas

## Interior Lights
Interior Lighting - OfficeMedium
Space Type | New Construction |  |  | Existing |  |  | Note
| LPD (W/ft²) | Additional LPD for Portable Lighting (W/ft²) | Source | LPD (W/ft²) | Additional LPD for Portable Lighting (W/ft²) | Source
Office Area (>250 square feet) | 0.6 | 0.1 | T24, part 6, 2025, Table 140.6 C IT Room Source: ASHRAE 90.1 2022, Table 9.5.2.1-1, computer room space type | 0.75 | - | T24, part 6, 2013, Table 140.6 C IT Room Source: ASHRAE 90.1 2013, TABLE9.6.1, computer room space type | It is assumed that 50% of the additional allowance lighting is in use.
Convention, Conference, Multipurpose and Meeting Area | 0.75 |  |  | 1.4
Lobby, Main Entry | 0.7 | 0.25 |  | 1.5 | 0.5
Storage (General) | 0.4 |  |  | 0.6
Electrical, Mechanical, Telephone Rooms | 0.4 |  |  | 0.7
IT Room (EPD 12) | 0.75 |  |  | 1.71
Restrooms | 0.65 |  |  | 0.65
Lounge, Breakroom, or Waiting Area | 0.55 | 0.125 |  | 1.1 | 0.25 |  | 2013 LPD is for "Lounge" area It is assumed that 50% of the additional allowance lighting is in use.
Stairwell | 0.6 |  |  | 0.6
Corridor Area | 0.4 |  |  | 0.6
Plenum | -
Whole Building method
| 2025 | 2013
LPD for Office Building ((W/ft²) | 0.6 | 0.8
Ref: T24, Table 140.6 B
Background Data [To be deleted prior to publication]
Ref: Title 24, Part 6- Table 140.6-C (office area >250nSF)
Title 24, part 6 Code cycle | Lighting density for office Buildings: (complete building Method) | Lighting density for office area >250 sf Floor area Method | Table | Note |  | T24, part 6 2022 | file://carcgl.com/amer/NOR/Groups/CodesStds/Standards/California/2022%20Building%20Energy%20Efficiency%20Standards%20for%20Residential%20and%20Nonresidential%20Buildings.pdf
2025 | 0.6 | 0.6, 0.2 (additional) | Table 140.6 C |  |  | T24, part 6 2019 | file://carcgl.com/amer/NOR/Groups/CodesStds/Standards/California/2016-CEC-400-2015-037-CMF.pdf
2022 | 0.6 | 0.6, 0.2 (additional) |  |  |  | T24, part 6 2016 | file://carcgl.com/amer/NOR/Groups/CodesStds/Standards/California/2016-CEC-400-2015-037-CMF.pdf
2019 | 0.65
2016 | 0.8
2013 | 0.8 | 0.75
2010 | 0.85
2008 | 0.085 | 0.9 | Table 146-E
2005 |  | 1.2
TBD: Review the CASE report on 2016 for lighting
Review of existing Medium Office prototype
Prototype/Source | Downloaded on | Zone | Light Intensity | Unit | Total intensity multipliers | Total lighting intensity | Core/Perims area ratio | Working days | 249
PNNL | 2024-02-01 | All | 0.53921 | W/ft2 | 1988.2232 | 1072.0652 | 41.4% | Saturday | 52
CEC (CBECC 2023) | 2024-06-01 | All | 0.6 | W/ft2 | 2238.1 | 1342.86 | 41.4% | Sunday | 52
[8 empty] | Holiday | 11
Interior lighting Schedules (existing prototypes extracted from the idf files (presented below)
| CEC |  |  |  | PNNL
Hour | CEC-Weekday | CEC-Saturday | CEC-Sunday |  | PNNL-Weekday | PNNL-Saturday | PNNL-Otherday
1 | 0.05 | 0.05 | 0.05 |  | 0.035971 | 0.035971 | 0.035971
2 | 0.05 | 0.05 | 0.05 |  | 0.035971 | 0.035971 | 0.035971
3 | 0.05 | 0.05 | 0.05 |  | 0.035971 | 0.035971 | 0.035971
4 | 0.05 | 0.05 | 0.05 |  | 0.035971 | 0.035971 | 0.035971
5 | 0.05 | 0.05 | 0.05 |  | 0.035971 | 0.035971 | 0.035971
6 | 0.1 | 0.05 | 0.05 |  | 0.071953 | 0.035971 | 0.035971
7 | 0.1 | 0.1 | 0.05 |  | 0.071953 | 0.071953 | 0.035971
8 | 0.3 | 0.1 | 0.05 |  | 0.21586 | 0.071953 | 0.035971
9 | 0.65 | 0.3 | 0.05 |  | 0.64758 | 0.21586 | 0.035971
10 | 0.65 | 0.3 | 0.05 |  | 0.64758 | 0.21586 | 0.035971
11 | 0.65 | 0.3 | 0.05 |  | 0.64758 | 0.21586 | 0.035971
12 | 0.65 | 0.3 | 0.05 |  | 0.64758 | 0.21586 | 0.035971
13 | 0.65 | 0.15 | 0.05 |  | 0.64758 | 0.10792 | 0.035971
14 | 0.65 | 0.15 | 0.05 |  | 0.64758 | 0.10792 | 0.035971
15 | 0.65 | 0.15 | 0.05 |  | 0.64758 | 0.10792 | 0.035971
16 | 0.65 | 0.15 | 0.05 |  | 0.64758 | 0.10792 | 0.035971
17 | 0.65 | 0.15 | 0.05 |  | 0.64758 | 0.10792 | 0.035971
18 | 0.35 | 0.05 | 0.05 |  | 0.35976 | 0.035971 | 0.035971
19 | 0.3 | 0.05 | 0.05 |  | 0.21586 | 0.035971 | 0.035971
20 | 0.3 | 0.05 | 0.05 |  | 0.21586 | 0.035971 | 0.035971
21 | 0.2 | 0.05 | 0.05 |  | 0.14391 | 0.035971 | 0.035971
22 | 0.2 | 0.05 | 0.05 |  | 0.14391 | 0.035971 | 0.035971
23 | 0.1 | 0.05 | 0.05 |  | 0.071953 | 0.035971 | 0.035971
24 | 0.05 | 0.05 | 0.05 |  | 0.035971 | 0.035971 | 0.035971
Sum of intensity multiplier | 8.1 | 2.8 | 1.2 |  | 7.555 | 2.0146 | 0.035971
| Same as Small Office | Same as Small Office | Same as Small Office

## Ext Lighting
Exterior Lighting - OfficeMedium
Motion Controlled Luminaires (W) | Non-motion Controlled Luminaires (W) | Total (W) | Source
1860.2954 | 856.2397 | 2716.5351 | Title 24, 2022
Exterior Lighting
Items (Assume LZ2) | Assumptions [2019 Outdoor Lighting CASE Report & PNNL 90.1-2010 TSD] |  | Unit | Lighting Power Allowance [T24, 2025, Table 140.7-A & 140.7-B] | Unit | Exterior Lighting Power (W)
IWA (Initial Wage Allowance) |  |  |  | 200 | (W) | 200
Parking area | 400 ft² for every parking space [2019 Lighting CASE report, Appendix H] 1 parking space per 250 ft² of gross building area [2019 Lighting CASE report,Table 38] | 85805.0197 | (ft²) | 0.019 | (W/ft²) | 1630.2954
Building Entrance | 2 building entrance (1 per 10,000 ft² footprint) | 2 | (count) | 15 | (W/ea) | 30
Hardscape Ornamental Light | 0.1 ft² per 1 ft² of gross building area for hardscape ornamental light [2019 Lighting CASE report,Table 36] | 5362.8137 | (ft²) | 0.007 | (W/ft²) | 37.5397
Building façade | 0.1 W per ft² of facade area Façade Area* = Perimeter × 0.5 × 30 ft (30 ft is the max height that is lit) The 0.5 factor assumes that only half of the perimeter walls are lit. -Formula is developed based on the 2019 Outdoor Lighting CASE report | 8187 | (ft²) | 0.1 | (W/ft²) | 818.7
Motion controlled Luminaires | [5 empty] | 1860.2954
Non-motion-controlled Luminaires | [5 empty] | 856.2397
Total | [5 empty] | 2716.5351
*Developed based on 2019 Outdoor Lighting CASE Report
Perimeter (ft) | 545.8
Total floor area (ft²) | 53628.1373
Floors (above ground) | 3

## Equipment
Equipment - OfficeMedium
Space Type | Plug load Power Density (W/ft²) | Gas Power Density (Btu/hr-ft²) | Refrigeration Power Density (W/ft²) | Source
Office Area (>250 square feet) | 0.7 |  |  | Proposed Updates to Equipment Power Densities and Schedules in the 2028 Energy Code Nonresidential and Multifamily Alternative Calculation Method (NRMFACM) Reference Manual, August 7, 2025
Convention, Conference, Multipurpose and Meeting Area | 1 |  |  | T24 2022 - Appendix 5.4A
Lobby, Main Entry | 0.5
Storage (General) | 0.2
Electrical, Mechanical, Telephone Rooms | 3
IT Room (EPD 12) | 12 |  |  | Feedback from TAG team
Restrooms | 0 |  |  | T24 2022 - Appendix 5.4A
Lounge, Breakroom, or Waiting Area | 1
Stairwell | 0
Corridor Area | 0
Plenum | 0
Elevator
Vintage | Class | Number of elevators (ne) | Cab Lighting Power Limit (W/ft2) | Fan Power Limit (W/CFM) | Cab Ventilation Fan & Lighting Shutoff | Design Motor Load (W) | Fan Load (W) | Lighting Load (W) | Total (W) | Note
Existing | F/G | 2 | 1.14 | 0.33 | When stopped and unoccupied with doors closed for over 15 minutes, cab interior lighting and ventilation shall be de-energized until required for operation. | 6326 | 165 | 68.17 | 6559.17 | Design load is calculated according to ISO 25745-2 method using Class F/G. Cab lighting and fan requirements are based on ASHRAE 90.1 2013.
New Construction | E | 2 | 0.6 | 0.33 | When the elevator cab is stopped and unoccupied with doors closed for over 15 minutes, the cab interior lighting and ventilation fans shall be switched off until elevator cab operation resumes. | 3292.92 | 165 | 35.88 | 3493.8 | Design load is calculated according to ISO 25745-2 method using Class E. Cab lighting and fan requirements are based on T24 2025 §120.6 (f).
Medium Office Elevator Calculations
Symbol | Definition | Value | Units | Source
E | Annual energy consumption of the elevator - Existing | 31370.62 | kWh/year | Calculated
| Annual energy consumption of the elevator - New Construction | 16329.61 | kWh/year | Calculated
C1 | Running-energy coefficient | 3.65 for Class E; 5.47 for Class F | Coefficient | ISO 25745-2 Table 7
C2 | Idle/standby coefficient | 800 for Class E; 1,600 for Class F | Coefficient | ISO 25745-2 Table 7
Q | Rated load of elevator | 1361 | kg | Assumed for all prototypes
Elevator Size | Cab floor area | 29.9 | ft^2 | W=6.781 ft, L=4.406 ft; assumed based on representative manufacturer
CFM | Cab fan airflow | 250 | cfm | Assumed for multifamily and commercial prototypes
cat | Usage category | 2 | - | ISO 25745-2 Table A.1
d | Operating days per year | 260 | days/year | ISO 25745-2 Table A.1
nf | Number of floors | 3 | floors | Prototype assumptions
h | Floor-to-floor height | 3.96 | m | Prototype assumptions
v | Elevator lift speed | 1 | m/s | ISO 25745-2 Table A.1
nd | Number of trips per day | 125 | trips/day | ISO 25745-2 Table A.1
S_pct | Percent of average travel distance | 0.67 | % | ISO 25745-2 Table 2
a | Acceleration | 1 | m/s^2 | Annex B of ISO 25745-2
j | Jerk | 1.25 | m/s^3 | Annex B of ISO 25745-2
td | Door time | 8 | seconds | Annex B of ISO 25745-2
S_av | Average distance traveled per trip | 7.96 | m/trip | Calculated (nf * h * S_pct)
t_av | Average trip time | 17.76 | seconds/trip | Calculated (S_av/v + v/a + a/j + td)
t_nr | Time not running per day | 23.38 | hours/day | Calculated (24 - nd * t_av)
Standby Hours | Annual standby hours | 8599.67 | hours/year | Calculated (24*(365-d)+t_nr*d)
Total light level | Total light level | 40 | lm/ft2 | PNNL Protoypes
EFLH | Equivalent full load hours | 4959 | hours | Calculated using the elevator schedule
Background Data [To be deleted prior to publication]
Equipment (Plug Load )- Prototypes comparison
|  |  |  | CEC | Note
|  |  | Core Zones | 1.5 W/ft2
Perimeter 3,1
Perimeter 2,4
|  |  | Elevator | 10000 W
|  |  | Elevatoir_lights_Fan |  |  | 61.9%
|  |  | Escalator | 3930 W
Yearly Load multiplier
|  | Office Area | [7 empty] | Elevator | [5 empty] | Escalator (only CEC) |  |  | Lights_Fan (ONLY PNNL)
|  | CEC 2022 |  |  | PNNL 2022 |  |  |  |  | CEC 2022 |  |  | PNNL 2022 |  |  | CEC 2022 |  |  | PNNL 2022
Hour |  | CEC-Weekday | CEC-Saturday | CEC-Sunday | PNNL-Weekday | PNNL-Saturday | PNNL-Sunday |  |  | CEC-Weekday | CEC-Saturday | CEC-Sunday | PNNL-Weekday | PNNL-Saturday | PNNL-Sunday | CEC-Weekday | CEC-Saturday | CEC-Sunday | PNNL-Weekday | PNNL-Saturday | PNNL-Sunday
1 |  | 0.05 | 0.05 | 0.05 | 0.30767 | 0.23076 | 0.23076 |  |  | 0 | 0 | 0 | 0.12 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 |  | 0.05 | 0.05 | 0.05 | 0.30767 | 0.23076 | 0.23076 |  |  | 0 | 0 | 0 | 0.12 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 |  | 0.05 | 0.05 | 0.05 | 0.30767 | 0.23076 | 0.23076 |  |  | 0 | 0 | 0 | 0.12 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 |  | 0.05 | 0.05 | 0.05 | 0.30767 | 0.23076 | 0.23076 |  |  | 0 | 0 | 0 | 0.12 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 |  | 0.05 | 0.05 | 0.05 | 0.30767 | 0.23076 | 0.23076 |  |  | 0 | 0 | 0 | 0.12 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 |  | 0.1 | 0.05 | 0.05 | 0.30767 | 0.23076 | 0.23076 |  |  | 0 | 0 | 0 | 0.12 | 0.12 | 0 | 1 | 1 | 0 | 0 | 0 | 0
7 |  | 0.1 | 0.1 | 0.05 | 0.38123 | 0.38123 | 0.28593 |  |  | 0 | 0 | 0 | 0.12 | 0.12 | 0 | 1 | 1 | 0 | 0 | 0 | 0
8 |  | 0.3 | 0.1 | 0.05 | 0.38123 | 0.38123 | 0.28593 |  |  | 0.35 | 0.16 | 0 | 0.35 | 0.16 | 0 | 1 | 1 | 0 | 0.35 | 0.16 | 0
9 |  | 0.9 | 0.3 | 0.05 | 0.85778 | 0.47654 | 0.28593 |  |  | 0.69 | 0.14 | 0 | 0.69 | 0.14 | 0 | 1 | 1 | 0 | 0.69 | 0.14 | 0
10 |  | 0.9 | 0.3 | 0.05 | 0.85778 | 0.47654 | 0.28593 |  |  | 0.43 | 0.21 | 0 | 0.43 | 0.21 | 0 | 1 | 1 | 0 | 0.43 | 0.21 | 0
11 |  | 0.9 | 0.3 | 0.05 | 0.85778 | 0.47654 | 0.28593 |  |  | 0.37 | 0.18 | 0 | 0.37 | 0.18 | 0 | 1 | 1 | 0 | 0.37 | 0.18 | 0
12 |  | 0.9 | 0.3 | 0.05 | 0.85778 | 0.47654 | 0.28593 |  |  | 0.43 | 0.25 | 0 | 0.43 | 0.25 | 0 | 1 | 1 | 0 | 0.43 | 0.25 | 0
13 |  | 0.9 | 0.15 | 0.05 | 0.76247 | 0.33358 | 0.28593 |  |  | 0.58 | 0.21 | 0 | 0.58 | 0.21 | 0 | 1 | 1 | 0 | 0.58 | 0.21 | 0
14 |  | 0.9 | 0.15 | 0.05 | 0.85778 | 0.33358 | 0.28593 |  |  | 0.48 | 0.13 | 0 | 0.48 | 0.13 | 0 | 1 | 1 | 0 | 0.48 | 0.13 | 0
15 |  | 0.9 | 0.15 | 0.05 | 0.85778 | 0.33358 | 0.28593 |  |  | 0.37 | 0.08 | 0 | 0.37 | 0.12 | 0 | 1 | 1 | 0 | 0.37 | 0.08 | 0
16 |  | 0.9 | 0.15 | 0.05 | 0.85778 | 0.33358 | 0.28593 |  |  | 0.37 | 0.04 | 0 | 0.37 | 0.12 | 0 | 1 | 1 | 0 | 0.37 | 0.04 | 0
17 |  | 0.9 | 0.15 | 0.05 | 0.85778 | 0.33358 | 0.28593 |  |  | 0.46 | 0.05 | 0 | 0.46 | 0.12 | 0 | 1 | 1 | 0 | 0.46 | 0.05 | 0
18 |  | 0.5 | 0.05 | 0.05 | 0.47654 | 0.28593 | 0.28593 |  |  | 0.62 | 0.06 | 0 | 0.62 | 0.12 | 0 | 1 | 1 | 0 | 0.62 | 0.06 | 0
19 |  | 0.3 | 0.05 | 0.05 | 0.38123 | 0.28593 | 0.23076 |  |  | 0.2 | 0 | 0 | 0.12 | 0.12 | 0 | 1 | 1 | 0 | 0.12 | 0 | 0
20 |  | 0.3 | 0.05 | 0.05 | 0.38123 | 0.23076 | 0.23076 |  |  | 0.12 | 0 | 0 | 0.12 | 0.12 | 0 | 1 | 0 | 0 | 0.04 | 0 | 0
21 |  | 0.2 | 0.05 | 0.05 | 0.38123 | 0.23076 | 0.23076 |  |  | 0.04 | 0 | 0 | 0.12 | 0.12 | 0 | 1 | 0 | 0 | 0.04 | 0 | 0
22 |  | 0.2 | 0.05 | 0.05 | 0.38123 | 0.23076 | 0.23076 |  |  | 0.04 | 0 | 0 | 0.12 | 0.12 | 0 | 1 | 0 | 0 | 0 | 0 | 0
23 |  | 0.1 | 0.05 | 0.05 | 0.38123 | 0.23076 | 0.23076 |  |  | 0 | 0 | 0 | 0.12 | 0.12 | 0 | 1 | 0 | 0 | 0 | 0 | 0
24 |  | 0.05 | 0.05 | 0.05 | 0.38123 | 0.23076 | 0.23076 |  |  | 0 | 0 | 0 | 0.12 | 0.12 | 0 | 1 | 0 | 0 | 0 | 0 | 0
|  | 10.5 | 2.8 | 1.2 | 12.9972 | 7.4467 | 6.2002

## Schedules
Schedules - OfficeMedium
Zone | Schedule Category | Schedule | Source | Type | Hour
[5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
All zones except for IT Rooms, Storage, Stairway, and Mechanical_Electrical | Office | Occupancy | T24 2022 - Appendix 5.4B, [Office] Updated base on Plug load and schedules project with CEC, 2025 | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
All zones except for IT Rooms, Storage, Stairway, and Mechanical_Electrical | Office | Lights | T24 2022 - Appendix 5.4B, [Office] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.35 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
All zones except for IT Rooms, Storage, Stairway, and Mechanical_Electrical | Office | ElecEquipment | Plug load and schedules project with CEC, 2025 | Weekday | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.74 | 0.87 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.5 | 0.45 | 0.45 | 0.45
|  |  |  | Saturday | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43
|  |  |  | Sunday | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43
All zones except for IT Rooms, Storage, Stairway, and Mechanical_Electrical | Office | HVACAvail | T24 2022 - Appendix 5.4B, [Office] Updated base on Plug load and schedules project with CEC, 2025 | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
All zones except for IT Rooms, Storage, Stairway, and Mechanical_Electrical | Office | ServiceHotWater | T24 2022 - Appendix 5.4B, [Office] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05
|  |  |  | Saturday | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04
|  |  |  | Sunday | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04
All zones except for IT Rooms, Storage, Stairway, and Mechanical_Electrical | Office | Infiltration | T24 2022 - Appendix 5.4B, [Office] Updated base on Plug load and schedules project with CEC, 202 | Weekday | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
All zones except for IT Rooms, Storage, Stairway, and Mechanical_Electrical | Office | HtgSetpt |  | Weekday | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
|  |  |  | Saturday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  |  | Sunday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
All zones except for IT Rooms, Storage, Stairway, and Mechanical_Electrical | Office | ClgSetpt |  | Weekday | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
|  |  |  | Saturday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
|  |  |  | Sunday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
Data
IT room | Data | Occupancy | T24 2022 - Appendix 5.4B, [Data] Updated base on office schedule | Weekday | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.25 | 0.65 | 0.65 | 0.65 | 0.65 | 0.6 | 0.6 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.25 | 0.1 | 0.05 | 0.05 | 0.05 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0
IT room | Data | Lights | T24 2022 - Appendix 5.4B, [Data] Updated base on office schedule | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.7 | 0.8 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.8 | 0.35 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05
IT room | Data | HVACAvail | T24 2022 - Appendix 5.4B, [Data] | Weekday | bar: Hour 1 to Hour 24
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
IT room | Data | ServiceHotWater | T24 2022 - Appendix 5.4B, [Data] | Weekday | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.9 | 0.9 | 0.5 | 0.5 | 0.7 | 0.5 | 0.5 | 0.5 | 0.1 | 0.1 | 0.1 | 0.1 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IT room | Data | Infiltration | T24 2022 - Appendix 5.4B, [Data] | Weekday | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  |  | Saturday | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  |  | Sunday | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
IT room | Data | ClgSetpt | Based on Activity level and thermostat setpoint | Weekday | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
|  |  |  | Saturday | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
|  |  |  | Sunday | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
Storage, Stairway, and Mechanical_Electrical
Storage, Stairway, and Mechanical_Electrical | Ancillary | Occupancy | T24 2022 - Appendix 5.4B, [Data] Updated base on office schedule | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
Storage, Stairway, and Mechanical_Electrical | Ancillary | Lights | T24 2022 - Appendix 5.4B, [Data] Updated base on office schedule | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.35 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Storage, Stairway, and Mechanical_Electrical | Ancillary | HVACAvail | T24 2022 - Appendix 5.4B, [Data] | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Storage, Stairway, and Mechanical_Electrical | Ancillary | ServiceHotWater | T24 2022 - Appendix 5.4B, [Data] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Storage, Stairway, and Mechanical_Electrical | Ancillary | Infiltration | T24 2022 - Appendix 5.4B, [Data] | Weekday | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
Storage, Stairway, and Mechanical_Electrical | Ancillary | HtgSetpt | Engineering Judgement | Weekday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  |  | Saturday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  |  | Sunday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Storage, Stairway, and Mechanical_Electrical | Ancillary | ClgSetpt | Engineering Judgement | Weekday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
|  |  |  | Saturday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
|  |  |  | Sunday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
Other | [28 empty] | EFLH
Stairway | Building | Elevator | T24 2022 - Appendix 5.4B, [Office] Updated base on Plug load and schedules project with CEC, 202 | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 4959
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Building | ExtLightingNonMotionCtrl |  | Weekday | bar: Hour 1 to Hour 24
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
| Building | ExtLightingMotionCtrl |  | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Office | Building | FunctionalAreaPeopleActivityLevel | Based on Activity level schedules in CEC Prototypes | Weekday | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
|  |  |  | Saturday | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
|  |  |  | Sunday | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
IT room | Building | ComputerRoomPeopleActivityLevel | Based on Activity level schedules in CEC Prototypes | Weekday | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
|  |  |  | Saturday | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
|  |  |  | Sunday | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
Conference room | Building | MeetingAreaPeopleActivityLevel | Based on Activity level schedules in CEC Prototypes | Weekday | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117
|  |  |  | Saturday | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117
|  |  |  | Sunday | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117
Corridor, Stair, Lobby, Restroom, Mech, Storage, Break | Building | CommonAreaPeopleActivityLevel | Based on Activity level schedules in CEC Prototypes | Weekday | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147
|  |  |  | Saturday | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147
|  |  |  | Sunday | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147
Background Data [To be deleted prior to publication] | bar: Hour 1
Operating Schedule
| System Capacity fraction | Developed based on CEC and CEUS | Office Zones | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.7 | 0.5 | 0.3 | 0.2 | 0.2 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.005 | 0 | 0 | 0 | 0 | 0
Alternative HVAC System Operating
| Alternative HVAC System Operating | Developed based on CEC schedules and CEUS operating hours | Office Closed Zones | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Otherday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Office Open Zones | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Otherday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Equipment (Plug load) (Nees to be updated based on the Plug load project with CEC) | T24 2022 - Appendix 5.4A | Office | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05
|  |  |  | Saturday | 0.43 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  |  |  | Sunday | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43
Background Data [To be deleted prior to publication] | bar: Hour 1
| Equipment | PNNL | Office Zones | Weekday | 0.40948 | 0.40948 | 0.40948 | 0.40948 | 0.40948 | 0.40948 | 0.47975 | 0.47975 | 0.95951 | 0.95951 | 0.95951 | 0.95951 | 0.90193 | 0.95951 | 0.95951 | 0.95951 | 0.95951 | 0.47975 | 0.1919 | 0.1919 | 0.1919 | 0.1919 | 0.1919 | 0.16379
|  |  |  | Saturday | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379
|  |  |  | Sunday | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379

## Energy Usage (hidden)
CalBEM Energy Consumption - OfficeMedium | [7 empty] | National Average (EnergyStar Portfolio Manager) |  |  |  | CEUS Energy Consumption - OfficeLarge
Prototype | CZ | CalBEM Electricity EUI (KBTU/ft²) | CalBEM Gas EUI (KBTU/ft²) | CalBEM Total EUI (KBTU/ft²) | New Construction Electricity EUI (KBTU/ft²) | New Construction Gas EUI (KBTU/ft²) | New Construction Total EUI (KBTU/ft²) | National Average | Acceptable RangeRange (25% Higher) | Acceptable RangeRange (25% Lower) | National Average Acceptable Range | Prototype | CZ | Total Floorspace (Thousand of ft2) | CEUS 2022 Electric Energy Intensity (kWh/ft²) | CEUS 2022 Annual Gas Intensity (kWh/ft²) | CEUS 2022 Total EUI (kBtu/ft²) | Acceptable Range (25% Higher) | Acceptable Range (25% Lower) | CEUS 2022 Acceptable Range
HotelSmall | 1 | [6 empty] | 59.8 | 74.75 | 44.85 | 29.9 | OfficeLarge | 1 | 5279 | 16.7 | 5.01 | 74.0745 | 92.5932 | 55.5559 | 37.0373
| 2 | [6 empty] | 65.5 | 81.875 | 49.125 | 32.75 |  | 2 | 12449 | 15.2 | 6.24 | 73.1533 | 91.4416 | 54.865 | 36.5766
| 3 | [6 empty] | 62.2 | 77.75 | 46.65 | 31.1 |  | 3 | 242565 | 14.3 | 4.83 | 65.2716 | 81.5895 | 48.9537 | 32.6358
| 4 | [6 empty] | 67.7 | 84.625 | 50.775 | 33.85 |  | 4 | 137610 | 14.4 | 4.76 | 65.3739 | 81.7174 | 49.0304 | 32.687
| 5 | [6 empty] | 59.7 | 74.625 | 44.775 | 29.85 |  | 5 | 3834 | 8.6 | 9.32 | 61.143 | 76.4288 | 45.8573 | 30.5715
| 6 | [6 empty] | 69 | 86.25 | 51.75 | 34.5 |  | 6 | 109980 | 10.9 | 4.88 | 53.8414 | 67.3017 | 40.381 | 26.9207
| 7 | [6 empty] | 64.9 | 81.125 | 48.675 | 32.45 |  | 7 | 76710 | 14.8 | 9.36 | 82.4339 | 103.0424 | 61.8254 | 41.217
| 8 | [6 empty] | 65.9 | 82.375 | 49.425 | 32.95 |  | 8 | 177013 | 10.4 | 4.24 | 49.9517 | 62.4396 | 37.4638 | 24.9758
| 9 | [6 empty] | 65.9 | 82.375 | 49.425 | 32.95 |  | 9 | 240000 | 10.9 | 4.38 | 52.1354 | 65.1692 | 39.1015 | 26.0677
| 10 | [6 empty] | 66.4 | 83 | 49.8 | 33.2 |  | 10 | 65927 | 11.9 | 7.21 | 65.2033 | 81.5041 | 48.9025 | 32.6017
| 11 | [6 empty] | 68.6 | 85.75 | 51.45 | 34.3 |  | 11 | 18413 | 11.4 | 4.29 | 53.5343 | 66.9179 | 40.1507 | 26.7671
| 12 | [6 empty] | 67.8 | 84.75 | 50.85 | 33.9 |  | 12 | 171620 | 14.4 | 6.12 | 70.0142 | 87.5178 | 52.5107 | 35.0071
| 13 | [6 empty] | 68.3 | 85.375 | 51.225 | 34.15 |  | 13 | 19959 | 15.9 | 3.71 | 66.9093 | 83.6366 | 50.182 | 33.4547
| 14 | [6 empty] | 69 | 86.25 | 51.75 | 34.5 |  | 14 | 18934 | 9.8 | 4.4 | 48.4504 | 60.563 | 36.3378 | 24.2252
| 15 | [6 empty] | 67.7 | 84.625 | 50.775 | 33.85 |  | 15 | 23127 | 9.7 | 5.14 | 50.6341 | 63.2926 | 37.9756 | 25.317
| 16 | [6 empty] | 70.6 | 88.25 | 52.95 | 35.3 |  | 16 | 39406 | 11.6 | 4.42 | 54.6602 | 68.3253 | 40.9952 | 27.3301
Source: CEUS 2022 Report/Data
And applying FZ-CZ multipliers for converting FZ data to CZ data
We don't have Medium Office specific data from CEUS. The data copied here belongs to the CEUS large office data which our Medium Office prototype falls within that group

## PV (hidden)
PV - TBD

## EV Charger (hidden)
EV Charger - OfficeMedium (TBD)
According To CEUS 2022 and their survey around 2018-2020, only 0.5% of large office buildings have EV chargers
Background Data [To be deleted prior to publication]
CEUS 2022 (Base on Survey 2018) | [7 empty] | The data presented in this worksheet represents the projected number of EV charger ports, or the number of cars that can be charged at the same time, for the year 2022 (last year of CEUC)
|  |  | Has EV Chargers |  |  |  |  | Level 1, 120 volt Charger (No. ports/SqFT) | [8 empty] | Level 2, 240 volt Charger (No. ports/SqFT) | [8 empty] | Level 3, DC fast (No. ports/SqFT) | [8 empty] | Charger Type Unkown (No. ports/SqFT) | [8 empty] | All Chargers Totals (No. ports/SqFT)
Calculation Method | Statewide/ Utility/ FCZ | Building Type | No | Yes | Total | Statewide/ Utility/ FCZ | Building Type | Public Only | Public & Employee | Public & Fleet | Employee Only | Employee & Fleet | Fleet Only | All 3 Types | Unknown | Level 1 Total | Public Only | Public & Employee | Public & Fleet | Employee Only | Employee & Fleet | Fleet Only | All 3 Types | Unknown | Level 2 Total | Public Only | Public & Employee | Public & Fleet | Employee Only | Employee & Fleet | Fleet Only | All 3 Types | Unknown | Level 3 Total | Public Only | Public & Employee | Public & Fleet | Employee Only | Employee & Fleet | Fleet Only | All 3 Types | Unknown | Unkonwn Total | Public Only | Public & Employee | Public & Fleet | Employee Only | Employee & Fleet | Fleet Only | All 3 Types | Unknown | Total
Floorspace-Based | Statewide | Office, Small | 91.63% | 8.371% | 100% | Statewide | Office, Small | 234.6311 | 257.2607 | 0 | 514.2646 | 0 | 22.2217 | 197.9831 | 0 | 1226.3611 | 108.945 | 831.3199 | 0 | 1332.4399 | 101.1641 | 78.5024 | 360.406 | 0 | 2812.7774 | 21.3759 | 0 | 0 | 15.7138 | 0 | 0 | 0 | 0 | 37.0897 | 56.9499 | 42.1476 | 0 | 212.1101 | 0 | 25.742 | 0 | 0 | 336.9496 | 421.9019 | 1130.7282 | 0 | 2074.5284 | 101.1641 | 126.466 | 558.3891 | 0 | 4413.1778
Floorspace-Based | FCZ01 Tot | Office, Small | 88.47% | 11.53% | 100% | FCZ01 Tot | Office, Small | 0 | 0 | 0 | 92.1148 | 0 | 0 | 5.6273 | 0 | 97.7421 | 0 | 290.1537 | 0 | 73.0277 | 95.6646 | 65.7399 | 24.3426 | 0 | 548.9286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9748 | 0 | 24.3426 | 0 | 0 | 52.3174 | 0 | 290.1537 | 0 | 193.1173 | 95.6646 | 90.0824 | 29.9699 | 0 | 698.988
Floorspace-Based | FCZ02 Tot | Office, Small | 87.66% | 12.34% | 100% | FCZ02 Tot | Office, Small | 0 | 0 | 0 | 0 | 0 | 21.0137 | 0 | 0 | 21.0137 | 0 | 189.1229 | 0 | 21.1561 | 0 | 0 | 0 | 0 | 210.279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189.1229 | 0 | 21.1561 | 0 | 21.0137 | 0 | 0 | 231.2926
Floorspace-Based | FCZ03 Tot | Office, Small | 93.39% | 6.61% | 100% | FCZ03 Tot | Office, Small | 0 | 78.751 | 0 | 0 | 0 | 0 | 0 | 0 | 78.751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.8719 | 0 | 0 | 0 | 0 | 0 | 0 | 12.8719 | 0 | 91.6228 | 0 | 0 | 0 | 0 | 0 | 0 | 91.6228
Floorspace-Based | FCZ04 Tot | Office, Small | 82.7% | 17.3% | 100% | FCZ04 Tot | Office, Small | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.11 | 0 | 0 | 0 | 0 | 44.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.9845 | 0 | 0 | 0 | 0 | 0 | 0 | 26.9845 | 0 | 26.9845 | 0 | 44.11 | 0 | 0 | 0 | 0 | 71.0945
Floorspace-Based | FCZ05 Tot | Office, Small | 96.4% | 3.601% | 100% | FCZ05 Tot | Office, Small | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.6347 | 0 | 0 | 0 | 0 | 19.6347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.6347 | 0 | 0 | 0 | 0 | 19.6347
Floorspace-Based | FCZ06 Tot | Office, Small | 93.41% | 6.592% | 100% | FCZ06 Tot | Office, Small | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2848 | 0 | 0 | 0 | 0 | 50.2848 | 0 | 0 | 0 | 50.2848 | 0 | 0 | 0 | 0 | 50.2848
Floorspace-Based | FCZ07 Tot | Office, Small | 91.77% | 8.231% | 100% | FCZ07 Tot | Office, Small | 0 | 0 | 0 | 199.1172 | 0 | 0 | 0 | 0 | 199.1172 | 0 | 229.2222 | 0 | 397.4995 | 0 | 0 | 0 | 0 | 626.7218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229.2222 | 0 | 596.6167 | 0 | 0 | 0 | 0 | 825.839
Floorspace-Based | FCZ08 Tot | Office, Small | 86.72% | 13.28% | 100% | FCZ08 Tot | Office, Small | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.6289 | 0 | 0 | 0 | 0 | 0 | 0 | 77.6289 | 0 | 0 | 0 | 14.8596 | 0 | 0 | 0 | 0 | 14.8596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.6289 | 0 | 14.8596 | 0 | 0 | 0 | 0 | 92.4885
Floorspace-Based | FCZ09 Tot | Office, Small | 90.94% | 9.064% | 100% | FCZ09 Tot | Office, Small | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Floorspace-Based | FCZ10 Tot | Office, Small | 95.6% | 4.399% | 100% | FCZ10 Tot | Office, Small | 0 | 0 | 0 | 27.5268 | 0 | 0 | 0 | 0 | 27.5268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.1608 | 0 | 0 | 0 | 0 | 50.1608 | 0 | 0 | 0 | 77.6876 | 0 | 0 | 0 | 0 | 77.6876
Floorspace-Based | FCZ11 Tot | Office, Small | 87.59% | 12.41% | 100% | FCZ11 Tot | Office, Small | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.1762 | 0 | 0 | 0 | 0 | 89.1762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.1762 | 0 | 0 | 0 | 0 | 89.1762
Floorspace-Based | FCZ12c Tot | Office, Small | 84.94% | 15.06% | 100% | FCZ12c Tot | Office, Small | 148.2736 | 164.5245 | 0 | 144.7477 | 0 | 0 | 181.593 | 0 | 639.1388 | 6.1825 | 0 | 0 | 246.2021 | 0 | 8.495 | 316.4711 | 0 | 577.3507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.3574 | 0 | 0 | 0 | 0 | 49.3574 | 154.456 | 164.5245 | 0 | 440.3072 | 0 | 8.495 | 498.0641 | 0 | 1265.8469
Floorspace-Based | FCZ12i Tot | Office, Small | 94.56% | 5.436% | 100% | FCZ12i Tot | Office, Small | 73.6026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.6026 | 0 | 0 | 0 | 369.1995 | 0 | 0 | 0 | 0 | 369.1995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.854 | 127.4565 | 0 | 0 | 369.1995 | 0 | 0 | 0 | 0 | 496.6561
Floorspace-Based | FCZ13 Tot | Office, Small | 96.48% | 3.519% | 100% | FCZ13 Tot | Office, Small | 0 | 0 | 0 | 22.8017 | 0 | 0 | 0 | 0 | 22.8017 | 36.1985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.1985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8017 | 0 | 0 | 0 | 0 | 22.8017 | 36.1985 | 0 | 0 | 45.6034 | 0 | 0 | 0 | 0 | 81.802
Floorspace-Based | FCZ16 Tot | Office, Small | 99.34% | 0.6613% | 100% | FCZ16 Tot | Office, Small | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.6415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.6415 | 20.2138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.2138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.8554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.8554
Floorspace-Based | FCZ17 Tot | Office, Small | 98.53% | 1.474% | 100% | FCZ17 Tot | Office, Small | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Data (hidden)
Space Function | Electric Equipment Load Intensity | Electric Equipment Load Intensity | LPD
Aging Eye/Low-vision (Corridor Area) |  |  | 2013 | 2016 | 2019 | 2025
Aging Eye/Low-vision (Dining)
Aging Eye/Low-vision (Lobby, Main Entry)
Aging Eye/Low-vision (Lounge/Waiting Area)
Aging Eye/Low-vision (Multipurpose Room)
Aging Eye/Low-vision (Religious Worship Area)
Aging Eye/Low-vision (Restroom)
Aging Eye/Low-vision (Stairwell)
Audience Seating Area
Auditorium Area
Auto Repair / Maintenance Area
Barber, Beauty Salon, Spa Area
Civic Meeting Place Area
Classroom, Lecture, Training, Vocational Areas
Concourse and Atria Area
Convention, Conference, Multipurpose and Meeting Area
Copy Room
Corridor Area
Dining Area (Bar/Lounge and Fine Dining)
Dining Area (Cafeteria/Fast Food)
Dining Area (Family and Leisure)
Electrical, Mechanical, Telephone Rooms
Exercise/Fitness Center and Gymnasium Areas
Financial Transaction Area
Healthcare Facility and Hospitals (Exam/Treatment Room)
Healthcare Facility and Hospitals (Imaging Room)
Healthcare Facility and Hospitals (Medical Supply Room)
Healthcare Facility and Hospitals (Nursery)
Healthcare Facility and Hospitals (Nurse's Station)
Healthcare Facility and Hospitals (Operating Room)
Healthcare Facility and Hospitals (Patient Room)
Healthcare Facility and Hospitals (Physical Therapy Room)
Healthcare Facility and Hospitals (Recovery Room)
Hotel Function Area
Kitchen/Food Preparation Area
Kitchenette or Residential Kitchen
Laboratory, Scientific
Laundry Area
Library (Reading Area)
Library (Stacks Area)
Lobby, Main Entry
Locker Room
Lounge, Breakroom, or Waiting Area
Manufacturing, Commercial & Industrial Work Area (Low Bay)
Manufacturing, Commercial & Industrial Work Area (High Bay)
Manufacturing, Commercial & Industrial Work Area (Precision)
Museum Area (Exhibition/Display)
Museum Area (Restoration Room)
Office Area (>250 square feet)
Office Area (<250 square feet)
Parking Garage Area (Parking Zone and Ramps)
Parking Garage Area (Daylight Adaptation Zones)
Pharmacy Area
Retail Sales Area (Grocery Sales)
Retail Sales Area (Retail Merchandise Sales)
Retail Sales Area (Fitting Room)
Religious Worship Area
Restrooms
Stairwell
Storage, Commercial/Industrial (Warehouse)
Storage, Commercial/Industrial (Refrigerated)
Storage, Commercial/Industrial (Shipping & Handling)
Storage (General)
Sports Arena - Playing Area (> 5,000 Spectators)
Sports Arena - Playing Area (2,000 - 5,000 Spectators)
Sports Arena - Playing Area (< 2,000 Spectators)
Sports Arena - Playing Area (Recreational)
Theater Area (Motion Picture)
Theater Area (Performance)
Transportation Function (Baggage Area)
Transportation Function (Ticketing Area)
Videoconferencing Studio
High-Rise Residential Living Spaces
Hotel/Motel Guest Room
All other
Attic
Reception Area
Elevator
Plenum
IT Room (EPD 12)
Computer Room (EPD 20)
Server Room (EPD 45)

## Weights (hidden)
% of floor area per CZ and vintage bin - OfficeLarge | [5 empty] | We don't have Medium Office specific data from CEUS. The data copied here belongs to the CEUS large office data which our Medium Office prototype falls within that group
Prototype | CZ | Vintage
Prototype | CZ | Pre-1978 | 1978-1997 | 1998-2007 | 2008-2018
OfficeLarge | 1 |  |  |  |  | 0% | Floor area distribution of CA office buildings (CEUS 2022)
| 2 |  |  |  |  | 0% | Office, Small | Office, Medium | Office, Large
| 3 |  |  |  |  | 0% | 35.39% | 29.43% | 35.18%
| 4 |  |  |  |  | 0%
| 5 |  |  |  |  | 0%
| 6 |  |  |  |  | 0%
| 7 |  |  |  |  | 0%
| 8 |  |  |  |  | 0%
| 9 |  |  |  |  | 0%
| 10 |  |  |  |  | 0%
| 11 |  |  |  |  | 0%
| 12 |  |  |  |  | 0%
| 13 |  |  |  |  | 0%
| 14 |  |  |  |  | 0%
| 15 |  |  |  |  | 0%
| 16 |  |  |  |  | 0%
Statewide
Source: CEUS 2022 dataset