## Notes
Data Sources
Dataset | Dodge 2023
| Commercial End-Use Survey (CEUS) 2022 | https://www.energy.ca.gov/publications/2023/2022-california-commercial-end-use-survey-ceus-final-report
| Commercial Buildings Energy Consumption Survey (CBECS) 2018 | https://www.eia.gov/consumption/commercial/data/2018/index.php
| ComStock 2023 | https://www.nrel.gov/buildings/comstock
Prototype | Pacific Northwest National Laboratory (PNNL) Outpatient prototype (90.1-2022) | https://www.energycodes.gov/prototype-building-models#Commercial
Codes | Title 24, part 6, referred to as T24 (1984, 1992,1998, 2001, 2005, 2008, 2013, 2016,2019, 2022, 2025) | https://www.energy.ca.gov/publications/2025/2025-building-energy-efficiency-standards-residential-and-nonresidential | 2025
|  | https://codes.iccsafe.org/codes/united-states/california | 2010+
| American Society of Heating, Refrigerating and Air-Conditioning Engineers (ASHRAE) 90.1 (2022) | https://www.ashrae.org/technical-resources/standards-and-guidelines/read-only-versions-of-ashrae-standards
| Code of Federal Regulations (CFR) Title 10 (2008, 2010) | https://www.govinfo.gov/content/pkg/FR-2009-03-23/pdf/FR-2009-03-23.pdf
| ASHRAE 170/OSHPD | https://www.ashrae.org/technical-resources/bookstore/health-care-facilities-resources
| 2022 California Mechanical Code (Title 24, Part 4) | https://up.codes/viewer/california/ca-mechanical-code-2022
| Facility Guidelines Institute Codes (FGI) 2022 Guidelines for Design and Construction of Outpatient Facilities | https://onesource.fgicodes.org/products/2022-guidelines-for-design-and-construction-of-outpatient-facilities
Other | Alternative Calculation Method (ACM) (2022) | https://www.energy.ca.gov/publications/2022/2022-nonresidential-and-multifamily-alternative-calculation-method-reference
| Nonres ACM 2022, Appendix 5.4A and Appendix 5.4B | https://www.energy.ca.gov/publications/2022/2022-nonresidential-and-multifamily-alternative-calculation-method-reference
| 2022 Reduced infiltration CASE report | https://title24stakeholders.com/wp-content/uploads/2020/10/2022-T24-Final-CASE-Report_Reduce-Infiltration.pdf
| 2019 Outdoor Lighting CASE Report | https://title24stakeholders.com/wp-content/uploads/2016/10/T24-2019-CASE-Study-Results-Report-Outdoor-Sources_Final_with-Attachments.pdf
| PNNL 20405, 2011 | https://www.pnnl.gov/main/publications/external/technical_reports/PNNL-20405.pdf
| PNNL-26949 | https://www.pnnl.gov/main/publications/external/technical_reports/PNNL-26949.pdf
| Air leakage Memo, NORESCO, 2025 | https://2050partners.sharepoint.com/:w:/r/sites/CalBEMCollaborativeEfforts/_layouts/15/Doc.aspx?sourcedoc=%7B3BEF8F74-7FAC-44F2-A70C-D76617660066%7D&file=Infiltration_rate_report_14May2025-Short-Version.docx&wdLOR=c494C5A60-5F8A-438B-874B-578DCB850072&action=default&mobileredirect=true
| 2019 High Efficiency Fume Hoods in Laboratory Spaces CASE Report | https://title24stakeholders.com/wp-content/uploads/2017/09/2019-T24-CASE-Report_Fume-Hoods_Final_September-2017.pdf?
| Targeting 100! Envisioning the High Performance Hospital: Implications for a New, Low Energy, High Performance Prototype | https://idl.be.uw.edu/wp-content/uploads/sites/32/2017/08/Targeting100_FullReport_063010.pdf
| ASHRAE's Advanced Energy Design Guide for Large Hospitals-50% (AEDG) | https://www.ashrae.org/technical-resources/aedgs/50-percent-aedg-free-download
| American Hospital Association (AHA) Statistics data for Hospital | https://www.ahadata.com/aha-hospital-statistics
| AEDG TSD: Bonnema, E., Doebber, I., Pless, S., Torcellini, P. (2010). NREL/TP-550-46314. | https://docs.nlr.gov/docs/fy10osti/46314.pdf
| Yousefi, F., Athalye, R., (2025), "Determining Vintage Bins for Prototype Development: An Analysis of California Commercial Buildings," ASHRAE Annual Conference | https://www.thefreelibrary.com/Determining+Vintage+Bins+for+Prototype+Development%3a+An+Analysis+of...-a0879271125
| ENERGY STAR certified commercial water heaters | https://www.energystar.gov/productfinder/product/certified-commercial-water-heaters/results?fuel_filter=Gas&markets_filter=United+States
| Grainger gas tank water heaters (sizes below commercial, e.g. 30–75 kBtu/h) | https://www.grainger.com/category/plumbing/water-heaters/gas-tank-water-heaters
| Grainger electric tank water heaters | https://www.grainger.com/category/plumbing/water-heaters/electric-tank-water-heaters
Construction Rate
* the general healthcare trends which apply to the broader Healthcare category, not outpatient.
Notes
Outpatient | An outpatient healthcare facility (also called an ambulatory care facility, outpatient clinic, or clinic) provides diagnostic, treatment, or surgical services to patients who go home the same day. There is no overnight inpatient stay. The building may be freestanding or attached to a hospital. It typically operates about 8–10 hours per day, not 24/7. FGI Guidelines for Design and Construction of Outpatient Facilities (2022), Part 2, splits this building family by program (surgery, imaging, urgent care, primary care, and others). Those programs do not share the same layout or HVAC, so they are not all represented by one energy model. This CalBEM prototype is a ~41,000 ft², three-story outpatient surgical/diagnostic building (PNNL/NREL geometry). Floor 1 is surgery and recovery; floors 2–3 are exam, office, and physical therapy. It represents FGI 2.7 Outpatient Surgery, with 2.3 Imaging, 2.2 General and Specialty Medical Services, and 2.12 Rehabilitation Therapy as they appear on that floor plan. HVAC follows healthcare ventilation (ASHRAE 170 / FGI / CMC Table 4-A) for procedure, imaging, and operating rooms. This prototype is not: a hospital (overnight / 24-hour inpatient care; CBECS inpatient mean 264,800 ft²); a medical office without diagnostic equipment (Office prototype); a typical small diagnostic medical office (CBECS mean 9,900 ft²); an urgent care, only, birth center, infusion, freestanding ED, endoscopy-only, dialysis, behavioral health, mobile unit, or dental facility (FGI 2.4–2.6, 2.8–2.11, 2.13–2.14). Those types would need a different layout and model.
EIA, 2018 CBECS | On average, hospitals were 264,800 square feet per building, but outpatient health care buildings averaged 13,700 square feet.
Source | https://www.eia.gov/consumption/commercial/

## Prototype
NORESCO, Updated September 2026
Outpatient
Characteristic | Value | Data Sources
Building Type | Outpatient
Building Category | Nonresidential
Version | v2-0
Vintages | 4 Vintages: Pre-1978 , 1978-1997 ,1998-2007 , 2008-2018 New Construction (2019+) | Based on the vintage bin analysis. A summary of the findings is presented in the following paper, with a link provided in the Notes tab: Yousefi, F., Athalye, R. (2025). “Determining Vintage Bins for Prototype Development: An Analysis of California Commercial Buildings.” ASHRAE Annual Conference.
Shape |  | The analysis uses prototype geometry originally developed by PNNL.
Total Floor Area (ft²) | 40950 | Assumption; based on AEDG TSD (Table ES-1 / Table 4-2 (41,000 ft²); Appendix D (40,946 ft²). Rounded.)
Aspect Ratio | n/a | Assumption; based on AEDG TSD §4.2, Figures 4-5–4-7 (non-rectangular plates)
Number of Floors | 3 | Assumption; based on AEDG TSD (Table ES-1 / Table 4-2
Roof type | Flat roof | Assumption; based on AEDG TSD (Table ES-1 / Table 4-2 (insulation entirely above deck); §5.3
WWR | North: 20.5%, East:19.1%, South: 24.1%, West: 12.9% Average Total: 20% | Assumption; based on AEDG TSD (Average: Table 4-2 / Table 5-1. By façade: Appendix D)
Shading Geometry | Fixed entrance canopy (12 ft) | Assumption; based on review feedback
Floor to floor height (feet) | 10 ft | Assumption; based on AEDG Table TSD (5-1 ceiling 10 ft; no plenums, §5.2.1)
Floor to ceiling height (feet) | 10 ft | Assumption; based on AEDG Table TSD (5-1 ceiling 10 ft; no plenums, §5.2.1)
Glazing sill height (feet) | 3 ft (4 ft high windows) | Typical window sill height-PNNL
Above grade wall area (ft²) | 16716.3529
Gross wall area (ft²) | 16716.3529
Roof area (ft²) | 14778.849
Underground Gross Wall Area (ft²) | 0

## Zones
Proposed Layout - Outpatient
Building | Space/ Thermal Zone | Space Type Primarily from [T24, 2022 Appendix 5.4A] - See Notes column | HVAC System Name | Schedule Category | Conditioned (Y/N) | Area Fraction | Area (ft²) | Volume (ft³) | Multipliers | Number of People | People (Persons/1,000 ft²) [T24, 2025,Table 120.1-A and NACM Appendix 5.4A] | Notes
Outpatient | Floor 1 Anesthesia | Healthcare Facility and Hospitals (Exam/Treatment Room) | AHU-4 | Health | Yes | 0.2638% | 108 | 1080 | 1 | 1 | 5
Outpatient | Floor 1 Bio Haz | Healthcare Facility and Hospitals (Medical Supply Room) | AHU-1 | Health | Yes | 0.1368% | 56 | 560 | 1 | 0 | 5
Outpatient | Floor 1 Café | Dining Area (Cafeteria/Fast Food) | AHU-1 | Health | Yes | 1.026% | 420 | 4200 | 1 | 14 | 33
Outpatient | Floor 1 Clean | Healthcare Facility and Hospitals (Medical Supply Room) | AHU-4 | Health | Yes | 0.3077% | 126 | 1260 | 1 | 1 | 5
Outpatient | Floor 1 Clean Work | Healthcare Facility and Hospitals (Medical Supply Room) | AHU-4 | Health | Yes | 0.403% | 165 | 1650 | 1 | 1 | 5
Outpatient | Floor 1 Dictation | Office Area (<250 square feet) | AHU-1 | Office | Yes | 0.3077% | 126 | 1260 | 1 | 0.63 | 5
Outpatient | Floor 1 Dressing Room | Office Area (<250 square feet) | AHU-1 | Office | Yes | 0.1099% | 45 | 450 | 1 | 0.225 | 5
Outpatient | Floor 1 Electrical Room | Electrical, Mechanical, Telephone Rooms | AHU-1 | Ancillary | Yes | 0.2393% | 98 | 980 | 1 | 0 | 1.5
Outpatient | Floor 1 Elevator Pump Room | Electrical, Mechanical, Telephone Rooms | AHU-1 | Ancillary | Yes | 0.2222% | 91 | 910 | 1 | 0 | 1.5
Outpatient | Floor 1 Humid | Office Area (<250 square feet) | AHU-1 | Office | Yes | 0.1319% | 54 | 540 | 1 | 0.27 | 5
Outpatient | Floor 1 IT Hall | Corridor Area | AHU-1 | Health | Yes | 0.3419% | 140 | 1400 | 1 | 1 | 5
Outpatient | Floor 1 IT Room | Office Area (<250 square feet) | AHU-1 | Office | Yes | 0.2735% | 112 | 1120 | 1 | 0.56 | 5
Outpatient | Floor 1 Lobby | Lobby, Main Entry | AHU-1 | Health | Yes | 1.519% | 622 | 6220 | 1 | 21 | 33
Outpatient | Floor 1 Lobby Hall | Corridor Area | AHU-1 | Health | Yes | 0.5861% | 240 | 2400 | 1 | 1 | 5
Outpatient | Floor 1 Lobby Toilet | Restrooms | AHU-1 | Health | Yes | 0.1319% | 54 | 540 | 1 | 0 | 5
Outpatient | Floor 1 Locker Room | Locker Room | AHU-1 | Health | Yes | 1.612% | 660 | 6600 | 1 | 7 | 10
Outpatient | Floor 1 Locker Room Hall | Corridor Area | AHU-1 | Health | Yes | 1.211% | 496 | 4960 | 1 | 2 | 5
Outpatient | Floor 1 Lounge | Lounge, Breakroom, or Waiting Area | AHU-1 | Health | Yes | 0.8792% | 360 | 3600 | 1 | 12 | 33
Outpatient | Floor 1 Med Gas | Healthcare Facility and Hospitals (Medical Supply Room) | AHU-1 | Health | Yes | 0.1368% | 56 | 560 | 1 | 0 | 5
Outpatient | Floor 1 MRI Control Room | Healthcare Facility and Hospitals (Imaging Room) | AHU-1 | Health | Yes | 0.4103% | 168 | 1680 | 1 | 1 | 5
Outpatient | Floor 1 MRI Hall | Corridor Area | AHU-1 | Health | Yes | 0.359% | 147 | 1470 | 1 | 1 | 5
Outpatient | Floor 1 MRI Room | Healthcare Facility and Hospitals (Imaging Room) | AHU-1 | Health | Yes | 1.075% | 440 | 4400 | 1 | 2 | 5
Outpatient | Floor 1 MRI Toilet | Restrooms | AHU-1 | Health | Yes | 0.1319% | 54 | 540 | 1 | 0 | 5
Outpatient | Floor 1 Nourishment | Kitchen/Food Preparation Area | AHU-1 | Health | Yes | 0.4445% | 182 | 1820 | 1 | 1 | 3
Outpatient | Floor 1 Nurse Hall | Corridor Area | AHU-1 | Health | Yes | 1.211% | 496 | 4960 | 1 | 2 | 5
Outpatient | Floor 1 Nurse Janitor | Storage (General) | AHU-1 | Health | Yes | 0.1319% | 54 | 540 | 1 | 0 | 2
Outpatient | Floor 1 Nurse Station | Healthcare Facility and Hospitals (Nurse's Station) | AHU-1 | Health | Yes | 0.6374% | 261 | 2610 | 1 | 1 | 5
Outpatient | Floor 1 Nurse Toilet | Restrooms | AHU-1 | Health | Yes | 0.1319% | 54 | 540 | 1 | 0 | 5
Outpatient | Floor 1 Office | Office Area (>250 square feet) | AHU-1 | Office | Yes | 1.18% | 483 | 4830 | 1 | 2.415 | 5
Outpatient | Floor 1 Operating Room 1 | Healthcare Facility and Hospitals (Operating Room) | AHU-4 | Health | Yes | 1.123% | 460 | 4600 | 1 | 2 | 5
Outpatient | Floor 1 Operating Room 2 | Healthcare Facility and Hospitals (Operating Room) | AHU-4 | Health | Yes | 1.172% | 480 | 4800 | 1 | 2 | 5
Outpatient | Floor 1 Operating Room 3 | Healthcare Facility and Hospitals (Operating Room) | AHU-4 | Health | Yes | 1.163% | 476 | 4760 | 1 | 2 | 5
Outpatient | Floor 1 PACU | Healthcare Facility and Hospitals (Recovery Room) | AHU-4 | Health | Yes | 0.2638% | 108 | 1080 | 1 | 1 | 5
Outpatient | Floor 1 Pre-Op Hall | Corridor Area | AHU-4 | Health | Yes | 1.29% | 528 | 5280 | 1 | 3 | 5
Outpatient | Floor 1 Pre-Op Room 1 | Healthcare Facility and Hospitals (Patient Room) | AHU-4 | Health | Yes | 0.4616% | 189 | 1890 | 1 | 1 | 5
Outpatient | Floor 1 Pre-Op Room 2 | Healthcare Facility and Hospitals (Patient Room) | AHU-4 | Health | Yes | 0.8255% | 338 | 3380 | 1 | 2 | 5
Outpatient | Floor 1 Pre-Op Toilet | Restrooms | AHU-4 | Health | Yes | 0.1319% | 54 | 540 | 1 | 0 | 5
Outpatient | Floor 1 Procedure Room | Healthcare Facility and Hospitals (Exam/Treatment Room) | AHU-4 | Health | Yes | 0.696% | 285 | 2850 | 1 | 1 | 5
Outpatient | Floor 1 Reception | Reception area | AHU-1 | Office | Yes | 1.243% | 509 | 5090 | 1 | 2.545 | 5
Outpatient | Floor 1 Reception Hall | Corridor Area | AHU-1 | Health | Yes | 0.3126% | 128 | 1280 | 1 | 1 | 5
Outpatient | Floor 1 Recovery Room | Healthcare Facility and Hospitals (Recovery Room) | AHU-4 | Health | Yes | 1.319% | 540 | 5400 | 1 | 3 | 5
Outpatient | Floor 1 Scheduling | Office Area (<250 square feet) | AHU-1 | Office | Yes | 0.2906% | 119 | 1190 | 1 | 0.595 | 5
Outpatient | Floor 1 Scrub | Corridor Area | AHU-4 | Health | Yes | 0.2051% | 84 | 840 | 1 | 0 | 5
Outpatient | Floor 1 Soil | Healthcare Facility and Hospitals (Medical Supply Room) | AHU-1 | Health | Yes | 0.3077% | 126 | 1260 | 1 | 1 | 5
Outpatient | Floor 1 Soil Hold | Healthcare Facility and Hospitals (Medical Supply Room) | AHU-1 | Health | Yes | 0.1368% | 56 | 560 | 1 | 0 | 5
Outpatient | Floor 1 Soil Work | Healthcare Facility and Hospitals (Medical Supply Room) | AHU-1 | Health | Yes | 0.4396% | 180 | 1800 | 1 | 1 | 5
Outpatient | Floor 1 Step Down | Healthcare Facility and Hospitals (Recovery Room) | AHU-4 | Health | Yes | 0.7327% | 300 | 3000 | 1 | 2 | 5
Outpatient | Floor 1 Sterile Hall | Corridor Area | AHU-4 | Health | Yes | 1.504% | 616 | 6160 | 1 | 3 | 5
Outpatient | Floor 1 Sterile Storage | Storage (General) | AHU-4 | Health | Yes | 0.9671% | 396 | 3960 | 1 | 1 | 2
Outpatient | Floor 1 Storage | Storage (General) | AHU-1 | Health | Yes | 2.247% | 920 | 9200 | 1 | 2 | 2
Outpatient | Floor 1 Sub-Sterile | Corridor Area | AHU-4 | Health | Yes | 0.4787% | 196 | 1960 | 1 | 1 | 5
Outpatient | Floor 1 Utility Hall | Corridor Area | AHU-1 | Health | Yes | 0.6252% | 256 | 2560 | 1 | 1 | 5
Outpatient | Floor 1 Utility Janitor | Storage (General) | AHU-1 | Health | Yes | 0.1026% | 42 | 420 | 1 | 0 | 2
Outpatient | Floor 1 Utility Room | Storage (General) | AHU-1 | Health | Yes | 0.8792% | 360 | 3600 | 1 | 1 | 2
Outpatient | Floor 1 Vestibule | Corridor Area | AHU-1 | Health | Yes | 0.1758% | 72 | 720 | 1 | 0 | 5
Outpatient | Floor 2 Conference | Convention, Conference, Multipurpose and Meeting Area | AHU-2 | Office | Yes | 0.8206% | 336 | 3360 | 1 | 11.088 | 33
Outpatient | Floor 2 Conference Toilet | Restrooms | AHU-2 | Health | Yes | 0.1563% | 64 | 640 | 1 | 0 | 5
Outpatient | Floor 2 Dictation | Office Area (<250 square feet) | AHU-2 | Office | Yes | 0.171% | 70 | 700 | 1 | 0.35 | 5
Outpatient | Floor 2 Exam 1 | Healthcare Facility and Hospitals (Exam/Treatment Room) | AHU-2 | Health | Yes | 0.8792% | 360 | 3600 | 1 | 2 | 5
Outpatient | Floor 2 Exam 2 | Healthcare Facility and Hospitals (Exam/Treatment Room) | AHU-2 | Health | Yes | 1.319% | 540 | 5400 | 1 | 3 | 5
Outpatient | Floor 2 Exam 3 | Healthcare Facility and Hospitals (Exam/Treatment Room) | AHU-2 | Health | Yes | 1.758% | 720 | 7200 | 1 | 4 | 5
Outpatient | Floor 2 Exam 4 | Healthcare Facility and Hospitals (Exam/Treatment Room) | AHU-2 | Health | Yes | 0.2051% | 84 | 840 | 1 | 0 | 5
Outpatient | Floor 2 Exam 5 | Healthcare Facility and Hospitals (Exam/Treatment Room) | AHU-2 | Health | Yes | 0.8548% | 350 | 3500 | 1 | 2 | 5
Outpatient | Floor 2 Exam 6 | Healthcare Facility and Hospitals (Exam/Treatment Room) | AHU-2 | Health | Yes | 0.5495% | 225 | 2250 | 1 | 1 | 5
Outpatient | Floor 2 Exam 7 | Healthcare Facility and Hospitals (Exam/Treatment Room) | AHU-2 | Health | Yes | 1.934% | 792 | 7920 | 1 | 4 | 5
Outpatient | Floor 2 Exam 8 | Healthcare Facility and Hospitals (Exam/Treatment Room) | AHU-2 | Health | Yes | 0.6594% | 270 | 2700 | 1 | 1 | 5
Outpatient | Floor 2 Exam 9 | Healthcare Facility and Hospitals (Exam/Treatment Room) | AHU-2 | Health | Yes | 0.9671% | 396 | 3960 | 1 | 2 | 5
Outpatient | Floor 2 Exam Hall 1 | Corridor Area | AHU-2 | Health | Yes | 0.4396% | 180 | 1800 | 1 | 1 | 5
Outpatient | Floor 2 Exam Hall 2 | Corridor Area | AHU-2 | Health | Yes | 0.4396% | 180 | 1800 | 1 | 1 | 5
Outpatient | Floor 2 Exam Hall 3 | Corridor Area | AHU-2 | Health | Yes | 0.4396% | 180 | 1800 | 1 | 1 | 5
Outpatient | Floor 2 Exam Hall 4 | Corridor Area | AHU-2 | Health | Yes | 0.4836% | 198 | 1980 | 1 | 1 | 5
Outpatient | Floor 2 Exam Hall 5 | Corridor Area | AHU-2 | Health | Yes | 0.4836% | 198 | 1980 | 1 | 1 | 5
Outpatient | Floor 2 Exam Hall 6 | Corridor Area | AHU-2 | Health | Yes | 0.4836% | 198 | 1980 | 1 | 1 | 5
Outpatient | Floor 2 Janitor | Storage (General) | AHU-2 | Health | Yes | 0.1539% | 63 | 630 | 1 | 0 | 2
Outpatient | Floor 2 Lounge | Lounge, Breakroom, or Waiting Area | AHU-2 | Health | Yes | 0.1954% | 80 | 800 | 1 | 3 | 33
Outpatient | Floor 2 Nurse Station 1 | Healthcare Facility and Hospitals (Nurse's Station) | AHU-2 | Health | Yes | 0.3663% | 150 | 1500 | 1 | 1 | 5
Outpatient | Floor 2 Nurse Station 2 | Healthcare Facility and Hospitals (Nurse's Station) | AHU-2 | Health | Yes | 0.4396% | 180 | 1800 | 1 | 1 | 5
Outpatient | Floor 2 Office | Office Area (>250 square feet) | AHU-2 | Office | Yes | 1.368% | 560 | 5600 | 1 | 2.8 | 5
Outpatient | Floor 2 Office Hall | Corridor Area | AHU-2 | Health | Yes | 1.084% | 444 | 4440 | 1 | 2 | 5
Outpatient | Floor 2 Reception | Reception area | AHU-2 | Office | Yes | 2.403% | 984 | 9840 | 1 | 4.92 | 5
Outpatient | Floor 2 Reception Hall | Corridor Area | AHU-2 | Health | Yes | 1.377% | 564 | 5640 | 1 | 3 | 5
Outpatient | Floor 2 Reception Toilet | Restrooms | AHU-2 | Health | Yes | 0.3077% | 126 | 1260 | 1 | 1 | 5
Outpatient | Floor 2 Scheduling 1 | Office Area (>250 square feet) | AHU-2 | Office | Yes | 0.7913% | 324 | 3240 | 1 | 1.62 | 5
Outpatient | Floor 2 Scheduling 2 | Office Area (>250 square feet) | AHU-2 | Office | Yes | 0.8352% | 342 | 3420 | 1 | 1.71 | 5
Outpatient | Floor 2 Storage 1 | Storage (General) | AHU-2 | Health | Yes | 0.1368% | 56 | 560 | 1 | 0 | 2
Outpatient | Floor 2 Storage 2 | Storage (General) | AHU-2 | Health | Yes | 0.2931% | 120 | 1200 | 1 | 0 | 2
Outpatient | Floor 2 Storage 3 | Storage (General) | AHU-2 | Health | Yes | 0.3517% | 144 | 1440 | 1 | 0 | 2
Outpatient | Floor 2 Utility | Storage (General) | AHU-2 | Health | Yes | 0.3077% | 126 | 1260 | 1 | 0 | 2
Outpatient | Floor 2 Work | Office Area (>250 square feet) | AHU-2 | Office | Yes | 4.127% | 1690 | 16900 | 1 | 8.45 | 5
Outpatient | Floor 2 Work Hall | Corridor Area | AHU-2 | Health | Yes | 2.037% | 834 | 8340 | 1 | 4 | 5
Outpatient | Floor 2 Work Toilet | Restrooms | AHU-2 | Health | Yes | 0.1319% | 54 | 540 | 1 | 0 | 5
Outpatient | Floor 2 X-Ray | Healthcare Facility and Hospitals (Imaging Room) | AHU-2 | Health | Yes | 2.198% | 900 | 9000 | 1 | 5 | 5
Outpatient | Floor 3 Dressing Room | Office Area (<250 square feet) | AHU-3 | Office | Yes | 0.1026% | 42 | 420 | 1 | 0.21 | 5
Outpatient | Floor 3 Elevator Hall | Corridor Area | AHU-3 | Health | Yes | 0.9036% | 370 | 3700 | 1 | 2 | 5
Outpatient | Floor 3 Humid | Office Area (<250 square feet) | AHU-3 | Office | Yes | 0.2638% | 108 | 1080 | 1 | 0.54 | 5
Outpatient | Floor 3 Janitor | Storage (General) | AHU-3 | Health | Yes | 0.1539% | 63 | 630 | 1 | 0 | 2
Outpatient | Floor 3 Locker | Locker Room | AHU-3 | Health | Yes | 0.2931% | 120 | 1200 | 1 | 1 | 10
Outpatient | Floor 3 Lounge | Lounge, Breakroom, or Waiting Area | AHU-3 | Health | Yes | 1.854% | 759 | 7590 | 1 | 25 | 33
Outpatient | Floor 3 Lounge Toilet | Restrooms | AHU-3 | Health | Yes | 0.4689% | 192 | 1920 | 1 | 1 | 5
Outpatient | Floor 3 Mechanical | Electrical, Mechanical, Telephone Rooms | AHU-3 | Ancillary | Yes | 0.8548% | 350 | 3500 | 1 | 1 | 1.5
Outpatient | Floor 3 Mechanical Hall | Corridor Area | AHU-3 | Ancillary | Yes | 0.7327% | 300 | 3000 | 1 | 2 | 5
Outpatient | Floor 3 Office | Office Area (>250 square feet) | AHU-3 | Office | Yes | 7.415% | 3036 | 30360 | 1 | 15.18 | 5
Outpatient | Floor 3 Office Hall | Corridor Area | AHU-3 | Health | Yes | 2.037% | 834 | 8340 | 1 | 4 | 5
Outpatient | Floor 3 Office Toilet | Restrooms | AHU-3 | Health | Yes | 0.1319% | 54 | 540 | 1 | 0 | 5
Outpatient | Floor 3 Physical Therapy 1 | Healthcare Facility and Hospitals (Physical Therapy Room) | AHU-3 | Health | Yes | 3.175% | 1300 | 13000 | 1 | 7 | 5
Outpatient | Floor 3 Physical Therapy 2 | Healthcare Facility and Hospitals (Physical Therapy Room) | AHU-3 | Health | Yes | 1.446% | 592 | 5920 | 1 | 3 | 5
Outpatient | Floor 3 Physical Therapy Toilet | Restrooms | AHU-3 | Health | Yes | 0.2051% | 84 | 840 | 1 | 0 | 5
Outpatient | Floor 3 Storage 1 | Storage (General) | AHU-3 | Health | Yes | 0.2638% | 108 | 1080 | 1 | 0 | 2
Outpatient | Floor 3 Storage 2 | Storage (General) | AHU-3 | Health | Yes | 0.2051% | 84 | 840 | 1 | 0 | 2
Outpatient | Floor 3 Treatment | Healthcare Facility and Hospitals (Exam/Treatment Room) | AHU-3 | Health | Yes | 1.163% | 476 | 4760 | 1 | 2 | 5
Outpatient | Floor 3 Undeveloped 1 | Storage (General) | AHU-3 | Health | Yes | 5.539% | 2268 | 22680 | 1 | 5 | 2
Outpatient | Floor 3 Undeveloped 2 | Storage (General) | AHU-3 | Health | Yes | 2.813% | 1152 | 11520 | 1 | 2 | 2
Outpatient | Floor 3 Utility | Storage (General) | AHU-3 | Health | Yes | 0.5275% | 216 | 2160 | 1 | 0 | 2
Outpatient | Floor 3 Work | Office Area (>250 square feet) | AHU-3 | Office | Yes | 1.402% | 574 | 5740 | 1 | 2.87 | 5
Outpatient | NE Stair | Stairwell | AHU-3 | Health | Yes | 0.4103% | 168 | 5040 | 1 | 1 | 5
Outpatient | NW Elevator | Elevator | Unconditioned | Health | Yes | 0.3419% | 140 | 4200 | 1 | 0 | 0
Outpatient | NW Stair | Stairwell | AHU-3 | Health | Yes | 0.4689% | 192 | 5760 | 1 | 1 | 5
Outpatient | SW Stair | Stairwell | AHU-3 | Health | Yes | 0.2345% | 96 | 2880 | 1 | 0 | 5
Total (1 Building) | Total ( 118 spaces) | Total (23 Space types) | Total ( Thermal Zones) |  | Total ( 118 Conditioned zones) |  | 40946 |  | 118 | 258.978
N

## Envelope
Envelope - Outpatient
Element | Prototype | Assembly Type | Construction | Unit | Vintage | Selected T24 | Notes | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
External Wall | Outpatient | ExtWall_MetalFramed_NonRes | Metal framed wall: Metal frame + insulation + gypsum board (Same as PNNL model, Analysis for Building Envelopes and Mechanical Systems Using 2012 CBECS Data, PNNL-26949, March 2018.) | U-value IP | Pre 1978 | N/A | ASHRAE 90.1,2022 Table A3.3.3.1, 3.5", R-0 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352
[5 empty] | 1978-1997 | 1986 | Copied from High-rise office alternative requirements (Table 2-53W): Package A with heat capacity between 10-14.99 (Btu/F-ft²) *T24, 1986, Table 2-53BB presents U-factors less than the next vintage (for wall density of 26-40 lb/ft² & Degree day<3500)! | 0.213 | 0.227 | 0.227 | 0.217 | 0.256 | 0.256 | 0.256 | 0.256 | 0.256 | 0.256 | 0.238 | 0.238 | 0.238 | 0.208 | 0.208 | 0.213
[5 empty] | 1998-2007 | 2001 | Table 1-H | 0.182 | 0.182 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.098 | 0.062 | 0.082 | 0.062 | 0.062 | 0.098 | 0.098 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.06 | 0.055 | 0.071 | 0.055 | 0.055 | 0.06 | 0.06 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055
Roof | Outpatient | FlatRoof_WoodFramedAndOther_NonRes | Metal deck roof: Roof membrane + roof insulation + metal decking (Same as PNNL) | U-value IP | Pre 1978 | N/A | Considering 30 years for roof/ insulation replacement. | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 1978-1997 | 1992 |  | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 1998-2007 | 2001 | Table 1-H | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.049 | 0.039 | 0.039 | 0.039 | 0.049 | 0.075 | 0.067 | 0.067 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039
[5 empty] | New Construction | 2025 | Table 140.3-B | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038
Windows | Outpatient | FixedWindow_NonRes | Single pane | U-value IP | Pre 1978 | N/A | ASHRAE Handbook of Fundamentals (Table 4-Ch15) for single pane & T24, 2013 for double pane(88%-12%)* | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288
[5 empty] | 1978-1997 | N/A |  | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288
|  |  | Double pane |  | 1998-2007 | 2001 | Table 1-H | 0.49 | 0.49 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.34 | 0.36 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.36
| Outpatient | FixedWindow_NonRes | Single pane | SHGC | Pre 1978 | N/A | ASHRAE Handbook of Fundamentals (Table 10-Ch15) for single pane & T24, 2013 for double pane(88%-12%)* | 0.7252 | 0.7252 | 0.7252 | 0.7252 | 0.7252 | 0.7252 | 0.7252 | 0.7252 | 0.7252 | 0.7252 | 0.7252 | 0.7252 | 0.7252 | 0.7252 | 0.7252 | 0.7252
[5 empty] | 1978-1997 | N/A |  | 0.7252 | 0.7252 | 0.7252 | 0.7252 | 0.7252 | 0.7252 | 0.7252 | 0.7252 | 0.7252 | 0.7252 | 0.7252 | 0.7252 | 0.7252 | 0.7252 | 0.7252 | 0.7252
|  |  | Double pane |  | 1998-2007 | 2001 | Table 1-H (Non North, WWR:11-20% ) | 0.43 | 0.36 | 0.55 | 0.55 | 0.55 | 0.61 | 0.61 | 0.61 | 0.61 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.43
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.22 | 0.25 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.25
*(According to CBECS 2018, ~ 88% of windows of healthcare buildings built before 2000 are single pane)
Infiltration
|  |  | Building | Zones | Vintage | I_75 6-sdied Infiltration rate @ 75 pa | Note | I-design (cfm/ft²) (4-sided Infiltration rate at normal pressure) (Design flow rate approach and Flow/Exterior Wall Area calculation method)
|  | Infiltration | Outpatient |  | Pre 1978 | 1.1 | 2022 CASE report (Table 38) | 0.341
[5 empty] | 1978-1997 | 1.1 | 2022 CASE report (Table 38) | 0.341
[5 empty] | 1998-2007 | 1.1 | 2022 CASE report (Table 38) | 0.341
[5 empty] | 2008-2018 | 1 | 2022 CASE report (Table 38) & T24, 2008-2016 (Table 140.3-B)--Air barrier is required in CZ 10-16 | 0.3121
[5 empty] | 2019+ | 0.6 | 2022 CASE report (Table 38) & T24, 2025 (Table 140.3-B)--Air barrier is required in all CZs | 0.186
Source: Title 24 air barrier requirements (all editions) and the standardized infiltration rate reported in the 2022 CASE report and Dodge 2023 data
|  |  |  | Air Leakage Memo: |  | Infiltration_rate_report_14May2025-Short-Version.docx

## Thermostat
Thermostat - Outpatient
Setpoint | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16 | Source | Note
Health Heating Setpoint (F) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | T24 2022 - Appendix 5.4B | PNNL Healthcare-Outpatient prototype use this setpoints: Administration zones: 72°F Cooling/70°F Heating, Critical zones: 72°F Cooling/70°F Heating, Operating rooms: 65°F Cooling/65°F Heating---PNNL Healthcare-Outpatient prototype use this setbacks: 77°F Cooling/65°F Heating, Critical zones: no setback, Operating rooms: 72°F Cooling/65°F Heating
Health Heating Setback (F) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
Health Cooling Setpoint (F) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
Health Cooling Setback (F) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
Kitchen Heating Setpoint (F) | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | PNNL 09.1, 2022 Restaurant prototype
Kitchen Heating Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Kitchen Cooling Setpoint (F) | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79
Kitchen Cooling Setback (F) | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86
Ancillary Heating Setpoint (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | Enginnering Judgment
Ancillary Heating Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Ancillary Cooling Setpoint (F) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
Ancillary Cooling Setback (F) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85

## HVAC System
HVAC System - Outpatient
Vintage | Spaces | Heating | Cooling | Air Distribution | Source | Note
Existing | Conditioned zones | Gas Boiler for Hydronic Reheat and Gas Furnace for Heating | RTU DX | Single Duct CAV--Outdoor air often supplied through RTU economizers or dedicated OA section | CEUS 2022 (Other system based on T24 and Engineering judgement) | Packaged RTU
New Construction | Conditioned zones | Gas Boiler for Hydronic Reheat and Gas Furnace for Heating | RTU DX | VAV + Hydronic Reheat | T24 2025 ACM 2025, Table 2 and 3 | System 5 – PVAV
Efficiency of HVAC system (Efficiency is capacity-dependent. The following table provides a general estimate of system efficiency based on preliminary simulations in one climate zone, or assuming cooling load based on rule of thumb)
Vintage | Upgrade/Installed year | DX Cooling | Gas Furnace | Gas Boiler | Source | Note
Pre 1978 | 2008 | EER=9.5 (≥ 240,000 Btu/h and < 760,000 Btu/h) | ≥225,000 Btu/h--80% Et | 80% Ec | T24, 2008 , Table 112-A (for DX Coil) -Title 24-2008 §111 / Title 20 Table E-3 (and 10 CFR 431.87 as in effect through March 1, 2012) for Boiler Efficiency- 10 CFR 431.77, in force since 1 Jan 1994 for furnace efficiency
1978-1997
1998-2007
2008-2018 | 2013 | EER=10 (≥ 240,000 Btu/h and < 760,000 Btu/h) | 80% Et | Gas-Fired Boiler > 300,000 Btu/h and ≤2,500,000 Btu/h-- 80% Et Gas-Fired Boiler > 2,500,000 Btu/h -- 82% Ec | T24, 2013 , Table 110.2-A (for DX Coil) -Table 110.2-J (for Gas Furnace thermal efficiency) - - Table 110.2-K (for Boiler thermal efficiency).
New Construction | 2025 | EER=10 (≥ 240,000 Btu/h and < 760,000 Btu/h) | 81% Et | Gas-Fired Boiler > 300,000 Btu/h and ≤2,500,000 Btu/h-- 80% Et Gas-Fired Boiler > 2,500,000 Btu/h -- 82% Ec | T24, 2025 , Table 110.2-A (for DX Coil) - - 10 CFR 431.86 , section § 431.87 Table 1 (for Boiler thermal efficiency) --Title 24-2008 §111 / Title 20 Table E-3 (and 10 CFR 431.87 as in effect through March 1, 2012)
|  |  | * Et = Thermal efficiency | * Ec = Combustion efficiency
Fan power
Vintage | Approach | System | Total Static Pressure (TSP) (in w.c.) | Fan Efficiency [ACM 2025] | Motor Efficiency | Fan Power Index (W/cfm) | Data Source | Note
Existing | PNNL 90.1-2011, TSP | Packaged RTU-CAV | 4.09 | 0.65 | ASHRAE 90.1, 2004, Table 10.8 * |  | Fan power formula: PNNL 20405, 2010, section 5.2.2.5 TSP and fan efficiency: PNNL 20405, 2010, Table 5.11, 90.1-04ac values Motor efficiency: ASHRAE 90.1, 2004, Table 10.8
Brake horsepower (bhp) = (Supply cfm × TSP in w.c.) / (6356 × fan efficiency)
Fan power (w/cfm) = (bhp × 746) / ( supply cfm × motor efficiency )
New Construction | ACM 2025 | Packaged RTU-CAV >5,000 cfm; <= 10,000 cfm | TSP (in w.c.) = fan power (W/cfm) × motor efficiency × fan efficiency × 6356 / 746 | 0.65 | 2025 ACM Table 12 ** | 0.78 | Fan power index: [ACM 2025, Table 13] Motot efficiency: [ ACM 2025, Table 12]
|  | Packaged RTU-CAV >10,000 cfm | TSP (in w.c.) = fan power (W/cfm) × motor efficiency × fan efficiency × 6356 / 746 |  |  | 0.748
|  | System 5-PVAV System >5,000 cfm; <= 10,000 cfm | TSP (in w.c.) = fan power (W/cfm) × motor efficiency × fan efficiency × 6356 / 746 |  |  | 1.013
|  | System 5-PVAV System >10,000 cfm | TSP = fan power × motor efficiency × fan efficiency × 6356 / 746 |  |  | 0.946
* According to PNNL 20405 section 5.2.2.5, the full-load efficiency of the motor serving the fan is taken from ASHRAE 90.1, 2004, Table 10.8, based on motor nameplate and assuming enclosed motors operating at 1,800 rotations per minute (rpm) Motor nameplate size (bhp) = brake horsepower (bhp) × 1.1 ( using a 10% oversizing factor)
** The full‑load efficiency of the motor serving the fan is taken from ACM 2025 Table 12 based on the cfm of the fan. Brake horsepower (bhp) = (Supply cfm from sizing run × fan power in W/cfm) / 746.

## Ventilation
Outdoor Airflow Rate - Outpatient
Space Type | Space/Thermal Zone | Number of People | Floor Area (ft²) | cfm/person [T24, 2025, Equation 120.1-F and Table 120.1-A] | cfm/ft² [T24, 2025, Equation 120.1-F and Table 120.1-A] | Required Exhaust Rate (cfm/ft²) [T24, 2025, Table 120.1-B – minimum exhaust rates OR CMC Table 4-A for Healthcare] | Required Exhaust Rate (cfm) [T24, 2025, Table 120.1-B – minimum exhaust rates] | Min OA Ventilation Requirement (cfm/ft²) [Table 4-A, 2022 California Mechanical Code]* | Total cfm Driven by People | Total cfm Driven by Area | Total cfm Driven by Exhaust | Total cfm | Note
Healthcare Facility and Hospitals (Exam/Treatment Room) | Floor 1 Anesthesia | 1 | 108 | 15 | n/a | 1.33 |  | 0.33333 | 15 | 36 | 143.64 | 143.64 | All Room air exhausted directly to the outdoor, according to Table 4-A, 2022 California Mechanical Code).
Healthcare Facility and Hospitals (Medical Supply Room) | Floor 1 Bio Haz | 0 | 56 | 15 | n/a |  |  | 0.33333 | 0 | 18.6667 | 0 | 18.6667
Dining Area (Cafeteria/Fast Food) | Floor 1 Café | 14 | 420 | 15 | 0.15 |  |  | 0 | 210 | 63 | 0 | 210
Healthcare Facility and Hospitals (Medical Supply Room) | Floor 1 Clean | 1 | 126 | 15 | n/a |  |  | 0.33333 | 15 | 42 | 0 | 42
Healthcare Facility and Hospitals (Medical Supply Room) | Floor 1 Clean Work | 1 | 165 | 15 | n/a |  |  | 0.33333 | 15 | 55 | 0 | 55
Office Area (<250 square feet) | Floor 1 Dictation | 0.63 | 126 | 15 | 0.15 |  |  | 0 | 9.45 | 18.9 | 0 | 18.9
Office Area (<250 square feet) | Floor 1 Dressing Room | 0.225 | 45 | 15 | 0.15 |  |  | 0 | 3.375 | 6.75 | 0 | 6.75
Electrical, Mechanical, Telephone Rooms | Floor 1 Electrical Room | 0 | 98 | 15 | n/a |  |  | 0 | 0 | 0 | 0 | 0
Electrical, Mechanical, Telephone Rooms | Floor 1 Elevator Pump Room | 0 | 91 | 15 | n/a |  |  | 0 | 0 | 0 | 0 | 0
Office Area (<250 square feet) | Floor 1 Humid | 0.27 | 54 | 15 | 0.15 |  |  | 0 | 4.05 | 8.1 | 0 | 8.1
Corridor Area | Floor 1 IT Hall | 1 | 140 | 15 | 0.15 |  |  | 0 | 15 | 21 | 0 | 21
Office Area (<250 square feet) | Floor 1 IT Room | 0.56 | 112 | 15 | 0.15 |  |  | 0 | 8.4 | 16.8 | 0 | 16.8
Lobby, Main Entry | Floor 1 Lobby | 21 | 622 | 15 | 0.15 |  |  | 0 | 315 | 93.3 | 0 | 315
Corridor Area | Floor 1 Lobby Hall | 1 | 240 | 15 | 0.15 |  |  | 0 | 15 | 36 | 0 | 36
Restrooms | Floor 1 Lobby Toilet | 0 | 54 | 15 | n/a |  | 50 | 0 | 0 | 0 | 50 | 0 | *Restrooms in California per 2025 T24 and CALGreen (Part 11) require mechanical exhaust ventilation, but they do not require additional dedicated outdoor air (OA) beyond that local exhaust. Bathroom exhaust and exhaust fan energy will be captured in the models. We will assume make-up air is drawn from adjacent spaces.
Locker Room | Floor 1 Locker Room | 7 | 660 | 15 | n/a | 0.25 |  | 0 | 105 | 0 | 165 | 165
Corridor Area | Floor 1 Locker Room Hall | 2 | 496 | 15 | 0.15 |  |  | 0 | 30 | 74.4 | 0 | 74.4
Lounge, Breakroom, or Waiting Area | Floor 1 Lounge | 12 | 360 | 15 | 0.15 |  |  | 0 | 180 | 54 | 0 | 180
Healthcare Facility and Hospitals (Medical Supply Room) | Floor 1 Med Gas | 0 | 56 | 15 | n/a |  |  | 0.33333 | 0 | 18.6667 | 0 | 18.6667
Healthcare Facility and Hospitals (Imaging Room) | Floor 1 MRI Control Room | 1 | 168 | 15 | n/a | 2.02 |  | 0.33333 | 15 | 56 | 339.36 | 339.36 | Exhaust Rate assumed according to PNNL outpatient model.The PNNL outpatient model used ASHRAE 170 / CMC Table 4-A (Negative Pressure Soiled utility/workroom or soiled holding , exhaust Required))
Corridor Area | Floor 1 MRI Hall | 1 | 147 | 15 | 0.15 |  |  | 0 | 15 | 22.05 | 0 | 22.05
Healthcare Facility and Hospitals (Imaging Room) | Floor 1 MRI Room | 2 | 440 | 15 | n/a | 2.02 |  | 0.33333 | 30 | 146.6667 | 888.8 | 888.8 | Exhaust Rate assumed according to PNNL outpatient model.The PNNL outpatient model used ASHRAE 170 / CMC Table 4-A (Negative Pressure X-ray room , exhaust Required))
Restrooms | Floor 1 MRI Toilet | 0 | 54 | 15 | n/a |  | 50 | 0 | 0 | 0 | 50 | 50 | Toilet rooms, intermittent exhaust 50 cfm per toilet
Kitchen/Food Preparation Area | Floor 1 Nourishment | 1 | 182 | 15 | 0.15 | 0.3 |  | 0 | 15 | 27.3 | 54.6 | 54.6
Corridor Area | Floor 1 Nurse Hall | 2 | 496 | 15 | 0.15 |  |  | 0 | 30 | 74.4 | 0 | 74.4
Storage (General) | Floor 1 Nurse Janitor | 0 | 54 | 15 | 0.15 |  |  | 0 | 0 | 8.1 | 0 | 8.1
Healthcare Facility and Hospitals (Nurse's Station) | Floor 1 Nurse Station | 1 | 261 | 15 | n/a |  |  | 0.33333 | 15 | 87 | 0 | 87
Restrooms | Floor 1 Nurse Toilet | 0 | 54 | 15 | n/a |  | 50 | 0 | 0 | 0 | 50 | 50 | Toilet rooms, intermittent exhaust 50 cfm per toilet
Office Area (>250 square feet) | Floor 1 Office | 2.415 | 483 | 15 | 0.15 |  |  | 0 | 36.225 | 72.45 | 0 | 72.45
Healthcare Facility and Hospitals (Operating Room) | Floor 1 Operating Room 1 | 2 | 460 | 15 | n/a |  |  | 0.66667 | 30 | 306.6667 | 0 | 306.6667
Healthcare Facility and Hospitals (Operating Room) | Floor 1 Operating Room 2 | 2 | 480 | 15 | n/a |  |  | 0.66667 | 30 | 320 | 0 | 320
Healthcare Facility and Hospitals (Operating Room) | Floor 1 Operating Room 3 | 2 | 476 | 15 | n/a |  |  | 0.66667 | 30 | 317.3333 | 0 | 317.3333
Healthcare Facility and Hospitals (Recovery Room) | Floor 1 PACU | 1 | 108 | 15 | n/a |  |  | 0.33333 | 15 | 36 | 0 | 36
Corridor Area | Floor 1 Pre-Op Hall | 3 | 528 | 15 | 0.15 |  |  | 0 | 45 | 79.2 | 0 | 79.2
Healthcare Facility and Hospitals (Patient Room) | Floor 1 Pre-Op Room 1 | 1 | 189 | 15 | n/a |  |  | 0.33333 | 15 | 63 | 0 | 63
Healthcare Facility and Hospitals (Patient Room) | Floor 1 Pre-Op Room 2 | 2 | 338 | 15 | n/a |  |  | 0.33333 | 30 | 112.6667 | 0 | 112.6667
Restrooms | Floor 1 Pre-Op Toilet | 0 | 54 | 15 | n/a |  | 50 | 0 | 0 | 0 | 50 | 50 | Toilet rooms, intermittent exhaust 50 cfm per toilet
Healthcare Facility and Hospitals (Exam/Treatment Room) | Floor 1 Procedure Room | 1 | 285 | 15 | n/a |  |  | 0.33333 | 15 | 95 | 0 | 95
Reception area | Floor 1 Reception | 2.545 | 509 | 15 | 0.15 |  |  | 0 | 38.175 | 76.35 | 0 | 76.35
Corridor Area | Floor 1 Reception Hall | 1 | 128 | 15 | 0.15 |  |  | 0 | 15 | 19.2 | 0 | 19.2
Healthcare Facility and Hospitals (Recovery Room) | Floor 1 Recovery Room | 3 | 540 | 15 | n/a |  |  | 0.33333 | 45 | 180 | 0 | 180
Office Area (<250 square feet) | Floor 1 Scheduling | 0.595 | 119 | 15 | 0.15 |  |  | 0 | 8.925 | 17.85 | 0 | 17.85
Corridor Area | Floor 1 Scrub | 0 | 84 | 15 | 0.15 |  |  | 0 | 0 | 12.6 | 0 | 12.6
Healthcare Facility and Hospitals (Medical Supply Room) | Floor 1 Soil | 1 | 126 | 15 | n/a | 1.67 |  | 0.33333 | 15 | 42 | 210.42 | 210.42 | Exhaust Rate assumed according to PNNL outpatient model.The PNNL outpatient model used ASHRAE 170 / CMC Table 4-A (Negative Pressure X-ray room , exhaust Required))
Healthcare Facility and Hospitals (Medical Supply Room) | Floor 1 Soil Hold | 0 | 56 | 15 | n/a | 1.67 |  | 0.33333 | 0 | 18.6667 | 93.52 | 93.52 | Exhaust Rate assumed according to PNNL outpatient model.The PNNL outpatient model used ASHRAE 170 / CMC Table 4-A (Negative Pressure X-ray room , exhaust Required))
Healthcare Facility and Hospitals (Medical Supply Room) | Floor 1 Soil Work | 1 | 180 | 15 | n/a | 1.67 |  | 0.33333 | 15 | 60 | 300.6 | 300.6 | Exhaust Rate assumed according to PNNL outpatient model.The PNNL outpatient model used ASHRAE 170 / CMC Table 4-A (Negative Pressure X-ray room , exhaust Required))
Healthcare Facility and Hospitals (Recovery Room) | Floor 1 Step Down | 2 | 300 | 15 | n/a |  |  | 0.33333 | 30 | 100 | 0 | 100
Corridor Area | Floor 1 Sterile Hall | 3 | 616 | 15 | 0.15 |  |  | 0 | 45 | 92.4 | 0 | 92.4
Storage (General) | Floor 1 Sterile Storage | 1 | 396 | 15 | 0.15 |  |  | 0 | 15 | 59.4 | 0 | 59.4
Storage (General) | Floor 1 Storage | 2 | 920 | 15 | 0.15 |  |  | 0 | 30 | 138 | 0 | 138
Corridor Area | Floor 1 Sub-Sterile | 1 | 196 | 15 | 0.15 |  |  | 0 | 15 | 29.4 | 0 | 29.4
Corridor Area | Floor 1 Utility Hall | 1 | 256 | 15 | 0.15 |  |  | 0 | 15 | 38.4 | 0 | 38.4
Storage (General) | Floor 1 Utility Janitor | 0 | 42 | 15 | 0.15 |  |  | 0 | 0 | 6.3 | 0 | 6.3
Storage (General) | Floor 1 Utility Room | 1 | 360 | 15 | 0.15 |  |  | 0 | 15 | 54 | 0 | 54
Corridor Area | Floor 1 Vestibule | 0 | 72 | 15 | 0.15 |  |  | 0 | 0 | 10.8 | 0 | 10.8
Convention, Conference, Multipurpose and Meeting Area | Floor 2 Conference | 11.088 | 336 | 15 | 0.15 |  |  | 0 | 166.32 | 50.4 | 0 | 166.32
Restrooms | Floor 2 Conference Toilet | 0 | 64 | 15 | n/a |  | 50 | 0 | 0 | 0 | 50 | 50 | Toilet rooms, intermittent exhaust 50 cfm per toilet
Office Area (<250 square feet) | Floor 2 Dictation | 0.35 | 70 | 15 | 0.15 |  |  | 0 | 5.25 | 10.5 | 0 | 10.5
Healthcare Facility and Hospitals (Exam/Treatment Room) | Floor 2 Exam 1 | 2 | 360 | 15 | n/a |  |  | 0.33333 | 30 | 120 | 0 | 120
Healthcare Facility and Hospitals (Exam/Treatment Room) | Floor 2 Exam 2 | 3 | 540 | 15 | n/a |  |  | 0.33333 | 45 | 180 | 0 | 180
Healthcare Facility and Hospitals (Exam/Treatment Room) | Floor 2 Exam 3 | 4 | 720 | 15 | n/a |  |  | 0.33333 | 60 | 240 | 0 | 240
Healthcare Facility and Hospitals (Exam/Treatment Room) | Floor 2 Exam 4 | 0 | 84 | 15 | n/a |  |  | 0.33333 | 0 | 28 | 0 | 28
Healthcare Facility and Hospitals (Exam/Treatment Room) | Floor 2 Exam 5 | 2 | 350 | 15 | n/a |  |  | 0.33333 | 30 | 116.6667 | 0 | 116.6667
Healthcare Facility and Hospitals (Exam/Treatment Room) | Floor 2 Exam 6 | 1 | 225 | 15 | n/a |  |  | 0.33333 | 15 | 75 | 0 | 75
Healthcare Facility and Hospitals (Exam/Treatment Room) | Floor 2 Exam 7 | 4 | 792 | 15 | n/a |  |  | 0.33333 | 60 | 264 | 0 | 264
Healthcare Facility and Hospitals (Exam/Treatment Room) | Floor 2 Exam 8 | 1 | 270 | 15 | n/a |  |  | 0.33333 | 15 | 90 | 0 | 90
Healthcare Facility and Hospitals (Exam/Treatment Room) | Floor 2 Exam 9 | 2 | 396 | 15 | n/a |  |  | 0.33333 | 30 | 132 | 0 | 132
Corridor Area | Floor 2 Exam Hall 1 | 1 | 180 | 15 | 0.15 |  |  | 0 | 15 | 27 | 0 | 27
Corridor Area | Floor 2 Exam Hall 2 | 1 | 180 | 15 | 0.15 |  |  | 0 | 15 | 27 | 0 | 27
Corridor Area | Floor 2 Exam Hall 3 | 1 | 180 | 15 | 0.15 |  |  | 0 | 15 | 27 | 0 | 27
Corridor Area | Floor 2 Exam Hall 4 | 1 | 198 | 15 | 0.15 |  |  | 0 | 15 | 29.7 | 0 | 29.7
Corridor Area | Floor 2 Exam Hall 5 | 1 | 198 | 15 | 0.15 |  |  | 0 | 15 | 29.7 | 0 | 29.7
Corridor Area | Floor 2 Exam Hall 6 | 1 | 198 | 15 | 0.15 |  |  | 0 | 15 | 29.7 | 0 | 29.7
Storage (General) | Floor 2 Janitor | 0 | 63 | 15 | 0.15 |  |  | 0 | 0 | 9.45 | 0 | 9.45
Lounge, Breakroom, or Waiting Area | Floor 2 Lounge | 3 | 80 | 15 | 0.15 |  |  | 0 | 45 | 12 | 0 | 45
Healthcare Facility and Hospitals (Nurse's Station) | Floor 2 Nurse Station 1 | 1 | 150 | 15 | n/a |  |  | 0.33333 | 15 | 50 | 0 | 50
Healthcare Facility and Hospitals (Nurse's Station) | Floor 2 Nurse Station 2 | 1 | 180 | 15 | n/a |  |  | 0.33333 | 15 | 60 | 0 | 60
Office Area (>250 square feet) | Floor 2 Office | 2.8 | 560 | 15 | 0.15 |  |  | 0 | 42 | 84 | 0 | 84
Corridor Area | Floor 2 Office Hall | 2 | 444 | 15 | 0.15 |  |  | 0 | 30 | 66.6 | 0 | 66.6
Reception area | Floor 2 Reception | 4.92 | 984 | 15 | 0.15 |  |  | 0 | 73.8 | 147.6 | 0 | 147.6
Corridor Area | Floor 2 Reception Hall | 3 | 564 | 15 | 0.15 |  |  | 0 | 45 | 84.6 | 0 | 84.6
Restrooms | Floor 2 Reception Toilet | 1 | 126 | 15 | n/a |  | 150 | 0 | 15 | 0 | 150 | 150 | Toilet rooms, intermittent exhaust 50 cfm per toilet
Office Area (>250 square feet) | Floor 2 Scheduling 1 | 1.62 | 324 | 15 | 0.15 |  |  | 0 | 24.3 | 48.6 | 0 | 48.6
Office Area (>250 square feet) | Floor 2 Scheduling 2 | 1.71 | 342 | 15 | 0.15 |  |  | 0 | 25.65 | 51.3 | 0 | 51.3
Storage (General) | Floor 2 Storage 1 | 0 | 56 | 15 | 0.15 |  |  | 0 | 0 | 8.4 | 0 | 8.4
Storage (General) | Floor 2 Storage 2 | 0 | 120 | 15 | 0.15 |  |  | 0 | 0 | 18 | 0 | 18
Storage (General) | Floor 2 Storage 3 | 0 | 144 | 15 | 0.15 |  |  | 0 | 0 | 21.6 | 0 | 21.6
Storage (General) | Floor 2 Utility | 0 | 126 | 15 | 0.15 |  |  | 0 | 0 | 18.9 | 0 | 18.9
Office Area (>250 square feet) | Floor 2 Work | 8.45 | 1690 | 15 | 0.15 |  |  | 0 | 126.75 | 253.5 | 0 | 253.5
Corridor Area | Floor 2 Work Hall | 4 | 834 | 15 | 0.15 |  |  | 0 | 60 | 125.1 | 0 | 125.1
Restrooms | Floor 2 Work Toilet | 0 | 54 | 15 | n/a |  | 50 | 0 | 0 | 0 | 50 | 50 | Toilet rooms, intermittent exhaust 50 cfm per toilet
Healthcare Facility and Hospitals (Imaging Room) | Floor 2 X-Ray | 5 | 900 | 15 | n/a | 2.02 |  | 0.33333 | 75 | 300 | 1818 | 1818 | Exhaust Rate assumed according to PNNL outpatient model.The PNNL outpatient model used ASHRAE 170 / CMC Table 4-A (Negative Pressure X-ray room , exhaust Required))
Office Area (<250 square feet) | Floor 3 Dressing Room | 0.21 | 42 | 15 | 0.15 |  |  | 0 | 3.15 | 6.3 | 0 | 6.3
Corridor Area | Floor 3 Elevator Hall | 2 | 370 | 15 | 0.15 |  |  | 0 | 30 | 55.5 | 0 | 55.5
Office Area (<250 square feet) | Floor 3 Humid | 0.54 | 108 | 15 | 0.15 |  |  | 0 | 8.1 | 16.2 | 0 | 16.2
Storage (General) | Floor 3 Janitor | 0 | 63 | 15 | 0.15 |  |  | 0 | 0 | 9.45 | 0 | 9.45
Locker Room | Floor 3 Locker | 1 | 120 | 15 | n/a | 0.25 |  | 0 | 15 | 0 | 30 | 30
Lounge, Breakroom, or Waiting Area | Floor 3 Lounge | 25 | 759 | 15 | 0.15 |  |  | 0 | 375 | 113.85 | 0 | 375
Restrooms | Floor 3 Lounge Toilet | 1 | 192 | 15 | n/a |  | 200 | 0 | 15 | 0 | 200 | 200 | Toilet rooms, intermittent exhaust 50 cfm per toilet
Electrical, Mechanical, Telephone Rooms | Floor 3 Mechanical | 1 | 350 | 15 | n/a |  |  | 0 | 15 | 0 | 0 | 15
Corridor Area | Floor 3 Mechanical Hall | 2 | 300 | 15 | 0.15 |  |  | 0 | 30 | 45 | 0 | 45
Office Area (>250 square feet) | Floor 3 Office | 15.18 | 3036 | 15 | 0.15 |  |  | 0 | 227.7 | 455.4 | 0 | 455.4
Corridor Area | Floor 3 Office Hall | 4 | 834 | 15 | 0.15 |  |  | 0 | 60 | 125.1 | 0 | 125.1
Restrooms | Floor 3 Office Toilet | 0 | 54 | 15 | n/a |  | 50 | 0 | 0 | 0 | 50 | 50 | Toilet rooms, intermittent exhaust 50 cfm per toilet
Healthcare Facility and Hospitals (Physical Therapy Room) | Floor 3 Physical Therapy 1 | 7 | 1300 | 15 | n/a |  |  | 0.33333 | 105 | 433.3333 | 0 | 433.3333
Healthcare Facility and Hospitals (Physical Therapy Room) | Floor 3 Physical Therapy 2 | 3 | 592 | 15 | n/a |  |  | 0.33333 | 45 | 197.3333 | 0 | 197.3333
Restrooms | Floor 3 Physical Therapy Toilet | 0 | 84 | 15 | n/a |  | 100 | 0 | 0 | 0 | 100 | 100 | Toilet rooms, intermittent exhaust 50 cfm per toilet
Storage (General) | Floor 3 Storage 1 | 0 | 108 | 15 | 0.15 |  |  | 0 | 0 | 16.2 | 0 | 16.2
Storage (General) | Floor 3 Storage 2 | 0 | 84 | 15 | 0.15 |  |  | 0 | 0 | 12.6 | 0 | 12.6
Healthcare Facility and Hospitals (Exam/Treatment Room) | Floor 3 Treatment | 2 | 476 | 15 | n/a |  |  | 0.33333 | 30 | 158.6667 | 0 | 158.6667
Storage (General) | Floor 3 Undeveloped 1 | 5 | 2268 | 15 | 0.15 |  |  | 0 | 75 | 340.2 | 0 | 340.2
Storage (General) | Floor 3 Undeveloped 2 | 2 | 1152 | 15 | 0.15 |  |  | 0 | 30 | 172.8 | 0 | 172.8
Storage (General) | Floor 3 Utility | 0 | 216 | 15 | 0.15 |  |  | 0 | 0 | 32.4 | 0 | 32.4
Office Area (>250 square feet) | Floor 3 Work | 2.87 | 574 | 15 | 0.15 |  |  | 0 | 43.05 | 86.1 | 0 | 86.1
Stairwell | NE Stair | 1 | 168 | 15 | 0.15 |  |  | 0 | 15 | 25.2 | 0 | 25.2
Elevator | NW Elevator | 0 | 140 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0
Stairwell | NW Stair | 1 | 192 | 17 | 0.15 |  |  | 0 | 17 | 28.8 | 0 | 28.8
Stairwell | SW Stair | 0 | 96 | 18 | 0.15 |  |  | 0 | 0 | 14.4 | 0 | 14.4
Total (23 Space types) | Total ( 118 spaces) | 258.978 | 40946 | 19 |  |  |  |  | 4920.582 | 0 | 0 | 4920.582
* calculated from CMC Table 4-A minimum outdoor ACH; cfm/ft² = ACH × 10 ft ceiling / 60. Table 4-A does not list cfm/ft².
Outdoor Airflow Rate per space type
Space Type | Total Floor Area (ft²) | Min. Occupancy Load (persons/1000 ft²) | Total Number of Occupants | cfm/ft² (Table 120.1-A – Minimum Ventilation Rates) | Required Exhaust Rate-cfm/ft² (Table 120.1-B – Minimum Exhaust Rates) | Min OA Ventilation Requirement-ACH-(Table 4-A, 2022 California Mechanical Code) | Min OA Ventilation Requirement-cfm/ft²-(Table 4-A, 2022 California Mechanical Code) | cfm
Healthcare Facility and Hospitals (Exam/Treatment Room) | 4606 | 10 | 46.06 | n/a | Floor 1 Anesthesia | 2 | 0.33333 | 1647
Healthcare Facility and Hospitals (Medical Supply Room) | 765 | 10 | 7.65 | n/a | Floor 1 Soil, Floor 1 Soil Hold, and Floor 1 Soil Work | 2 | 0.33333 | 728
Healthcare Facility and Hospitals (Imaging Room) | 1508 | 10 | 15.08 | n/a | Floor 1 MRI Room, Floor 1 MRI Control Room, Floor 2 X-Ray | 2 | 0.33333 | 3046
Healthcare Facility and Hospitals (Nurse's Station) | 591 | 10 | 5.91 | n/a |  | 2 | 0.33333 | 197
Healthcare Facility and Hospitals (Operating Room) | 1416 | 10 | 14.16 | n/a |  | 4 | 0.66667 | 944
Healthcare Facility and Hospitals (Recovery Room) | 948 | 10 | 9.48 | n/a |  | 2 | 0.33333 | 316
Healthcare Facility and Hospitals (Physical Therapy Room) | 1892 | 10 | 18.92 | n/a |  | 2 | 0.33333 | 630.6667
Healthcare Facility and Hospitals (Patient Room) | 527 | 10 | 5.27 | n/a |  | 2 | 0.33333 | 175.6667
Dining Area (Cafeteria/Fast Food) | 420 | 33 | 13.86 | 0.15 |  |  |  | 207.9
Office Area (<250 square feet) | 676 | 5 | 3.38 | 0.15 |  |  |  | 101.4
Office Area (>250 square feet) | 7009 | 5 | 35.045 | 0.15 |  |  |  | 1051.35
Convention, Conference, Multipurpose and Meeting Area | 0 | 33 | 0 | 0.15 |  |  |  | 0
Lobby, Main Entry | 622 | 33 | 20.526 | 0.15 |  |  |  | 307.89
Corridor Area | 7879 | 5 | 39.395 | 0.15 |  |  |  | 1181.85
Restrooms | 790 | 5 | 3.95 | n/a | 50/70 cfm/Unit |  |  | 0
Locker Room | 0 | 10 | 0 | n/a | 0.25 |  |  | #VALUE!
Kitchen/Food Preparation Area | 182 | 3 | 0.546 | 0.15 | 0.7 |  |  | 127.4
Storage (General) | 6172 | 2 | 12.344 | 0.15 |  |  |  | 925.8
Lounge, Breakroom, or Waiting Area | 0 | 33 | 0 | 0.15 |  |  |  | 0
Reception area | 1493 | 5 | 7.465 | 0.15 |  |  |  | 223.95
Stairwell | 456 | 5 | 2.28 | 0.15 |  |  |  | 68.4
Electrical, Mechanical, Telephone Rooms | 0 | 1.5 | 0 | n/a |  |  |  | #VALUE!
Total | 37952 |  | 261.321 |  |  |  |  | #VALUE!

## Water Heater
Water Heater - Outpatient
Vintage | WH Type | Efficiency | Number of WH | Tank Volume (gal) | Tank Loss | Source
Existing | Gas | 0.8 | 1 | See table below for CZ-specific values: Climate Zone Water Heater Sizing and Loss Coefficients, Storage Volume column (col F) | See table below: Climate Zone Water Heater Sizing and Loss Coefficients, Standby Loss column (col G) | See table below for sources: Climate Zone Water Heater Sizing and Loss Coefficients
New Construction | Gas | 0.8 | 1 | See table below for CZ-specific values: Climate Zone Water Heater Sizing and Loss Coefficients, Storage Volume column (col F) | See table below: Climate Zone Water Heater Sizing and Loss Coefficients, Standby Loss column (col G) | See table below for sources: Climate Zone Water Heater Sizing and Loss Coefficients
Peak Hot Water Consumption
Space Name | Baseline WH Type [CEUS 2022] | Total Area (ft²) |  | Number of People | Hot Water Usage Specification (gal/hr per person) [T24, 2022, Appendix 5.4A , sheet: "2022 SpaceFuncData-Input"] | Peak Hot Water Usage (gal/hr) | Peak Hot Water Usage (gal/min) | Note
Floor 1 Anesthesia | Gas | 108 |  | 1 | 0.24 | 0.24 | 0.004 | For space types marked with an asterisk (the ‘*’ symbol), the water‑heater type is listed as electric in Appendix 5.4A, sheet ‘2022 SpaceFuncData‑Input.’ However, we modified the value based on CEUS data, which indicates that gas is the primary fuel type.
Floor 1 Bio Haz | Gas | 56 |  | 0 | 0.24 | 0 | 0
Floor 1 Café | Gas | 420 |  | 14 | 0.578 | 8.092 | 0.13487
Floor 1 Clean | Gas | 126 |  | 1 | 0.24 | 0.24 | 0.004
Floor 1 Clean Work | Gas | 165 |  | 1 | 0.24 | 0.24 | 0.004
Floor 1 Dictation | Gas | 126 |  | 0.63 | 0.18 | 0.1134 | 0.00189
Floor 1 Dressing Room | Gas | 45 |  | 0.225 | 0.18 | 0.0405 | 0.000675
Floor 1 Electrical Room | Gas | 98 |  | 0 | 0.18 | 0 | 0
Floor 1 Elevator Pump Room | Gas | 91 |  | 0 | 0.18 | 0 | 0
Floor 1 Humid | Gas | 54 |  | 0.27 | 0.18 | 0.0486 | 0.00081
Floor 1 IT Hall | Gas | 140 |  | 1 | 0 | 0 | 0
Floor 1 IT Room | Gas | 112 |  | 0.56 | 0.18 | 0.1008 | 0.00168
Floor 1 Lobby | Gas | 622 |  | 21 | 0.09 | 1.89 | 0.0315
Floor 1 Lobby Hall | Gas | 240 |  | 1 | 0 | 0 | 0
Floor 1 Lobby Toilet | Gas | 54 |  | 0 | 0 | 0 | 0
Floor 1 Locker Room | Gas | 660 |  | 7 | 0.578 | 4.046 | 0.067433
Floor 1 Locker Room Hall | Gas | 496 |  | 2 | 0 | 0 | 0
Floor 1 Lounge | Gas | 360 |  | 12 | 0.09 | 1.08 | 0.018
Floor 1 Med Gas | Gas | 56 |  | 0 | 0.24 | 0 | 0
Floor 1 MRI Control Room | Gas | 168 |  | 1 | 0.24 | 0.24 | 0.004
Floor 1 MRI Hall | Gas | 147 |  | 1 | 0 | 0 | 0
Floor 1 MRI Room | Gas | 440 |  | 2 | 0.24 | 0.48 | 0.008
Floor 1 MRI Toilet | Gas | 54 |  | 0 | 0 | 0 | 0
Floor 1 Nourishment | Gas | 182 |  | 1 | 0.578 | 0.578 | 0.0096333
Floor 1 Nurse Hall | Gas | 496 |  | 2 | 0 | 0 | 0
Floor 1 Nurse Janitor | Gas | 54 |  | 0 | 0 | 0 | 0
Floor 1 Nurse Station | Gas | 261 |  | 1 | 0.24 | 0.24 | 0.004
Floor 1 Nurse Toilet | Gas | 54 |  | 0 | 0 | 0 | 0
Floor 1 Office | Gas | 483 |  | 2.415 | 0.18 | 0.4347 | 0.007245
Floor 1 Operating Room 1 | Gas | 460 |  | 2 | 0.24 | 0.48 | 0.008
Floor 1 Operating Room 2 | Gas | 480 |  | 2 | 0.24 | 0.48 | 0.008
Floor 1 Operating Room 3 | Gas | 476 |  | 2 | 0.24 | 0.48 | 0.008
Floor 1 PACU | Gas | 108 |  | 1 | 0.24 | 0.24 | 0.004
Floor 1 Pre-Op Hall | Gas | 528 |  | 3 | 0 | 0 | 0
Floor 1 Pre-Op Room 1 | Gas | 189 |  | 1 | 0.24 | 0.24 | 0.004
Floor 1 Pre-Op Room 2 | Gas | 338 |  | 2 | 0.24 | 0.48 | 0.008
Floor 1 Pre-Op Toilet | Gas | 54 |  | 0 | 0 | 0 | 0
Floor 1 Procedure Room | Gas | 285 |  | 1 | 0.24 | 0.24 | 0.004
Floor 1 Reception | Gas | 509 |  | 2.545 | 0.18 | 0.4581 | 0.007635
Floor 1 Reception Hall | Gas | 128 |  | 1 | 0 | 0 | 0
Floor 1 Recovery Room | Gas | 540 |  | 3 | 0.24 | 0.72 | 0.012
Floor 1 Scheduling | Gas | 119 |  | 0.595 | 0.18 | 0.1071 | 0.001785
Floor 1 Scrub | Gas | 84 |  | 0 | 0 | 0 | 0
Floor 1 Soil | Gas | 126 |  | 1 | 0.24 | 0.24 | 0.004
Floor 1 Soil Hold | Gas | 56 |  | 0 | 0.24 | 0 | 0
Floor 1 Soil Work | Gas | 180 |  | 1 | 0.24 | 0.24 | 0.004
Floor 1 Step Down | Gas | 300 |  | 2 | 0.24 | 0.48 | 0.008
Floor 1 Sterile Hall | Gas | 616 |  | 3 | 0 | 0 | 0
Floor 1 Sterile Storage | Gas | 396 |  | 1 | 0 | 0 | 0
Floor 1 Storage | Gas | 920 |  | 2 | 0 | 0 | 0
Floor 1 Sub-Sterile | Gas | 196 |  | 1 | 0 | 0 | 0
Floor 1 Utility Hall | Gas | 256 |  | 1 | 0 | 0 | 0
Floor 1 Utility Janitor | Gas | 42 |  | 0 | 0 | 0 | 0
Floor 1 Utility Room | Gas | 360 |  | 1 | 0 | 0 | 0
Floor 1 Vestibule | Gas | 72 |  | 0 | 0 | 0 | 0
Floor 2 Conference | Gas | 336 |  | 11.088 | 0.09 | 0.99792 | 0.016632
Floor 2 Conference Toilet | Gas | 64 |  | 0 | 0 | 0 | 0
Floor 2 Dictation | Gas | 70 |  | 0.35 | 0.18 | 0.063 | 0.00105
Floor 2 Exam 1 | Gas | 360 |  | 2 | 0.24 | 0.48 | 0.008
Floor 2 Exam 2 | Gas | 540 |  | 3 | 0.24 | 0.72 | 0.012
Floor 2 Exam 3 | Gas | 720 |  | 4 | 0.24 | 0.96 | 0.016
Floor 2 Exam 4 | Gas | 84 |  | 0 | 0.24 | 0 | 0
Floor 2 Exam 5 | Gas | 350 |  | 2 | 0.24 | 0.48 | 0.008
Floor 2 Exam 6 | Gas | 225 |  | 1 | 0.24 | 0.24 | 0.004
Floor 2 Exam 7 | Gas | 792 |  | 4 | 0.24 | 0.96 | 0.016
Floor 2 Exam 8 | Gas | 270 |  | 1 | 0.24 | 0.24 | 0.004
Floor 2 Exam 9 | Gas | 396 |  | 2 | 0.24 | 0.48 | 0.008
Floor 2 Exam Hall 1 | Gas | 180 |  | 1 | 0 | 0 | 0
Floor 2 Exam Hall 2 | Gas | 180 |  | 1 | 0 | 0 | 0
Floor 2 Exam Hall 3 | Gas | 180 |  | 1 | 0 | 0 | 0
Floor 2 Exam Hall 4 | Gas | 198 |  | 1 | 0 | 0 | 0
Floor 2 Exam Hall 5 | Gas | 198 |  | 1 | 0 | 0 | 0
Floor 2 Exam Hall 6 | Gas | 198 |  | 1 | 0 | 0 | 0
Floor 2 Janitor | Gas | 63 |  | 0 | 0 | 0 | 0
Floor 2 Lounge | Gas | 80 |  | 3 | 0.09 | 0.27 | 0.0045
Floor 2 Nurse Station 1 | Gas | 150 |  | 1 | 0.24 | 0.24 | 0.004
Floor 2 Nurse Station 2 | Gas | 180 |  | 1 | 0.24 | 0.24 | 0.004
Floor 2 Office | Gas | 560 |  | 2.8 | 0.18 | 0.504 | 0.0084
Floor 2 Office Hall | Gas | 444 |  | 2 | 0 | 0 | 0
Floor 2 Reception | Gas | 984 |  | 4.92 | 0.18 | 0.8856 | 0.01476
Floor 2 Reception Hall | Gas | 564 |  | 3 | 0 | 0 | 0
Floor 2 Reception Toilet | Gas | 126 |  | 1 | 0 | 0 | 0
Floor 2 Scheduling 1 | Gas | 324 |  | 1.62 | 0.18 | 0.2916 | 0.00486
Floor 2 Scheduling 2 | Gas | 342 |  | 1.71 | 0.18 | 0.3078 | 0.00513
Floor 2 Storage 1 | Gas | 56 |  | 0 | 0 | 0 | 0
Floor 2 Storage 2 | Gas | 120 |  | 0 | 0 | 0 | 0
Floor 2 Storage 3 | Gas | 144 |  | 0 | 0 | 0 | 0
Floor 2 Utility | Gas | 126 |  | 0 | 0 | 0 | 0
Floor 2 Work | Gas | 1690 |  | 8.45 | 0.18 | 1.521 | 0.02535
Floor 2 Work Hall | Gas | 834 |  | 4 | 0 | 0 | 0
Floor 2 Work Toilet | Gas | 54 |  | 0 | 0 | 0 | 0
Floor 2 X-Ray | Gas | 900 |  | 5 | 0.24 | 1.2 | 0.02
Floor 3 Dressing Room | Gas | 42 |  | 0.21 | 0.18 | 0.0378 | 0.00063
Floor 3 Elevator Hall | Gas | 370 |  | 2 | 0 | 0 | 0
Floor 3 Humid | Gas | 108 |  | 0.54 | 0.18 | 0.0972 | 0.00162
Floor 3 Janitor | Gas | 63 |  | 0 | 0 | 0 | 0
Floor 3 Locker | Gas | 120 |  | 1 | 0.578 | 0.578 | 0.0096333
Floor 3 Lounge | Gas | 759 |  | 25 | 0.09 | 2.25 | 0.0375
Floor 3 Lounge Toilet | Gas | 192 |  | 1 | 0 | 0 | 0
Floor 3 Mechanical | Gas | 350 |  | 1 | 0.18 | 0.18 | 0.003
Floor 3 Mechanical Hall | Gas | 300 |  | 2 | 0 | 0 | 0
Floor 3 Office | Gas | 3036 |  | 15.18 | 0.18 | 2.7324 | 0.04554
Floor 3 Office Hall | Gas | 834 |  | 4 | 0 | 0 | 0
Floor 3 Office Toilet | Gas | 54 |  | 0 | 0 | 0 | 0
Floor 3 Physical Therapy 1 | Gas | 1300 |  | 7 | 0.24 | 1.68 | 0.028
Floor 3 Physical Therapy 2 | Gas | 592 |  | 3 | 0.24 | 0.72 | 0.012
Floor 3 Physical Therapy Toilet | Gas | 84 |  | 0 | 0 | 0 | 0
Floor 3 Storage 1 | Gas | 108 |  | 0 | 0 | 0 | 0
Floor 3 Storage 2 | Gas | 84 |  | 0 | 0 | 0 | 0
Floor 3 Treatment | Gas | 476 |  | 2 | 0.24 | 0.48 | 0.008
Floor 3 Undeveloped 1 | Gas | 2268 |  | 5 | 0 | 0 | 0
Floor 3 Undeveloped 2 | Gas | 1152 |  | 2 | 0 | 0 | 0
Floor 3 Utility | Gas | 216 |  | 0 | 0 | 0 | 0
Floor 3 Work | Gas | 574 |  | 2.87 | 0.18 | 0.5166 | 0.00861
NE Stair | Gas | 168 |  | 1 | 0 | 0 | 0
NW Elevator | Gas | 140 |  | 0 | 0 | 0 | 0
NW Stair | Gas | 192 |  | 1 | 0 | 0 | 0
SW Stair | Gas | 96 |  | 0 | 0 | 0 | 0
Total | Gas storage |  |  |  |  | 75 |  | Minimum peak hot water usage is 75 gal according to ACM 2025
Total | Electric resistance |  |  |  |  | 0
Design supply temperature (°F) | 135 | CEC-400-2022-009-CMF-REV2-AP5.4B
WH system factor | 0.6 | 2025 ACM §5.9.2 Rated Capacity
Water mass conversion (lb/gal) | 8.2877 | 2025 ACM §5.9.2 Rated Capacity
Reheat multiplier | 0.4 | 2025 ACM §5.9.2 Storage Volume
Climate Zone Water Heater Sizing and Loss Coefficients
Climate Zone | Minimum Monthly Mains Temp (°F) [T24 2022 - Appendix 5.4B] | Heat Output (Btu/hr) [ACM, 2025, 5.9.2: Rated capacity section] |  | WH Capacity (Btu/hr) [ACM, 2025, 5.9.2: Rated capacity section] | Required Energy Input (Btu/hr) | Storage Volume (gal) | Standby Loss [Title 20, §1605.1 Table F-4; Appendix B: Water Heating Calculation Method] |  | Off/On Cycle Loss Coefficient to Ambient Temp |  | Source/Note
CZ01 | 47.9 | 54139.4002 |  | 32483.6401 | 60000 | 34 | 716.4047 | Btu/hr | 10.2344 | Btu/h·°F | Required Energy Input: vendor/available catalog size (Market data table). Storage Volume: standard/available catalog tank size (Market data table).
CZ02 | 50.8 | 52336.8255 |  | 31402.0953 | 60000 | 34 | 716.4047 | Btu/hr | 10.2344 | Btu/h·°F
CZ03 | 52.2 | 51466.617 |  | 30879.9702 | 60000 | 34 | 716.4047 | Btu/hr | 10.2344 | Btu/h·°F
CZ04 | 52.7 | 51155.8282 |  | 30693.4969 | 60000 | 34 | 716.4047 | Btu/hr | 10.2344 | Btu/h·°F
CZ05 | 51.6 | 51839.5635 |  | 31103.7381 | 60000 | 34 | 716.4047 | Btu/hr | 10.2344 | Btu/h·°F
CZ06 | 56.8 | 48607.3605 |  | 29164.4163 | 60000 | 34 | 716.4047 | Btu/hr | 10.2344 | Btu/h·°F
CZ07 | 58.4 | 47612.8365 |  | 28567.7019 | 60000 | 34 | 716.4047 | Btu/hr | 10.2344 | Btu/h·°F
CZ08 | 58.4 | 47612.8365 |  | 28567.7019 | 60000 | 34 | 716.4047 | Btu/hr | 10.2344 | Btu/h·°F
CZ09 | 57.6 | 48110.0985 |  | 28866.0591 | 60000 | 34 | 716.4047 | Btu/hr | 10.2344 | Btu/h·°F
CZ10 | 57.1 | 48420.8872 |  | 29052.5323 | 60000 | 34 | 716.4047 | Btu/hr | 10.2344 | Btu/h·°F
CZ11 | 50.5 | 52523.2987 |  | 31513.9792 | 60000 | 34 | 716.4047 | Btu/hr | 10.2344 | Btu/h·°F
CZ12 | 51.4 | 51963.879 |  | 31178.3274 | 60000 | 34 | 716.4047 | Btu/hr | 10.2344 | Btu/h·°F
CZ13 | 51.7 | 51777.4057 |  | 31066.4434 | 60000 | 34 | 716.4047 | Btu/hr | 10.2344 | Btu/h·°F
CZ14 | 50.1 | 52771.9297 |  | 31663.1578 | 60000 | 34 | 716.4047 | Btu/hr | 10.2344 | Btu/h·°F
CZ15 | 63.2 | 44629.2645 |  | 26777.5587 | 60000 | 34 | 716.4047 | Btu/hr | 10.2344 | Btu/h·°F
CZ16 | 41.4 | 58179.654 |  | 34907.7924 | 60000 | 34 | 716.4047 | Btu/hr | 10.2344 | Btu/h·°F
Market data
Catalog gas input (Btu/h) | Input source | Elec resistance tank (kW) |  | Elec resistance (Btu/h) | Catalog gas tank (gal) | Tank source | Elec tank (gal) | Elec tank source | Sources and links → Note tab
60000 | Grainger | 1.5 |  | 5118 | 34 | ENERGY STAR | 6 | Grainger
75100 | Grainger | 2 |  | 6824 | 35 | Grainger | 10 | Grainger
76000 | Both | 3 |  | 10236 | 48 | Grainger | 15 | Grainger
80000 | Grainger | 4.5 |  | 15355 | 50 | Both | 20 | Grainger
99900 | ENERGY STAR | 6 |  | 20473 | 55 | ENERGY STAR | 28 | Grainger
100000 | Both | 8 |  | 27297 | 60 | ENERGY STAR | 30 | Grainger
120000 | ENERGY STAR | 9 |  | 30709 | 65 | Both | 36 | Grainger
125000 | Both | 10 |  | 34121 | 72 | Grainger | 40 | Grainger
130000 | Both | 12 |  | 40946 | 75 | Both | 47
145000 | ENERGY STAR | 12.1 |  | 41287 | 76 | Grainger | 50
150000 | ENERGY STAR | 18 |  | 61419 | 80 | Both | 65
156000 | Grainger | 24 |  | 81891 | 82 | Grainger | 80
160000 | Both | 27 |  | 92128 | 85 | Grainger | 85
175000 | ENERGY STAR | 36 |  | 122837 | 90 | Both | 105
180000 | Grainger | 54 |  | 184256 | 91 | Grainger | 120
199000 | ENERGY STAR |  |  |  | 100 | Both
199900 | Both |  |  |  | 110 | ENERGY STAR
200000 | ENERGY STAR |  |  |  | 119 | Both
250000 | Both |  |  |  | 125 | ENERGY STAR
251000 | ENERGY STAR
270000 | Grainger
285000 | ENERGY STAR
300000 | Both
320000 | ENERGY STAR
360000 | Grainger
398000 | ENERGY STAR
399000 | ENERGY STAR
399900 | Both
499900 | Grainger
550000 | Grainger
715000 | Grainger
Space Type | Hot Water Usage Specification (gal/hr per person) [T24, 2022, Appendix 5.4A , sheet: "2022 SpaceFuncData-Input"]
Healthcare Facility and Hospitals (Exam/Treatment Room) | 0.24
Healthcare Facility and Hospitals (Medical Supply Room) | 0.24
Healthcare Facility and Hospitals (Imaging Room) | 0.24
Healthcare Facility and Hospitals (Nurse's Station) | 0.24
Healthcare Facility and Hospitals (Operating Room) | 0.24
Healthcare Facility and Hospitals (Recovery Room) | 0.24
Healthcare Facility and Hospitals (Physical Therapy Room) | 0.24
Healthcare Facility and Hospitals (Patient Room) | 0.24
Dining Area (Cafeteria/Fast Food) | 0.578
Office Area (<250 square feet) | 0.18
Office Area (>250 square feet) | 0.18
Convention, Conference, Multipurpose and Meeting Area | 0.09
Lobby, Main Entry | 0.09
Corridor Area | 0
Restrooms | 0
Locker Room | 0.578
Kitchen/Food Preparation Area | 0.578
Storage (General) | 0
Lounge, Breakroom, or Waiting Area | 0.09
Reception area | 0.18
Stairwell | 0
Electrical, Mechanical, Telephone Rooms | 0.18

## Interior Lights
Interior Lighting - Outpatient
Space | New Construction |  |  | Existing |  |  | Notes
| LPD (W/ft²) | Additional LPD for Portable Lighting (W/ft²) | Source | LPD (W/ft²) | Additional LPD for Portable Lighting (W/ft²) | Source
Healthcare Facility and Hospitals (Exam/Treatment Room) | 1.15 |  | T24, 2025, Table 140.6 C (Area category method) | 1.2 |  | T24, 2016, Table 140.6 C (Area category method)
Healthcare Facility and Hospitals (Medical Supply Room) | 0.55 |  |  | 1.2
Healthcare Facility and Hospitals (Imaging Room) | 0.6 | 0.2 |  | 1.2 |  |  | Additional lighting for: decorative/display
Healthcare Facility and Hospitals (Nurse's Station) | 0.85 | 0.2 |  | 1.2 |  |  | Additional lighting for: detailed task work
Healthcare Facility and Hospitals (Operating Room) | 1.9 |  |  | 1.2
Healthcare Facility and Hospitals (Recovery Room) | 0.9 | 0.1 |  | 1.2 |  |  | Additional lighting for: tunable white or dim-to-warm
Healthcare Facility and Hospitals (Physical Therapy Room) | 0.75 | 0.1 |  | 1.2 |  |  | Additional lighting for: tunable white or dim-to-warm
Healthcare Facility and Hospitals (Patient Room) | 0.7 | 0.15 |  | 1.2 |  |  | Additional lighting for: detailed task work
Dining Area (Cafeteria/Fast Food) | 0.45 | 0.25 |  | 1 |  |  | Additional lighting for: decorative/display
Office Area (<250 square feet) | 0.65 | 0.1 |  | 1 |  |  | Additional lighting for: decorative/display It is assumed that 50% of the additional allowance lighting is in use.
Office Area (>250 square feet) | 0.6 | 0.1 |  | 0.75 |  |  | Additional lighting for: decorative/display It is assumed that 50% of the additional allowance lighting is in use.
Convention, Conference, Multipurpose and Meeting Area | 0.75 | 0.25 |  | 1.2 | 0.5 |  | Additional lighting for: decorative/display
Lobby, Main Entry | 0.7 | 0.25 |  | 0.95 | 0.5 |  | Additional lighting for: decorative/display
Corridor Area | 0.4 |  |  | 0.6 |  |  | Additional lighting for: decorative/display
Restrooms | 0.65 |  |  | 0.6 |  |  | Additional lighting for: decorative/display
Locker Room | 0.45 |  |  | 0.7
Kitchen/Food Preparation Area | 0.95 |  |  | 1.2
Storage (General) | 0.4 |  |  | 0.6
Lounge, Breakroom, or Waiting Area | 0.55 | 0.25 |  | 0.9 | 0.5 |  | Additional lighting for: decorative/display
Stairwell | 0.6 |  |  | 0.6 |  |  | Additional lighting for: decorative/display
Electrical, Mechanical, Telephone Rooms | 0.4 |  |  | 0.55 |  |  | Additional lighting for: decorative/display
Reception area | 0.7 | 0.25 |  | 0.95 | 0.2 |  | Additional lighting for: decorative/display
Elevator | 0 |  |  | 0

## Ext Lighting
Exterior Lighting - Outpatient
Motion Controlled Luminaires (W) | Non-motion Controlled Luminaires (W) | Total (W) | Source
2390.08 | 1552.635 | 3942.715 | T24, 2022 & 2025 2019 Outdoor Lighting CASE report PNNL 90.1-2010 TSD
Exterior Lighting
Items (Assume LZ2) | Assumptions [2019 Outdoor Lighting CASE Report] |  | Unit | Lighting Power Allowance [Title 24, 2025, Table 140.7-A & 140.7-B] | Unit | Exterior Lighting Power (W)
IWA (Initial Wattage Allowance) | Lighting Zone 3 |  |  | 350 | (W) | 350
Parking area | 400 ft² for every parking space [2019 Lighting CASE report, Appendix H] 1 parking space per 360 ft² of gross building area [2019 Lighting CASE report,Table 38] | 45500 | (ft²) | 0.025 | (W/ft²) | 1638
Building Entrance | 14 building entrance Per building Geometry | 14 | (count) | 19 | (W/ea) | 266
Hardscape Ornamental Light | 0.1 ft² per 1 ft² of gross building area [2019 Lighting CASE report,Table 36] | 4095 | (ft²) | 0.013 | (W/ft²) | 53.235
Building façade | 0.1 W per 1 ft² of facade area Façade Area = Perimeter × 0.5 × 30 ft (30 ft is the max height that is lit) * The 0.5 factor assumes that only half of the perimeter walls are lit. -Formula ia developed based on the 2019 Outdoor Lighting CASE report | 8820 | (ft²) | 0.17 | (W/ft²) | 1499.4
Non-sales canopy |  | 504 | (ft²) | 0.27 | (W/ft²) | 136.08
Motion Controlled Luminaires (W) | [5 empty] | 2390.08
Non-motion-controlled Luminaires | [5 empty] | 1552.635
Total | [5 empty] | 3942.715
Total floor area | 40950
Perimeter | 588
Floors | 3

## Equipment
Equipment - Outpatient
Spaces | Plug load Power Density (W/ft²) | Gas Power Density (Btu/hr-ft²) | Refrigeration Power Density (W/ft²) | Source | Note
Healthcare Facility and Hospitals (Exam/Treatment Room) | 1.5 | 1.1259 |  | T24 2022 - Appendix 5.4A, DOE / PNNL Commercial Prototype Building Models, AEDG 50% | Appendix 5.4A: Gas equipment=1.1259 Btu/h-ft²--CEC model has the Gas equipment for 3.59 Btu/h-ft²
Healthcare Facility and Hospitals (Medical Supply Room) | 1.5
Healthcare Facility and Hospitals (Imaging Room) | 10 |  |  |  | PNNL has EPD=10 for Imaging room
Healthcare Facility and Hospitals (Nurse's Station) | 1.5
Healthcare Facility and Hospitals (Operating Room) | 4 |  |  |  | AEDG 50%
Healthcare Facility and Hospitals (Recovery Room) | 1.5
Healthcare Facility and Hospitals (Physical Therapy Room) | 1.5
Healthcare Facility and Hospitals (Patient Room) | 1.5
Dining Area (Cafeteria/Fast Food) | 0.5 |  | 0.25 |  | CEC: Refrig Load = 0.25 w/ft²
Office Area (<250 square feet) | 0.7 |  |  |  | Plug load and schedules project with CEC, 2025
Office Area (>250 square feet) | 0.7 |  |  |  | Plug load and schedules project with CEC, 2025
Convention, Conference, Multipurpose and Meeting Area | 1
Lobby, Main Entry | 0.5
Corridor Area | 0
Restrooms | 0
Locker Room | 0.5
Kitchen/Food Preparation Area | 1.5 | 17.5377 | 1.12 |  | Appendix 5.4A: Gas equipment=17.53768 -- CEC: Refrig Load = 1.12 w/ft²
Storage (General) | 0.2
Lounge, Breakroom, or Waiting Area | 1
Stairwell | 0
Electrical, Mechanical, Telephone Rooms | 3
Reception area | 0.5
Elevator | 0
Elevator
Vintage | Class | Number of elevators (ne) | Cab Lighting Power Limit (W/ft2) | Fan Power Limit (W/CFM) | Cab Ventilation Fan & Lighting Shutoff | Design Motor Load (W) | Fan Load (W) | Lighting Load (W) | Total (W) | Note
Existing | F/G | 2 | 1.14 | 0.33 | When stopped and unoccupied with doors closed for over 15 minutes, cab interior lighting and ventilation shall be de-energized until required for operation. | 16836.06 | 165 | 68.17 | 17069.23 | Design load is calculated according to ISO 25745-2 method using Class F/G. Cab lighting and fan requirements are based on ASHRAE 90.1 2013.
New Construction | E | 2 | 0.6 | 0.33 | When the elevator cab is stopped and unoccupied with doors closed for over 15 minutes, the cab interior lighting and ventilation fans shall be switched off until elevator cab operation resumes. | 9178.16 | 165 | 35.88 | 9379.04 | Design load is calculated according to ISO 25745-2 method using Class E. Cab lighting and fan requirements are based on T24 2025 §120.6 (f).
Outpatient Health Care Elevator Calculations
Symbol | Definition | Value | Units | Source
E | Annual energy consumption of the elevator - Existing | 54785.87 | kWh/year | Calculated
| Annual energy consumption of the elevator - New Construction | 29866.48 | kWh/year | Calculated
C1 | Running-energy coefficient | 3.65 for Class E; 5.47 for Class F | Coefficient | ISO 25745-2 Table 7
C2 | Idle/standby coefficient | 800 for Class E; 1,600 for Class F | Coefficient | ISO 25745-2 Table 7
Q | Rated load of elevator | 1361 | kg | Assumed for all prototypes
Elevator Size | Cab floor area | 29.9 | ft^2 | W=6.781 ft, L=4.406 ft; assumed based on representative manufacturer
CFM | Cab fan airflow | 250 | cfm | Assumed for multifamily and commercial prototypes
cat | Usage category | 3 | - | ISO 25745-2 Table A.1
d | Operating days per year | 360 | days/year | ISO 25745-2 Table A.1
nf | Number of floors | 3 | floors | Prototype assumptions
h | Floor-to-floor height | 3.05 | m | Prototype assumptions
v | Elevator lift speed | 1.6 | m/s | ISO 25745-2 Table A.1
nd | Number of trips per day | 300 | trips/day | ISO 25745-2 Table A.1
S_pct | Percent of average travel distance | 0.67 | % | ISO 25745-2 Table 2
a | Acceleration | 1 | m/s^2 | Annex B of ISO 25745-2
j | Jerk | 1.25 | m/s^3 | Annex B of ISO 25745-2
td | Door time | 8 | seconds | Annex B of ISO 25745-2
S_av | Average distance traveled per trip | 6.13 | m/trip | Calculated (nf * h * S_pct)
t_av | Average trip time | 14.23 | seconds/trip | Calculated (S_av/v + v/a + a/j + td)
t_nr | Time not running per day | 22.81 | hours/day | Calculated (24 - nd * t_av)
Standby Hours | Annual standby hours | 8333.05 | hours/year | Calculated (24*(365-d)+t_nr*d)
Total light level | Total light level | 40 | lm/ft2 | PNNL Prototypes
EFLH | Equivalent full load hours | 3254.08 | hours | Calculated using the elevator schedule

## Schedules
Schedules - Outpatient
Zone | Schedule Category | Schedule | Source | Type | Hour
[5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
All the zones except those with space type of office or conference | Health | Occupancy | T24 2022 - Appendix 5.4B, [Health] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
All the zones except those with space type of office or conference | Health | Lights | T24 2022 - Appendix 5.4B, [Health] | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.45 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1
|  |  |  | Saturday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
All the zones except those with space type of office or conference | Health | ElecEquipment | T24 2022 - Appendix 5.4B, [Health] | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1
|  |  |  | Saturday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
All the zones except those with space type of office or conference | Health | ServiceHotWater | T24 2022 - Appendix 5.4B, [Health] | Weekday | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.17 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.18 | 0.18 | 0.18 | 0.1 | 0.01 | 0.01
|  |  |  | Saturday | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.2 | 0.28 | 0.3 | 0.3 | 0.24 | 0.24 | 0.23 | 0.23 | 0.23 | 0.1 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
|  |  |  | Sunday | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
All the zones except those with space type of office or conference | Health | GasEquipment | T24 2022 - Appendix 5.4B, [Health] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.75 | 0.2 | 0.1 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
All the zones except those with space type of office or conference | Health | Refrigeration | T24 2022 - Appendix 5.4B, [Health] | Weekday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Saturday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Sunday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
All the zones except those with space type of office or conference | Health | Infiltration | T24 2022 - Appendix 5.4B, [Health] | Weekday | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1
|  |  |  | Saturday | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1
|  |  |  | Sunday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
All the zones except those with space type of office or conference | Health | HVACAvail | T24 2022 - Appendix 5.4B, [Health] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
All the zones except those with space type of office or conference | Health | HtgSetpt |  | Weekday | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
|  |  |  | Saturday | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
|  |  |  | Sunday | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
All the zones except those with space type of office or conference | Health | ClgSetpt |  | Weekday | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
|  |  |  | Saturday | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
|  |  |  | Sunday | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
Other
Zones with space type of Office or conference | Office | Occupancy | T24 2022 - Appendix 5.4B, [Office] Updated base on Plug load and schedules project with CEC, 2025 | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
Zones with space type of Office or conference | Office | Lights | T24 2022 - Appendix 5.4B, [Office] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.35 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Zones with space type of Office or conference | Office | ElecEquipment | Plug load and schedules project with CEC, 2025 | Weekday | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.74 | 0.87 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.5 | 0.45 | 0.45 | 0.45
|  |  |  | Saturday | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43
|  |  |  | Sunday | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43
Zones with space type of Office or conference | Office | HVACAvail | T24 2022 - Appendix 5.4B, [Office] Updated base on Plug load and schedules project with CEC, 202 | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zones with space type of Office or conference | Office | ServiceHotWater | T24 2022 - Appendix 5.4B, [Office] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.12 | 0.14 | 0.07 | 0.07 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05
|  |  |  | Sunday | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04
Zones with space type of Office or conference | Office | Infiltration | T24 2022 - Appendix 5.4B, [Office] Updated base on Plug load and schedules project with CEC, 202 | Weekday | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
Zones with space type of Office or conference | Office | HtgSetpt | Honeywell-INNCOM e7 Thermostat User Guide & Engineering Judgement | Weekday | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
|  |  |  | Saturday | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
|  |  |  | Sunday | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
Zones with space type of Office or conference | Office | ClgSetpt | Honeywell-INNCOM e7 Thermostat User Guide & Engineering Judgement | Weekday | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
|  |  |  | Saturday | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
|  |  |  | Sunday | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
|  | Other | [26 empty] | EFLH
| Building | Elevator | T24 2022 - Appendix 5.4B, [Health] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02 | 0.75 | 1 | 1 | 1 | 0.75 | 1 | 1 | 1 | 1 | 1 | 0.52 | 0.52 | 0.52 | 0.28 | 0 | 0 | 3254.08
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02 | 0.46 | 0.7 | 0.7 | 0.7 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.25 | 0.02 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Building | ExtLightingNonMotionCtrl | PNNL Hospital Prototype (2022) | Weekday | bar: Hour 1 to Hour 24
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
| Building | ExtLightingMotionCtrl | PNNL Hospital Prototype (2022) Modified to 0 for 11 pm to 5 am during weekday and 12 am to 5 am during weekend | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Office, Exam Room,Nurse Station, Recovery Room,Operating Room. Patient Room,Physical Therapy, Imaging Room, Medical Supply Room | Building | FunctionalAreaPeopleActivityLevel | CEC Hospital Prototype | Weekday | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
|  |  |  | Saturday | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
|  |  |  | Sunday | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
Corridor, Lobby, Restroom, Mechanical Room, Elevator, Stairwell, Reception rea, Lounge and Breakroom | Building | CommonAreaPeopleActivityLevel | CEC Hospital Prototype | Weekday | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5
|  |  |  | Saturday | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5
|  |  |  | Sunday | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5
Dining | Building | DiningAreaPeopleActivityLevel | CEC Hospital Prototype | Weekday | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2
|  |  |  | Saturday | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2
|  |  |  | Sunday | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2
Kitchen | Building | KitchenPeopleActivityLevel | CEC Hospital Prototype | Weekday | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8
|  |  |  | Saturday | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8
|  |  |  | Sunday | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8
Locker room | Building | LockerRoomPeopleActivityLevel | CEC Hospital Prototype | Weekday | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9
|  |  |  | Saturday | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9
|  |  |  | Sunday | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9
Health OR |  | Other
All the zones | Health | Occupancy | T24 2022 - Appendix 5.4B, [Health] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
All the zones | Health | Lights | T24 2022 - Appendix 5.4B, [Health] | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.45 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1
|  |  |  | Saturday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
All the zones | Health | ElecEquipment | T24 2022 - Appendix 5.4B, [Health] | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1
|  |  |  | Saturday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
All the zones | Health | ServiceHotWater | T24 2022 - Appendix 5.4B, [Health] | Weekday | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.17 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.18 | 0.18 | 0.18 | 0.1 | 0.01 | 0.01
|  |  |  | Saturday | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.2 | 0.28 | 0.3 | 0.3 | 0.24 | 0.24 | 0.23 | 0.23 | 0.23 | 0.1 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
|  |  |  | Sunday | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
All the zones | Health | GasEquipment | T24 2022 - Appendix 5.4B, [Health] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.75 | 0.2 | 0.1 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
All the zones | Health | Refrigeration | T24 2022 - Appendix 5.4B, [Health] | Weekday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Saturday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Sunday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
Perimeter zones under Health category | Health | Infiltration | T24 2022 - Appendix 5.4B, [Health] | Weekday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1
|  |  |  | Saturday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1
|  |  |  | Sunday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
All the zones | Health | HVACAvail | T24 2022 - Appendix 5.4B, [Health] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
All the zones | Health | HtgSetpt |  | Weekday | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68
|  |  |  | Saturday | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68
|  |  |  | Sunday | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68
All the zones | Health | ClgSetpt |  | Weekday | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68
|  |  |  | Saturday | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68
|  |  |  | Sunday | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68

## Energy Usage (hidden)
CalBEM Energy Consumption - Outpatient | [11 empty] | Energy Consumption - Outpatient
Prototype | CZ | CalBEM Electricity EUI (KBTU/ft²) | CalBEM Gas EUI (KBTU/ft²) | CalBEM Total EUI (KBTU/ft²) | New Construction Electricity EUI (KBTU/ft²) | New Construction Gas EUI (KBTU/ft²) | New Construction Total EUI (KBTU/ft²) | National Average | Acceptable Range (25% Higher) | Acceptable Range (25% Lower) | National Average Acceptable EUI Range | Prototype | CZ | Total Floorspace (Thousand of ft²) | CEUS 2023 Electricity EUI (kBtu/ft²) | CEUS 2023 Gas EUI (kBtu/ft²) | CEUS 2023 Total EUI (kBtu/ft²) | Acceptable Range (25% Higher) | Acceptable Range (25% Lower) | CEUS 2022 Acceptable EUI Range
Outpatient | 1 | [6 empty] | 108 | 135 | 81 | 54 | Outpatient | 1 | 7059 | 70.9802 | 51.1577 | 122.1379 | 152.6724 | 91.6034 | 61.069
| 2 | [6 empty] | 106.4 | 133 | 79.8 | 53.2 |  | 2 | 14514 | 45.6312 | 53.4755 | 99.1067 | 123.8834 | 74.33 | 49.5533
| 3 | [6 empty] | 104.6 | 130.75 | 78.45 | 52.3 |  | 3 | 56689 | 53.4877 | 48.1605 | 101.6482 | 127.0603 | 76.2362 | 50.8241
| 4 | [6 empty] | 111.8 | 139.75 | 83.85 | 55.9 |  | 4 | 29372 | 54.7559 | 50.1593 | 104.9152 | 131.1441 | 78.6864 | 52.4576
| 5 | [6 empty] | 103.8 | 129.75 | 77.85 | 51.9 |  | 5 | 5067 | 39.8282 | 24.8165 | 64.6447 | 80.8058 | 48.4835 | 32.3223
| 6 | [6 empty] | 107.3 | 134.125 | 80.475 | 53.65 |  | 6 | 32891 | 54.9321 | 75.4764 | 130.4085 | 163.0106 | 97.8064 | 65.2042
| 7 | [6 empty] | 108.5 | 135.625 | 81.375 | 54.25 |  | 7 | 31754 | 74.8437 | 45.4861 | 120.3298 | 150.4123 | 90.2474 | 60.1649
| 8 | [6 empty] | 113.6 | 142 | 85.2 | 56.8 |  | 8 | 50355 | 56.5439 | 86.9115 | 143.4554 | 179.3193 | 107.5916 | 71.7277
| 9 | [6 empty] | 113.1 | 141.375 | 84.825 | 56.55 |  | 9 | 72118 | 45.2257 | 63.3727 | 108.5983 | 135.7479 | 81.4488 | 54.2992
| 10 | [6 empty] | 110.1 | 137.625 | 82.575 | 55.05 |  | 10 | 55175 | 66.7723 | 63.834 | 130.6063 | 163.2578 | 97.9547 | 65.3031
| 11 | [6 empty] | 119.3 | 149.125 | 89.475 | 59.65 |  | 11 | 20961 | 67.7136 | 42.2205 | 109.9341 | 137.4176 | 82.4506 | 54.967
| 12 | [6 empty] | 115.6 | 144.5 | 86.7 | 57.8 |  | 12 | 93863 | 69.3375 | 42.635 | 111.9726 | 139.9657 | 83.9794 | 55.9863
| 13 | [6 empty] | 121.5 | 151.875 | 91.125 | 60.75 |  | 13 | 30306 | 75.5934 | 48.3022 | 123.8956 | 154.8695 | 92.9217 | 61.9478
| 14 | [6 empty] | 119.9 | 149.875 | 89.925 | 59.95 |  | 14 | 13400 | 63.1769 | 77.509 | 140.6859 | 175.8574 | 105.5144 | 70.3429
| 15 | [6 empty] | 137.9 | 172.375 | 103.425 | 68.95 |  | 15 | 24206 | 61.2178 | 63.6567 | 124.8745 | 156.0932 | 93.6559 | 62.4373
| 16 | [6 empty] | 113.1 | 141.375 | 84.825 | 56.55 |  | 16 | 57915 | 72.2681 | 64.3832 | 136.6513 | 170.8142 | 102.4885 | 68.3257
Ref: CEUS 2022 Report
And converted FZ level data to CZ level
CEUS has only one category for healthcare.
Background Data [To be deleted prior to publication]

## Weights (hidden)
% of Floor Area per CZ and Vintage Bin - Outpatient | [7 empty] | % of Floor Area per CZ and Vintage Bin - Outpatient
Prototype | CZ | Vintage Bin | [5 empty] | Prototype | Vintage Bin | CZ
|  | Pre-1978 | 1978-1997 | 1998-2007 | 2008-2018 | Not available |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
Outpatient | 1 | [5 empty] | 0% | Outpatient | Pre-1978 | [16 empty] | 0%
| 2 | [5 empty] | 0% |  | 1978-1997 | [16 empty] | 0%
| 3 | [5 empty] | 0% |  | 1998-2007 | [16 empty] | 0%
| 4 | [5 empty] | 0% |  | 2008-2018 | [16 empty] | 0%
| 5 | [5 empty] | 0% |  | Not available | [16 empty] | 0%
| 6 | [5 empty] | 0% |  | Total
| 7 | [5 empty] | 0%
| 8 | [5 empty] | 0%
| 9 | [5 empty] | 0%
| 10 | [5 empty] | 0%
| 11 | [5 empty] | 0%
| 12 | [5 empty] | 0%
| 13 | [5 empty] | 0%
| 14 | [5 empty] | 0%
| 15 | [5 empty] | 0%
| 16 | [5 empty] | 0%
Statewide
Ref: CEUS 2022 dataset
And converted FZ level data to CZ level
CEUS has only one category for healthcare.
Background Data [To be deleted prior to publication]

## PV (hidden)
PV - Outpatient
TBD

## EV Charger (hidden)
EV Charger - Outpatient
TBD
Background Data [To be deleted prior to publication]

## Data (hidden)
Space Function | Electric Equipment Load Intensity | Electric Equipment Load Intensity | LPD
Aging Eye/Low-vision (Corridor Area) |  |  | 2013 | 2016 | 2019 | 2025
Aging Eye/Low-vision (Dining)
Aging Eye/Low-vision (Lobby, Main Entry)
Aging Eye/Low-vision (Lounge/Waiting Area)
Aging Eye/Low-vision (Multipurpose Room)
Aging Eye/Low-vision (Religious Worship Area)
Aging Eye/Low-vision (Restroom)
Aging Eye/Low-vision (Stairwell)
Audience Seating Area
Auditorium Area
Auto Repair / Maintenance Area
Barber, Beauty Salon, Spa Area
Civic Meeting Place Area
Classroom, Lecture, Training, Vocational Areas
Concourse and Atria Area
Convention, Conference, Multipurpose and Meeting Area
Copy Room
Corridor Area
Dining Area (Bar/Lounge and Fine Dining)
Dining Area (Cafeteria/Fast Food)
Dining Area (Family and Leisure)
Electrical, Mechanical, Telephone Rooms
Exercise/Fitness Center and Gymnasium Areas
Financial Transaction Area
Healthcare Facility and Hospitals (Exam/Treatment Room)
Healthcare Facility and Hospitals (Imaging Room)
Healthcare Facility and Hospitals (Medical Supply Room)
Healthcare Facility and Hospitals (Nursery)
Healthcare Facility and Hospitals (Nurse's Station)
Healthcare Facility and Hospitals (Operating Room)
Healthcare Facility and Hospitals (Patient Room)
Healthcare Facility and Hospitals (Physical Therapy Room)
Healthcare Facility and Hospitals (Recovery Room)
Hotel Function Area
Kitchen/Food Preparation Area
Kitchenette or Residential Kitchen
Laboratory, Scientific
Laundry Area
Library (Reading Area)
Library (Stacks Area)
Lobby, Main Entry
Locker Room
Lounge, Breakroom, or Waiting Area
Manufacturing, Commercial & Industrial Work Area (Low Bay)
Manufacturing, Commercial & Industrial Work Area (High Bay)
Manufacturing, Commercial & Industrial Work Area (Precision)
Museum Area (Exhibition/Display)
Museum Area (Restoration Room)
Office Area (>250 square feet)
Office Area (<250 square feet)
Parking Garage Area (Parking Zone and Ramps)
Parking Garage Area (Daylight Adaptation Zones)
Pharmacy Area
Retail Sales Area (Grocery Sales)
Retail Sales Area (Retail Merchandise Sales)
Retail Sales Area (Fitting Room)
Religious Worship Area
Restrooms
Stairwell
Storage, Commercial/Industrial (Warehouse)
Storage, Commercial/Industrial (Refrigerated)
Storage, Commercial/Industrial (Shipping & Handling)
Storage (General)
Sports Arena - Playing Area (> 5,000 Spectators)
Sports Arena - Playing Area (2,000 - 5,000 Spectators)
Sports Arena - Playing Area (< 2,000 Spectators)
Sports Arena - Playing Area (Recreational)
Theater Area (Motion Picture)
Theater Area (Performance)
Transportation Function (Baggage Area)
Transportation Function (Ticketing Area)
Videoconferencing Studio
High-Rise Residential Living Spaces
Hotel/Motel Guest Room
All other
Attic
Reception area
Elevator
Plenum
IT Room (EPD 12)
Computer Room (EPD 20)
Server Room (EPD 45)