## Notes
Data Sources
Dataset | Dodge 2023
| Commercial End-Use Survey (CEUS) 2022 | https://www.energy.ca.gov/publications/2023/2022-california-commercial-end-use-survey-ceus-final-report
| Commercial Buildings Energy Consumption Survey (CBECS) 2018 | https://www.eia.gov/consumption/commercial/data/2018/index.php?view=microdata
| Comstock 2023 | https://data.openei.org/s3_viewer?bucket=oedi-data-lake&prefix=nrel-pds-building-stock%2Fend-use-load-profiles-for-us-building-stock%2F2023%2Fcomstock_amy2018_release_2%2Fmetadata_and_annual_results%2Fby_state%2Fstate%3DCA%2F
Prototypes | California Energy Commission (CEC) Medium Retail prototype (CBECC 2022.3.1) | https://bees.noresco.com/software2022.html
| Pacific Northwest National Laboratory (PNNL) Strip Mall Retail prototypes (90.1-2022) | https://www.energycodes.gov/prototype-building-models#Commercial
| Database for Energy Efficient Resources (DEER) Retail prototypes (June 2023) | https://github.com/sound-data/DEER-Prototypes-EnergyPlus
Codes | Title 24, part 6, referred to as T24 (1984, 1992,1998, 2001, 2005, 2008, 2013, 2016,2019, 2022, 2025) | https://www.energy.ca.gov/publications/2025/2025-building-energy-efficiency-standards-residential-and-nonresidential | 2025
|  | https://codes.iccsafe.org/codes/united-states/california | 2010+
| American Society of Heating, Refrigerating and Air-Conditioning Engineers (ASHRAE) 90.1 (2022) | https://www.ashrae.org/technical-resources/standards-and-guidelines/read-only-versions-of-ashrae-standards
| Code of Federal Regulations (CFR) Title 10 ( 2010) | https://www.govinfo.gov/content/pkg/FR-2009-03-23/pdf/FR-2009-03-23.pdf
| CFR Title 10 ( 2024) | https://www.govinfo.gov/content/pkg/CFR-2024-title10-vol3/pdf/CFR-2024-title10-vol3-part431-subpartF.pdf
Others | Alternative Calculation Method (ACM) (2022) | https://www.energy.ca.gov/publications/2022/2022-nonresidential-and-multifamily-alternative-calculation-method-reference
| ACM (2025) | https://www.energy.ca.gov/publications/2025/2025-nonresidential-and-multifamily-alternative-calculation-method-reference
| Nonres ACM 2022, Appendix 5.4A and Appendix 5.4B | https://www.energy.ca.gov/publications/2022/2022-nonresidential-and-multifamily-alternative-calculation-method-reference
| 2022 Reduced infiltration Codes and Standards Enhancement (CASE) report | https://title24stakeholders.com/wp-content/uploads/2020/10/2022-T24-Final-CASE-Report_Reduce-Infiltration.pdf
| 2019 Outdoor Lighting CASE Report | https://title24stakeholders.com/wp-content/uploads/2016/10/T24-2019-CASE-Study-Results-Report-Outdoor-Sources_Final_with-Attachments.pdf
| PNNL 20405, 2011 | https://www.pnnl.gov/main/publications/external/technical_reports/PNNL-20405.pdf
| Air leakage Memo, NORESCO, 2025 | Infiltration_rate_report_14May2025-Short-Version.docx
| Yousefi, F., Athalye, R., (2025), "Determining Vintage Bins for Prototype Development: An Analysis of California Commercial Buildings," ASHRAE Annual Conference | https://www.thefreelibrary.com/Determining+Vintage+Bins+for+Prototype+Development%3a+An+Analysis+of...-a0879271125
| Proposed Updates to Equipment Power Densities and Building Schedules for the 2028 Energy Code, referred to as "Plug load and schedules project with CEC, 2025" (Docket Number =25-BSTD-03 & TN=265693) | https://efiling.energy.ca.gov/GetDocument.aspx?tn=265693&DocumentContentId=102545
| ENERGY STAR certified commercial water heaters | https://www.energystar.gov/productfinder/product/certified-commercial-water-heaters/results?fuel_filter=Gas&markets_filter=United+States
| Grainger gas tank water heaters (sizes below commercial, e.g. 30–75 kBtu/h) | https://www.grainger.com/category/plumbing/water-heaters/gas-tank-water-heaters
| Grainger electric tank water heaters | https://www.grainger.com/category/plumbing/water-heaters/electric-tank-water-heaters
Notes
This prototype represents a partitioned strip mall typology for retail up to approximately 100,000 ft².

## Prototype
NORESCO, Updated September 2026
RetailStripMall
Characteristic | Value | Data Sources
Building Type | Small Retail
Building Category | Nonresidential
Version | v2-0
Vintages | 4 Vintages: Pre-1978 , 1978-1997 ,1998-2007 , 2008-2018 New Construction (2019+) | Based on the vintage bin analysis. A summary of the findings is presented in the following paper, with a link provided in the Notes tab: Yousefi, F., Athalye, R. (2025). “Determining Vintage Bins for Prototype Development: An Analysis of California Commercial Buildings.” ASHRAE Annual Conference.
Shape |  | Geometry of CBECC Retail Strip Mall prototype was adapted
Total Floor Area (ft²) | 9,375 (125 ft x 75 ft) | Geometry of CBECC Retail Strip Mall prototype was adapted
Aspect Ratio | 1.67 overall (0.33 for small store & 0.67 for large store) | Geometry of CBECC Retail Strip Mall prototype was adapted
Number of Floors | 1
Roof type | Roof membrane+Roof insulation+metal decking
WWR | 8.24% | Geometry of CBECC Retail Strip Mall prototype was adapted
Shading Geometry | none
Floor to floor height (feet) | N/A
Floor to ceiling height (feet) | 17 | Geometry of CBECC Retail Strip Mall prototype was adapted
Glazing sill height (feet) | 3.0 ft (top of the window is 8 ft high) | Geometry of CBECC Retail Strip Mall prototype was adapted
Existing Retail Prototypes
| CEC: Retail_Large | CPUC: Retail_Multistory Large (Rt3) | CPUC: Retail_Single-Story Large (RtL)
Large size prototype
Total floor area (ft²) | 240000 | 120000 | 130502
| CEC: Retail_Medium | PNNL : Retail_Stand alone | PNNL: Retail_Stripmall | CPUC: Retail_Grocery
Medium size prototype | zoning same as PNNL Stand alone with more skylight
Total floor area (ft²) | 24692 | 24692 | 22500 | 49997
| CEC: Retail_Stripmall (Mixed use) | CPUC: Retail_Small (RtS)
Small size prototype
Total floor area (ft²) | 9375 | 8001

## Zones
Proposed Layout - RetailStripMall
Building | Space/Thermal Zone | Space Type [Primarily from: T24, 2022 Appendix 5.4A] - See Notes column | Building | HVAC System Name (NC) | HVAC System Name (Existing) | Schedule Category | Conditioned (Y/N) | Area Fraction | Area (ft²) | Volume (ft³) | Multipliers | Number of People | People (Persons/1,000 ft²) [T24, 2025,Table 120.1-A] | Notes | Spaces and Zoning layout
RetailStripMall | LG_Store_1 | Retail Sales Area (Retail Merchandise Sales) | RetailStripMall | SZVAVHP_LG_Store | SZAC_LG_Store | Retail | Y | 40% | 3750.0386 | 63750.0423 | 1 | 63.7507 | 17
RetailStripMall | SM_Store_1 | Retail Sales Area (Retail Merchandise Sales) | RetailStripMall | SZVAVHP_SM_Store1 | SZAC_SM_Store1 | Retail | Y | 20% | 1874.9655 | 31875.0211 | 1 | 31.8744 | 17
RetailStripMall | SM_Store_2 | Retail Sales Area (Retail Merchandise Sales) | RetailStripMall | SZVAVHP_SM_Store2 | SZAC_SM_Store2 | Retail | Y | 20% | 1874.9655 | 31875.0211 | 1 | 31.8744 | 17
RetailStripMall | SM_Store_3 | Retail Sales Area (Retail Merchandise Sales) | RetailStripMall | SZVAVHP_SM_Store3 | SZAC_SM_Store3 | Retail | Y | 20% | 1874.9655 | 31875.0211 | 1 | 31.8744 | 17
Total (1 Building) | Total (4 Space)s | Total (1 Space type) | Total (1 Building) | Total (4 HVAC systems) | Total (4 HVAC systems) | Total (1 Schedule category) | Total (4 Conditioned zones) | 100% | 9374.9351 | 159375.1057 |  | 159.3739
Plan from CBECC 2022, Retail_Stripmall prototype
Background Data [To be deleted prior to publication]
Floorspace-Types-30Oct2024
Retail (CEUS 2022, statewide %)
| Conditioned | Unconditioned |  |  | Ventilated
| 82.62% | 17.37% |  |  | 0.8344
Likely storage in larger Retail (see Medium/Standalone)
N

## Envelope
Envelope - RetailStripMall
Element | Prototype | Assembly Type | Construction | Thermal Properties | Vintage | Selected T24 | Note | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
External Wall | RetailStripmall | ExtWall_MetalFramed_NonRes | Metal framed wall: Metal-frame walls + insulation + Gypsum board | U-factor IP | Pre 1978 | N/A | ASHRAE 90.1, 2022, Table A3.3.3.1, 3.5", R-0 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352
[5 empty] | 1978-1997 | 1986 | Heat Capacity was considered 10.0-14.99 (Btu/F-ft²) | 0.15083 | 0.15748 | 0.15748 | 0.14368 | 0.14368 | 0.21645 | 0.21645 | 0.21645 | 0.21645 | 0.21645 | 0.18622 | 0.18622 | 0.18622 | 0.15873 | 0.15873 | 0.15083
[5 empty] | 1998-2007 | 2001 | TABLE 1-H-NonRes Bldgs | 0.182 | 0.182 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182
[5 empty] | 2008-2018 | 2013 | TABLE 140.3-B-NonRes Bldgs | 0.098 | 0.062 | 0.082 | 0.062 | 0.062 | 0.098 | 0.098 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062
[5 empty] | 2019+ | 2025 | TABLE 140.3-B-NonRes Bldgs | 0.06 | 0.055 | 0.071 | 0.055 | 0.055 | 0.06 | 0.06 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055
Roof | RetailStripmall | FlatRoof_WoodFramedAndOther_NonRes | Metal deck roof: Roof membrane+roof insulation+metal decking | U-factor IP | Pre 1978 | N/A | Considering 30 years for roof/ insulation replacement. | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 1978-1997 | 1992 |  | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 1998-2007 | 2001 | Table 1-H | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.049 | 0.039 | 0.039 | 0.039 | 0.049 | 0.075 | 0.067 | 0.067 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.047 | 0.047 | 0.047 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028
Windows | RetailStripmall | FixedWindow_NonRes | CBECS 2018 shows that ~ 50 % of retail that were built before 2000 are single pane | U-factor IP | Pre 1978 | N/A | 2021 ASHRAE Handbook of Fundamentals - Section 15.9 Table 4 for single pane & T24, 2013 Table 140.3-B for double pane (50%-50%) | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74
[5 empty] | 1978-1997 | N/A |  | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74
|  |  | Double pane |  | 1998-2007 | 2001 | Table 1-H | 0.49 | 0.49 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.34 | 0.36 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.36
| RetailStripmall | FixedWindow_NonRes | CBECS 2018 shows that ~ 50 % of retail that were built before 2000 are single pane | SHGC | Pre 1978 | N/A | 2021 ASHRAE Handbook of Fundamentals - Section 15.22 Table 10 for single pane & T24, 2013 Table 140.3-B for double pane (50%-50%) | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52
[5 empty] | 1978-1997 | N/A |  | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52
|  |  | Double pane |  | 1998-2007 | 2001 | Table 1-H (Non north 0-10%) | 0.49 | 0.47 | 0.61 | 0.61 | 0.61 | 0.61 | 0.61 | 0.61 | 0.61 | 0.47 | 0.47 | 0.47 | 0.47 | 0.46 | 0.46 | 0.49
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.22 | 0.25 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.25
Infiltration
|  |  | Building | Zones | Vintage | I_75 (cfm/ft²) 6-sdied Infiltration rate @ 75 pa | Note | I-design (cfm/ft²) (4-sided Infiltration rate at normal pressure) (Design flow rate approach and Flow/Exterior Wall Area calculation method)
|  | Infiltration | RetailStripMall |  | Pre 1978 | 1.1 | 2022 CASE report (Table 38) | #REF! | [15 empty] | Floor or roof area (ft2) | 9374.9351
[5 empty] | 1978-1997 | 1.1 | 2022 CASE report (Table 38) | #REF! | [15 empty] | Walls area (ft2) | 6800
[5 empty] | 1998-2007 | 1.1 | 2022 CASE report (Table 38) | #REF! | [15 empty] | Building 4 sided area (ft2) | 6800
[5 empty] | 2008-2018 | 1 | 2022 CASE report (Table 38) & T24, 2008-2016 (TABLE 140.3-B) | #REF! | [15 empty] | Building 6 sided area (ft2) | 25549.8701
[5 empty] | 2019+ | 0.6 (barrier in all CZ) | 2022 CASE report (Table 38) & T24, 2025 (TABLE 140.3-B) | #REF!
Source: Title 24 air barrier requirements (all editions) and the standardized infiltration rate reported in the 2022 CASE report and Dodge 2023 data
|  |  |  | Air Leakage Memo: |  | Infiltration_rate_report_14May2025-Short-Version.docx

## HVAC System
HVAC system - RetailStripMall
Vintage | Heating | Cooling | Air Distribution | Other systems | Source
Existing | PSZAC (furnace) | PSZAC (DX cooling) | PSZAC | OA mixing Economizer for Vintage 3 and 4 | CEUS 2022
New Construction | SZVAVHP | SZVAVHP | PSZVAVHP | OA mixing Economizer | Title 24, 2025, Engineering judgement
Efficiency of HVAC System (Efficiency is capacity-dependent. The following table provides a general estimate of system efficiency based on preliminary simulations in one climate zone, or assuming cooling load based on rule of thumb)
Vintage | Upgrade year | Heating | Cooling | Source
Pre 1978 | 2008 | Thermal Efficiency of 80% | SEER=13.0 for <65 kBtu/h EER 10.1 for 65-135 kBtu/h EER 9.5 for 135-240 kBtu/h EER 9.3 for 240-760 kBtu/h | T24, Table 112-A (2008) 10 CFR § 431.97, Table 1 (2008) California Title 20 Appliance Efficiency Regulations, Table E-4, Standards for Gas- and Oil-Fired Central Furnaces (2008)
1978-1997
1998-2007
2008-2018 | 2013 | Thermal Efficiency of 80%; | SEER 13 for <65 kBtu/h EER 11.0 for 65-135 kBtu/h EER 10.8 for 135-240 kBtu/h EER 9.8 for 240-760 kBtu/h | T24 Tables 110.2-A, 110.2-J (2013) 10 CFR, § 431.97, Table 1 (2013)
New Construction | 2025 | HSPF 8.0 for <65 kBtu/h COP 3.4 for 65-135 kBtu/h COP 3.3 for 135-240 kBtu/h COP 3.2 for >240 kBtu/h | SEER 14 for <65 kBtu/h EER 10.8, IEER 13.9 for 65-135 kBtu/h EER 10.4, IEER = 13.3 135-240 kBtu/h EER 9.3, IEER=12.3 for >240 kBtu/h | 10 CFR § 431.97(b) Table 1 (2025) Title 20 Appliance Efficiency Regulations, Section 1605.1, Table C-5 (2025) T24, Table 110.2-B (2025)
Fan Power
Vintage | Approach | System | Total Static Pressure (TSP) (in w.c.) | Fan Efficiency [ACM 2025] | Motor Efficiency | Fan Power Index (W/cfm) | Data Source | Note
Existing | PNNL 90.1-2011, TSP | CAV < 7,437 cfm | 2.5 | 0.65 | ASHRAE 90.1, 2004, Table 10.8 * |  | Fan power formula: PNNL 20405, 2010, section 5.2.2.5 TSP and fan efficiecncy: PNNL 20405, 2010, Table 5.11, 90.1-04ac values Motor and drive efficiency: ASHRAE 90.1, 2004, Table 10.8
|  | CAV >= 7,437 cfm | 4.09
Brake horsepower (bhp) = (Supply cfm × TSP in w.c.) / (6356 × fan efficiency)
Fan power (w/cfm) = (bhp × 746) / ( supply cfm × motor efficiency )
New Construction | ACM 2025 | SZVAVHP (System 7b), tenant unit ≤5,000 cfm | TSP = fan power × motor efficiency × fan efficiency × 6356 / 746 | 0.65 | 2025 ACM Table 12 ** | 0.744 | Fan power index: [ACM 2025, Table 13] Motor efficiency: [ACM 2025, Table 12]
|  | SZVAVHP (System 7b), >5,000 and ≤10,000 cfm | TSP = fan power × motor efficiency × fan efficiency × 6356 / 746 |  |  | 0.72
* According to PNNL 20405 section 5.2.2.5, the full-load efficiency of the motor serving the fan is taken from ASHRAE 90.1, 2004, Table 10.8, based on motor nameplate and assuming enclosed motors operating at 1,800 rotations per minute (rpm) Motor nameplate size (bhp) = brake horsepower (bhp) × 1.1 ( using a 10% oversizing factor)
** The full‑load efficiency of the motor serving the fan is taken from ACM 2025 Table 12 based on the cfm of the fan. Brake horsepower (bhp) = (Supply cfm from sizing run × fan power in W/cfm) / 746. Note: Strip-mall packaged SZVAVHP. ACM System 7b ≤5,000 cfm. Note: ACM System 7b mid bin, if a tenant unit is above 5,000 cfm.
Background Data [To be deleted prior to publication]
〖𝐹𝑎𝑛 𝑝𝑜𝑤𝑒𝑟〗_(𝑤/𝑐𝑓𝑚)=(〖𝑇𝑆𝑃〗_(𝑖𝑛 𝑤.𝑐)∗746)/(6356∗𝜇_𝑓𝑎𝑛∗𝜇_𝑚𝑜𝑡𝑜𝑟 )
𝑏ℎ𝑝=(𝑐𝑓𝑚∗〖𝑇𝑆𝑃〗_(𝑖𝑛 𝑤.𝑐.))/〖6356∗𝜇〗_𝑓𝑎𝑛
〖𝐹𝑎𝑛 𝑝𝑜𝑤𝑒𝑟〗_(𝑤/𝑐𝑓𝑚)=(𝑏ℎ𝑝∗746)/(𝑐𝑓𝑚∗𝜇_𝑚𝑜𝑡𝑜𝑟 )
𝑏ℎ𝑝=(〖𝐹𝑎𝑛 𝑝𝑜𝑤𝑒𝑟〗_(𝑤/𝑐𝑓𝑚)∗𝑐𝑓𝑚∗𝜇_𝑚𝑜𝑡𝑜𝑟)/746

## Ventilation
Outdoor Airflow Rate - RetailStripMall
Space/Thermal Zone | Number of People | Floor Area (ft²) | cfm/person [T24, 2025, Equation 120.1-F and Table 120.1-A] | cfm/ft² [T24, 2025, Equation 120.1-F and Table 120.1-A] | Required Exhaust Rate [T24, 2025, Table 120.1-B – minimum exhaust rates] | Total cfm Driven by People | Total cfm Driven by Area | Total cfm Driven by Exhaust | Total cfm | Notes
LG_Store_1 | 63.7507 | 3750.0386 | 15 | 0.2 | 2* 25/50 per unit | 956.2598 | 750.0077 | 50 | 956.2598 | Although the restroom is not simulated as a separate zone, its exhaust rate and fan load are included in the model.
SM_Store_1 | 31.8744 | 1874.9655 | 15 | 0.2 |  | 478.1162 | 374.9931 | 0 | 478.1162
SM_Store_2 | 31.8744 | 1874.9655 | 15 | 0.2 |  | 478.1162 | 374.9931 | 0 | 478.1162
SM_Store_3 | 31.8744 | 1874.9655 | 15 | 0.2 |  | 478.1162 | 374.9931 | 0 | 478.1162
2390.6084
Background Data [To be deleted prior to publication]

## Thermostat
Thermostat Setpoints - RetailStripMall
Setpoint | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16 | Source
Heating Setpoint (F) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | T24 2022 - Appendix 5.4B
Heating Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Cooling Setpoint (F) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
Cooling Setback (F) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85

## Water Heater
Water Heater - RetailStripMall
Vintage | WH Type | Efficiency | Number of WH | Tank Volume (gal) | Tank Loss | Source
Existing | Electric | 1 | 1 | See table below for CZ-specific values: Climate Zone Water Heater Sizing and Loss Coefficients, Storage Volume column (col F) | See table below: Climate Zone Water Heater Sizing and Loss Coefficients, Standby Loss column (col G) | See table below for sources: Climate Zone Water Heater Sizing and Loss Coefficients
New Construction | Electric | 1 | 1 | See table below for CZ-specific values: Climate Zone Water Heater Sizing and Loss Coefficients, Storage Volume column (col F) | See table below: Climate Zone Water Heater Sizing and Loss Coefficients, Standby Loss column (col G) | See table below for sources: Climate Zone Water Heater Sizing and Loss Coefficients
Peak Hot Water Consumption
Space Name | Baseline WH Type [CEUS 2022] | Total Area (ft²) | Number of People | Hot Water Usage Specification (gal/hr per person) [T24, 2022, Appendix 5.4A , sheet: "2022 SpaceFuncData-Input"] | Peak Hot Water Usage (gal/hr) | Peak Hot Water Usage (gal/min) | Note
LG_Store_1 | Electric | 3750.0386 | 63.7507 | 0.18 | 11.4751 | 0.19125 | For space types marked with an asterisk (the ‘*’ symbol), the water‑heater type is listed as electric in Appendix 5.4A, sheet ‘2022 SpaceFuncData‑Input.’ However, we modified the value based on CEUS data, which indicates that gas is the primary fuel type.
SM_Store_1 | Electric | 1874.9655 | 31.8744 | 0.18 | 5.7374 | 0.095623
SM_Store_2 | Electric | 1874.9655 | 31.8744 | 0.18 | 5.7374 | 0.095623
SM_Store_3 | Electric | 1874.9655 | 31.8744 | 0.18 | 5.7374 | 0.095623
Total | Gas storage |  |  |  | 0 |  | Minimum peak hot water usage is 75 gal according to ACM 2025
Total | Electric resistance |  |  |  | 75
Design supply temperature (°F) | 135 | CEC-400-2022-009-CMF-REV2-AP5.4B
WH system factor | 0.6 | 2025 ACM §5.9.2 Rated Capacity
Water mass conversion (lb/gal) | 8.2877 | 2025 ACM §5.9.2 Rated Capacity
Reheat multiplier | 0.4 | 2025 ACM §5.9.2 Storage Volume
Climate Zone Water Heater Sizing and Loss Coefficients (Individual WH)
Climate Zone | Minimum Monthly Mains Temp (°F) [T24 2022 - Appendix 5.4B] | Heat Output (Btu/hr) [ACM, 2025, 5.9.2: Rated capacity section] | WH Capacity (Btu/hr) [ACM, 2025, 5.9.2: Rated capacity section] | Required Energy Input (Btu/hr) | Storage Volume (gal) | Standby Loss [Title 20, §1605.1 Table F-4; Appendix B: Water Heating Calculation Method] |  | Off/On Cycle Loss Coefficient to Ambient Temp |  | Source/Note
CZ01 | 47.9 | 54139.4002 | 32483.6401 | 34121 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F | Required Energy Input: vendor/available catalog size (Market data table). Storage Volume: standard/available catalog tank size (Market data table).
CZ02 | 50.8 | 52336.8255 | 31402.0953 | 34121 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F
CZ03 | 52.2 | 51466.617 | 30879.9702 | 34121 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F
CZ04 | 52.7 | 51155.8282 | 30693.4969 | 30709 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F
CZ05 | 51.6 | 51839.5635 | 31103.7381 | 34121 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F
CZ06 | 56.8 | 48607.3605 | 29164.4163 | 30709 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F
CZ07 | 58.4 | 47612.8365 | 28567.7019 | 30709 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F
CZ08 | 58.4 | 47612.8365 | 28567.7019 | 30709 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F
CZ09 | 57.6 | 48110.0985 | 28866.0591 | 30709 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F
CZ10 | 57.1 | 48420.8872 | 29052.5323 | 30709 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F
CZ11 | 50.5 | 52523.2987 | 31513.9792 | 34121 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F
CZ12 | 51.4 | 51963.879 | 31178.3274 | 34121 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F
CZ13 | 51.7 | 51777.4057 | 31066.4434 | 34121 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F
CZ14 | 50.1 | 52771.9297 | 31663.1578 | 34121 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F
CZ15 | 63.2 | 44629.2645 | 26777.5587 | 27297 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F
CZ16 | 41.4 | 58179.654 | 34907.7924 | 40946 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F
Market data
Catalog gas input (Btu/h) | Input source | Elec resistance tank (kW) | Elec resistance (Btu/h) | Catalog gas tank (gal) | Tank source | Elec tank (gal) | Elec tank source | Sources and links → Note tab
60000 | Grainger | 1.5 | 5118 | 34 | ENERGY STAR | 6 | Grainger
75100 | Grainger | 2 | 6824 | 35 | Grainger | 10 | Grainger
76000 | Both | 3 | 10236 | 48 | Grainger | 15 | Grainger
80000 | Grainger | 4.5 | 15355 | 50 | Both | 20 | Grainger
99900 | ENERGY STAR | 6 | 20473 | 55 | ENERGY STAR | 28 | Grainger
100000 | Both | 8 | 27297 | 60 | ENERGY STAR | 30 | Grainger
120000 | ENERGY STAR | 9 | 30709 | 65 | Both | 36 | Grainger
125000 | Both | 10 | 34121 | 72 | Grainger | 40 | Grainger
130000 | Both | 12 | 40946 | 75 | Both | 47
145000 | ENERGY STAR | 12.1 | 41287 | 76 | Grainger | 50
150000 | ENERGY STAR | 18 | 61419 | 80 | Both | 65
156000 | Grainger | 24 | 81891 | 82 | Grainger | 80
160000 | Both | 27 | 92128 | 85 | Grainger | 85
175000 | ENERGY STAR | 36 | 122837 | 90 | Both | 105
180000 | Grainger | 54 | 184256 | 91 | Grainger | 120
199000 | ENERGY STAR |  |  | 100 | Both
199900 | Both |  |  | 110 | ENERGY STAR
200000 | ENERGY STAR |  |  | 119 | Both
250000 | Both |  |  | 125 | ENERGY STAR
251000 | ENERGY STAR
270000 | Grainger
285000 | ENERGY STAR
300000 | Both
320000 | ENERGY STAR
360000 | Grainger
398000 | ENERGY STAR
399000 | ENERGY STAR
399900 | Both
499900 | Grainger
550000 | Grainger
715000 | Grainger

## Interior Lights
Interior Lighting - RetailStripMall
Space Type | New Construction |  |  | Existing |  |  | Note
| LPD (W/ft²) | Additional LPD for Portable Lighting (W/ft²) | Source | LPD (W/ft²) | Additional LPD for Portable Lighting (W/ft²) | Source
Retail Sales Area (Retail Merchandise Sales) | 0.95 | 0.09 | T24, part 6, 2025, Table 140.6-C | 1.2 | 0.06 | T24, part 6, 2016, Table 140.6-C | The percentage of additional lighting depends heavily on the specific store type. As a general assumption, additional lighting is calculated for 20% of the Retail Sales Area.
Background Data [To be deleted prior to publication]

## Ext Lighting
Exterior Lighting - RetailStripMall
Motion Controlled Luminaires (W) | Non-motion Controlled Luminaires (W) | Total (W) | Source
472.9153 | 346.5625 | 819.4778 | T24, 2022
Exterior Lighting
Items (Assume LZ2) | Assumptions [2019 Outdoor Lighting CASE Report & PNNL 90.1-2010 TSD] |  | Unit | Lighting Power Allowance [T24, 2025, Table 140.7-A & 140.7-B] | Unit | Exterior lighting power (w)
IWA (Initial Wattage Allowance) |  |  |  | 200 | W | 200
Parking area | 400 ft² for every parking space [2019 Lighting CASE report, Appendix H] 1 parking space per 360 ft² of gross building area [2019 Lighting CASE report, Table 38] | 10416.5945 | (ft²) | 0.019 | (W/ft²) | 197.9153
Building Entrance | 5 building entrance | 5 | (count) | 15 | (W/ea) | 75
Hardscape Ornamental Light | 0.1 ft² per 1 ft² of gross bldg area [2019 Lighting CASE report, Table 36] *The 0.5 multiplier has not been applied, as it is assumed it will be incorporated later during the measure analysis study. | 937.4935 | (ft²) | 0.007 | (W/ft²) | 6.5625
Building façade | 0.1 W per 1 ft² of facade area Façade Area = Perimeter × 0.5 × 17' The 0.5 factor assumes that only half of the perimeter walls are lit. -Formula ia developed based on the 2019 Outdoor Lighting CASE report | 3400 | (ft²) | 0.1 | (W/ft²) | 340
Sales canopy | 0.1 ft² per ft² of gross bldg area | 0 | (ft²) | 0.47 | (W/ft²) | 0
Motion controlled Luminaires | [5 empty] | 472.9153
Non-motion-controlled Luminaires | [5 empty] | 346.5625
Total | [5 empty] | 819.4778
*Developed based on 2019 Outdoor Lighting CASE Report
Perimeter | 400
Total floor area | 9374.9351
Floors | 1
Background Data [To be deleted prior to publication]

## Equipment
Equipment - RetailStripMall
Space Type | Plug Load Power Density (W/ft²) | Refrigerator Power Density (W/ft²) | Gas Power Density (Btu/hr-ft²) | Source
Retail Sales Area (Retail Merchandise Sales) | 0.3 |  |  | Mix of sources including "High-Efficiency Retrofit Lessons for Retail from a SuperTarget" (2013) & ASHRAE 90.1 Prototype
Background Data [To be deleted prior to publication]

## Schedules
Schedules - RetailStripMall
Zone | Schedule Category | Schedule | Source | Type | Hour
[5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
All Zones | Retail | Occupancy | NLR Study "Final Optimization Report: Empowering Energy Efficiency in Existing Big-Box Retail/Grocery Stores", (2020) | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.7 | 0.8 | 0.8 | 0.6 | 0.3 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.4 | 0.6 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.8 | 0.7 | 0.6 | 0.5 | 0.3 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.3 | 0.5 | 0.7 | 0.8 | 0.8 | 0.8 | 0.8 | 0.7 | 0.7 | 0.6 | 0.5 | 0.4 | 0.2 | 0 | 0 | 0
All Zones | Retail | Lights | T24 2022 - Appendix 5.4B, [Retail] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.7 | 0.05 | 0.05
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.7 | 0.05 | 0.05
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.7 | 0.05 | 0.05
All Zones | Retail | ElecEquipment | Plug load and schedules project with CEC, 2025 | Weekday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.4 | 0.4 | 0.4
|  |  |  | Saturday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.4 | 0.4 | 0.4
|  |  |  | Sunday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.4 | 0.4 | 0.4
All Zones | Retail | HVACAvail | T24 2022 - Appendix 5.4B, [Retail] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
All Zones | Retail | ServiceHotWater | T24 2022 - Appendix 5.4B, [Retail] | Weekday | 0.04 | 0.05 | 0.05 | 0.04 | 0.04 | 0.04 | 0.04 | 0.15 | 0.23 | 0.32 | 0.41 | 0.57 | 0.62 | 0.61 | 0.5 | 0.45 | 0.46 | 0.47 | 0.42 | 0.34 | 0.33 | 0.23 | 0.13 | 0.08
|  |  |  | Saturday | 0.11 | 0.1 | 0.08 | 0.06 | 0.06 | 0.06 | 0.07 | 0.2 | 0.24 | 0.27 | 0.42 | 0.54 | 0.59 | 0.6 | 0.49 | 0.48 | 0.47 | 0.46 | 0.44 | 0.36 | 0.29 | 0.22 | 0.16 | 0.13
|  |  |  | Sunday | 0.07 | 0.07 | 0.07 | 0.06 | 0.06 | 0.06 | 0.07 | 0.1 | 0.12 | 0.14 | 0.29 | 0.31 | 0.36 | 0.36 | 0.34 | 0.35 | 0.37 | 0.34 | 0.25 | 0.27 | 0.21 | 0.16 | 0.1 | 0.06
All Zones | Retail | Infiltration | T24 2022 - Appendix 5.4B, [Retail] | Weekday | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1
|  |  |  | Saturday | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1
|  |  |  | Sunday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1
All Zones | Retail | Refrigeration | T24 2022 - Appendix 5.4B, [Retail] | Weekday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Saturday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Sunday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
All Zones | Retail | HtgSetpt | T24 2022 - Appendix 5.4B, [Retail] | Weekday | 60 | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 60 | 60 | 60
|  |  |  | Saturday | 60 | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 60 | 60
|  |  |  | Sunday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 60 | 60 | 60 | 60 | 60
All Zones | Retail | ClgSetpt | T24 2022 - Appendix 5.4B, [Retail] | Weekday | 85 | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 85 | 85 | 85
|  |  |  | Saturday | 85 | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 85 | 85
|  |  |  | Sunday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 85 | 85 | 85 | 85 | 85
Other
| Building | ExtLightingNonMotionCtrl |  | Weekday | bar: Hour 1 to Hour 24
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
| Building | ExtLightingMotionCtrl |  | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Retails | Building | RetailSalePeopleActivityLevel | Based on Activity level schedules in CEC Prototypes | Weekday | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
|  |  |  | Saturday | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
|  |  |  | Sunday | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
Background Data [To be deleted prior to publication]
Background Data [To be deleted prior to publication] | bar: Hour 1

## Energy Usage (hidden)
CalBEM Energy Consumption - RetailStripMall | [7 empty] | National Average (EnergyStar Portfolio Manager) |  |  |  | CEUS Energy Consumption : Retail | [8 empty] | PNNL RetailStripMall 2007 (with floor area of 22,500 ft2) for San Diego shows 62 KBTU/ft2 | PNNL results are close to RetailMedium
Prototype | CZ | CalBEM Electricity EUI (KBTU/ft²) | CalBEM Gas EUI (KBTU/ft²) | CalBEM Total EUI (KBTU/ft²) | New Construction Electricity EUI (KBTU/ft²) | New Construction Gas EUI (KBTU/ft²) | New Construction Total EUI (KBTU/ft²) | National Average | Acceptable Range (25% Higher) | Acceptable Range (25% Lower) | National Average Acceptable EUI Range | Prototype | CZ | Total Floorspace (Thousand of ft²) | CEUS 2023 Electricity EUI (kBtu/ft²) | CEUS 2023 Gas EUI (kBtu/ft²) | CEUS 2023 Total EUI (kBtu/ft²) | Acceptable Range (25% Higher) | Acceptable Range (25% Lower) | CEUS 2022 Acceptable EUI Range | PNNL RetailStripMall 2022 (with floor area of 22,500 ft2) for San Diego shows 29 KBTU/ft2
RetailStripMall | 1 | [6 empty] | 46.8 | 58.5 | 35.1 | 23.4 | Retail | 1 | 13814 | 37.9 | 10.4 | 48.3 | 60.375 | 36.225 | 24.15
| 2 | [6 empty] | 58.4 | 73 | 43.8 | 29.2 |  | 2 | 25239 | 26.6 | 14.8 | 41.4 | 51.75 | 31.05 | 20.7
| 3 | [6 empty] | 52.3 | 65.375 | 39.225 | 26.15 |  | 3 | 88648 | 34.8 | 11.9 | 46.7 | 58.375 | 35.025 | 23.35
| 4 | [6 empty] | 60.9 | 76.125 | 45.675 | 30.45 |  | 4 | 44551 | 35.5 | 11.5 | 47 | 58.75 | 35.25 | 23.5
| 5 | [6 empty] | 50.4 | 63 | 37.8 | 25.2 |  | 5 | 9847 | 31.7 | 14.6 | 46.3 | 57.875 | 34.725 | 23.15
| 6 | [6 empty] | 57.8 | 72.25 | 43.35 | 28.9 |  | 6 | 92562 | 29.3 | 4.6 | 33.9 | 42.375 | 25.425 | 16.95
| 7 | [6 empty] | 57.8 | 72.25 | 43.35 | 28.9 |  | 7 | 63471 | 35.1 | 3.2 | 38.3 | 47.875 | 28.725 | 19.15
| 8 | [6 empty] | 58.9 | 73.625 | 44.175 | 29.45 |  | 8 | 147354 | 29 | 4.5 | 33.5 | 41.875 | 25.125 | 16.75
| 9 | [6 empty] | 59.6 | 74.5 | 44.7 | 29.8 |  | 9 | 212697 | 32.1 | 4.8 | 36.9 | 46.125 | 27.675 | 18.45
| 10 | [6 empty] | 60.2 | 75.25 | 45.15 | 30.1 |  | 10 | 149832 | 31.7 | 5.3 | 37 | 46.25 | 27.75 | 18.5
| 11 | [6 empty] | 62.3 | 77.875 | 46.725 | 31.15 |  | 11 | 45934 | 36.2 | 9.3 | 45.5 | 56.875 | 34.125 | 22.75
| 12 | [6 empty] | 61.3 | 76.625 | 45.975 | 30.65 |  | 12 | 195816 | 37.5 | 9.8 | 47.3 | 59.125 | 35.475 | 23.65
| 13 | [6 empty] | 62.3 | 77.875 | 46.725 | 31.15 |  | 13 | 67122 | 42.3 | 8.9 | 51.2 | 64 | 38.4 | 25.6
| 14 | [6 empty] | 62.6 | 78.25 | 46.95 | 31.3 |  | 14 | 39049 | 29.3 | 4.4 | 33.7 | 42.125 | 25.275 | 16.85
| 15 | [6 empty] | 60.1 | 75.125 | 45.075 | 30.05 |  | 15 | 73160 | 34.1 | 8.3 | 42.4 | 53 | 31.8 | 21.2
| 16 | [6 empty] | 61.2 | 76.5 | 45.9 | 30.6 |  | 16 | 149464 | 32.8 | 5.3 | 38.1 | 47.625 | 28.575 | 19.05
Ref: CEUS 2022 Report
And converted FZ level data to CZ level
CEUS has only one category for Retail
Background Data [To be deleted prior to publication]

## Weights (hidden)
% of Floor Area per CZ and Vintage Bin - Retail | [6 empty] | % of Floor Area per CZ and Vintage Bin - Retail
Prototype | CZ | Vintage Bin |  |  |  |  | Prototype | Vintage Bin | CZ
|  | Pre-1978 | 1978-1997 | 1998-2007 | 2008-2018 |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
Retail | 1 |  |  |  |  | 0% | Retail | Pre-1978 | [16 empty] | 0%
| 2 |  |  |  |  | 0% |  | 1978-1997 | [16 empty] | 0%
| 3 |  |  |  |  | 0% |  | 1998-2007 | [16 empty] | 0%
| 4 |  |  |  |  | 0% |  | 2008-2018 | [16 empty] | 0%
| 5 |  |  |  |  | 0% |  | Not available | [16 empty] | 0%
| 6 |  |  |  |  | 0% |  | Total | [16 empty] | 0%
| 7 |  |  |  |  | 0%
| 8 |  |  |  |  | 0%
| 9 |  |  |  |  | 0%
| 10 |  |  |  |  | 0%
| 11 |  |  |  |  | 0%
| 12 |  |  |  |  | 0%
| 13 |  |  |  |  | 0%
| 14 |  |  |  |  | 0%
| 15 |  |  |  |  | 0%
| 16 |  |  |  |  | 0%
| Statewide |  |  |  |  | 0%
Ref: CEUS 2022 dataset
And converted FZ level data to CZ level
CEUS has only one category for Retail

## PV (hidden)
PV - RetailStripMall
TBD

## EV Charger (hidden)
EV Charger - RetailStripMall
TBD
Background Data [To be deleted prior to publication]

## Data (hidden)
Space Function | Electric Equipment Load Intensity | Electric Equipment Load Intensity | LPD
Aging Eye/Low-vision (Corridor Area) |  |  | 2013 | 2016 | 2019 | 2025
Aging Eye/Low-vision (Dining)
Aging Eye/Low-vision (Lobby, Main Entry)
Aging Eye/Low-vision (Lounge/Waiting Area)
Aging Eye/Low-vision (Multipurpose Room)
Aging Eye/Low-vision (Religious Worship Area)
Aging Eye/Low-vision (Restroom)
Aging Eye/Low-vision (Stairwell)
Audience Seating Area
Auditorium Area
Auto Repair / Maintenance Area
Barber, Beauty Salon, Spa Area
Civic Meeting Place Area
Classroom, Lecture, Training, Vocational Areas
Concourse and Atria Area
Convention, Conference, Multipurpose and Meeting Area
Copy Room
Corridor Area
Dining Area (Bar/Lounge and Fine Dining)
Dining Area (Cafeteria/Fast Food)
Dining Area (Family and Leisure)
Electrical, Mechanical, Telephone Rooms
Exercise/Fitness Center and Gymnasium Areas
Financial Transaction Area
Healthcare Facility and Hospitals (Exam/Treatment Room)
Healthcare Facility and Hospitals (Imaging Room)
Healthcare Facility and Hospitals (Medical Supply Room)
Healthcare Facility and Hospitals (Nursery)
Healthcare Facility and Hospitals (Nurse's Station)
Healthcare Facility and Hospitals (Operating Room)
Healthcare Facility and Hospitals (Patient Room)
Healthcare Facility and Hospitals (Physical Therapy Room)
Healthcare Facility and Hospitals (Recovery Room)
Hotel Function Area
Kitchen/Food Preparation Area
Kitchenette or Residential Kitchen
Laboratory, Scientific
Laundry Area
Library (Reading Area)
Library (Stacks Area)
Lobby, Main Entry
Locker Room
Lounge, Breakroom, or Waiting Area
Manufacturing, Commercial & Industrial Work Area (Low Bay)
Manufacturing, Commercial & Industrial Work Area (High Bay)
Manufacturing, Commercial & Industrial Work Area (Precision)
Museum Area (Exhibition/Display)
Museum Area (Restoration Room)
Office Area (>250 square feet)
Office Area (<250 square feet)
Parking Garage Area (Parking Zone and Ramps)
Parking Garage Area (Daylight Adaptation Zones)
Pharmacy Area
Retail Sales Area (Grocery Sales)
Retail Sales Area (Retail Merchandise Sales)
Retail Sales Area (Fitting Room)
Religious Worship Area
Restrooms
Stairwell
Storage, Commercial/Industrial (Warehouse)
Storage, Commercial/Industrial (Refrigerated)
Storage, Commercial/Industrial (Shipping & Handling)
Storage (General)
Sports Arena - Playing Area (> 5,000 Spectators)
Sports Arena - Playing Area (2,000 - 5,000 Spectators)
Sports Arena - Playing Area (< 2,000 Spectators)
Sports Arena - Playing Area (Recreational)
Theater Area (Motion Picture)
Theater Area (Performance)
Transportation Function (Baggage Area)
Transportation Function (Ticketing Area)
Videoconferencing Studio
High-Rise Residential Living Spaces
Hotel/Motel Guest Room
All other
Attic
Reception Area
Elevator
Plenum
IT Room (EPD 12)
Computer Room (EPD 20)
Server Room (EPD 45)