## Notes
Data Sources
Dataset | Dodge 2023
CEUS 2022
CBECS 2018
ComStock 2023
Prototype | CEC Small Office prototype (CBECC 2022.3.1) | https://bees.noresco.com/software2022.html
| PNNL Small Office prototype (90.1-2022) | https://www.energycodes.gov/prototype-building-models#Commercial
| DEER Small Office prototype (June 2023) | https://github.com/sound-data/DEER-Prototypes-EnergyPlus
| ORNL 2019 Small Office prototype zoning | https://web.eecs.utk.edu/~jnew1/publications/2019_IBPSA_OpenStudioOffice.pdf
Codes | T24, referred to as T24 (1984, 1992,1998, 2001, 2005, 2008, 2013, 2016,2019, 2022, 2025)
ASHRAE 90.1 (2022)
| CFR Title 10 (2010) | https://www.govinfo.gov/content/pkg/FR-2009-03-23/pdf/FR-2009-03-23.pdf
| CFR Title 10 (2013) | https://www.govinfo.gov/content/pkg/CFR-2013-title10-vol3/pdf/CFR-2013-title10-vol3-part431.pdf
| CFR Title 10 (2024) | https://www.govinfo.gov/content/pkg/CFR-2024-title10-vol3/pdf/CFR-2024-title10-vol3-part431-subpartF.pdf
Others | https://www.mass.gov/doc/small-office-prototype-basis-of-design-report/download | https://www.mass.gov/lists/stretch-energy-code-development-support-documentation
Massachusetts uses commercial prototype for its stretch code energy analysis and the above ones are the supporting documents for small office prototype
ACM (2022)
| Title 24, 2022 - Appendix 5.4A and Appendix 5.4B | https://www.energy.ca.gov/publications/2022/2022-nonresidential-and-multifamily-alternative-calculation-method-reference | https://www.energy.ca.gov/publications/2022/2022-nonresidential-and-multifamily-alternative-calculation-method-reference | https://www.energy.ca.gov/publications/2022/2022-nonresidential-and-multifamily-alternative-calculation-method-reference | https://www.energy.ca.gov/publications/2022/2022-nonresidential-and-multifamily-alternative-calculation-method-reference
| 2022 Reduced infiltration CASE report | https://title24stakeholders.com/wp-content/uploads/2020/10/2022-T24-Final-CASE-Report_Reduce-Infiltration.pdf | https://title24stakeholders.com/wp-content/uploads/2020/10/2022-T24-Final-CASE-Report_Reduce-Infiltration.pdf | https://title24stakeholders.com/wp-content/uploads/2020/10/2022-T24-Final-CASE-Report_Reduce-Infiltration.pdf | https://title24stakeholders.com/wp-content/uploads/2020/10/2022-T24-Final-CASE-Report_Reduce-Infiltration.pdf
| PNNL 20405, 2010 | https://www.pnnl.gov/main/publications/external/technical_reports/PNNL-20405.pdf | file:///N:/Prj_SUS/2023/S23668%20SCE%20CA%20Prototypes%20Development/Technical/NR/0_Input%20data/Lighting/PNNL-20405.pdf | file:///N:/Prj_SUS/2023/S23668%20SCE%20CA%20Prototypes%20Development/Technical/NR/0_Input%20data/Lighting/PNNL-20405.pdf | file:///N:/Prj_SUS/2023/S23668%20SCE%20CA%20Prototypes%20Development/Technical/NR/0_Input%20data/Lighting/PNNL-20405.pdf
| Air leakage Memo, NORESCO, 2025 | Infiltration_rate_report_14May2025-Short-Version.docx | Infiltration_rate_report_14May2025-Short-Version.docx | Infiltration_rate_report_14May2025-Short-Version.docx | Infiltration_rate_report_14May2025-Short-Version.docx
Construction Rate
Notes
| Saturation is defined as the % of total floorspace for each combination of end-use and fuel-type. | [5 empty] | 1978-84 | 1985-97 | 1992-1997
1986 is the representative year for the 1984-1997 vintage bin | Most offices in this vintage bin were built after 1984 (more than 53% ) and the CA energy code did not noticeably changed between 1984 to 1992) . Edition 1986 included 6 prescriptive package per CZ for office buildings compared to 1984 with 3 package per CZ. Also "Heat Capacity" for external wall is considered between 10.0 to 14.99 (BTU/F/ft²) Package A was selected for the thermal properties |  |  |  |  | Construction rate (Dodge 2023 data for new small offices) | 46.54% | 53.46% | 9.365%
2001 is the representative year for the 1998-2007 vintage bin | Wall and roof prescriptive criteria from 1998 to 2005 remain unchanged except for CZ2 and 6 in 2001 code (the percentage of change is less than 10%). Since the construction rate between 1998-2005 is greater than the 2006-2007 period, the envelope properties of 1998 -2005 were chosen for envelope properties. Since the windows requirement considerably changed in the 2001 code, the nominated year for this vintage is 2001. It should be noticed that, only one Title 24 should be chosen within each vintage bin for building envelope properties since the entire envelope is built at once. We can't choose 1998 for walls and 2001 for windows. Wall and roof prescriptive criteria from 1998 to 2005 remain unchanged except for CZ2 and 6 in 2001 version (the percentage of change is less than 10%).
2013 is the representative year for the 2008-2018 vintage bin | Wall properties remain unchanged from the 2008 code to the 2016 code but the roof did changed. Although the 2016 code introduced improvement for roof in nearly all CZ and for wall in a few CZ, and construction activity surged between 2017 and 2018, the extended period from 2008 to 2016 resulted in a higher construction rate during that time . As a result, it was decided to select the code that was effective during 2008-2016. The 2013 code modified the solar reflectance requirement for low-sloped roof products ( by approximately 15%), and enhanced window properties. Therefore, the 2013 code was chosen as the representative code. Additionally, construction activity from 2014-2018 was higher compared to 2008-2013 period.

## Prototype
NORESCO, Updated November 2025
OfficeSmall
Characteristic | Value | Data Sources
Building Type | Small Office
Building Category | Nonresidential
Vintages | 4 Vintages: Pre-1978 , 1978-1997 ,1998-2007 , 2008-2018 New Construction (2019+) | Based on the vintage bin analysis | NonRes-Vintage bins-Draft Report-30Nov2023-Final.docx
Shape |  | Rectangular shape is supported by CBECS, CEC, and PNNL
Total Floor Area (ft²) | 5502 (90.8 ft x 60.5ft) | Supported by Dodge 2023 data (Same as CEC and PNNL)
Aspect Ratio | 1.5 | Same as CEC and PNNL
Number of Floors | 1 | Supported by Dodge 2023 data -(Same as CEC and PNNL) DEER considered two floors
Roof type | Tilted (Steep-Sloped) | Supported by CBECS 2018 data (Same as CEC and PNNL)
WWR | 24.4% for South and 19.8% for the other three orientations | CEC: overall 21.2% same as PNNL DEER: 33% in all directions CBECS: 2-25%
Shading Geometry | No Shades | Same as CEC and PNNL
Floor to floor height (feet) | 10 | Same as CEC and PNNL
Floor to ceiling height (feet) | 10 | Same as CEC and PNNL
Glazing sill height (feet) | 3 (top of the window is 8 ft high with 5 ft high glass) | Same as CEC and PNNL
Background Data [To be deleted prior to publication]
Equipment (Plug Load )- Prototypes comparison
|  |  | Unit | CEC OffSml | DEER OFS | PNNL | ComStock | Note
|  |  | W/ft2 | 1.5 | 1.5 | 0.63 |  | PNNL considers higher load for electric equipment
|  |  | Yearly Load multiplier | 2835.7 | 2835.7 | 3837.815

## Zones
Proposed Layout - OfficeSmall
Space/Thermal Zone | Space Type | HVAC System Name/AHU Name | Schedule Category | Conditioned (Y/N) | Area Fraction | Area (ft²) | Volume (ft³) | Multipliers | Number of People | People (Persons/1,000 ft²) [T24, 2025,Table 120.1-A]
Open_Office_N | Office Area (>250 square feet) | AHU_N | Office | Yes | 16.59% | 912.6975 | 9126.975 | 1 | 4.5635 | 5
Closed_Office_W | Office Area (>250 square feet) | AHU_W | Office | Yes | 16.51% | 908.46 | 9084.6 | 1 | 4.5423 | 5
Closed_Office_E | Office Area (>250 square feet) | AHU_E | Office | Yes | 16.51% | 908.46 | 9084.6 | 1 | 4.5423 | 5
Conference | Convention, Conference, Multipurpose and Meeting Area | AHU_S | Office | Yes | 8.294% | 456.35 | 4563.5 | 1 | 15.0596 | 33
Lobby_Lounge | Lobby, Main Entry | AHU_S | Office | Yes | 8.294% | 456.35 | 4563.5 | 1 | 4.5635 | 10 | People: 10 according to ASHRAE 62.1, Table 6-1 for main entry lobbies T24: 33 for main Entry lobbies & 5 for reception area
Storage | Storage (General) | AHU_W | Office | Yes | 13.52% | 743.8879 | 7438.8791 | 1 | 1.4878 | 2
Mechanical_Electrical | Electrical, Mechanical, Telephone Rooms | AHU_S | Office | Yes | 2.076% | 114.23 | 1142.3 | 1 |  | -
Restroom | Restrooms | AHU_W | Office | Yes | 4.076% | 224.28 | 2242.8 | 1 |  | -
Break_CopyRoom | Lounge, Breakroom, or Waiting Area | AHU_S | Office | Yes | 2% | 110.05 | 1100.5 | 1 | 3.6317 | 33
Corridor_W | Corridor Area | AHU_W | Office | Yes | 2.222% | 122.26 | 1222.6 | 1 | 0.6113 | 5
Corridor_N | Corridor Area | AHU_N | Office | Yes | 3.842% | 211.39 | 2113.9 | 1 | 1.0569 | 5
Corridor_E | Corridor Area | AHU_E | Office | Yes | 2.222% | 122.26 | 1222.6 | 1 | 0.6113 | 5
Corridor_S | Corridor Area | AHU_S | Office | Yes | 3.842% | 211.39 | 2113.9 | 1 | 1.0569 | 5
Attic | Attic |  | n/a | No | 100% | 6114.3047 | 25437.1108 | 1 |  | -
Total (14 Space) | Total (9 Space) | Total (4 HVAC system) | Total (1 category) | Total (4 Conditioned zones, 1 Unconditioned Zones) | 100% | 5502.0654 | 80457.7649 | 1
Ref: Geometry and zones: ORNL 2019 small office prototype with modification
https://web.eecs.utk.edu/~jnew1/publications/2019_IBPSA_OpenStudioOffice.pdf
https://web.eecs.utk.edu/~jnew1/presentations/2019_IBPSA_OpenStudioOffice.pdf
Background Data [To be deleted prior to publication]
Review zones of Existing Small Office Prototype
| Parameter | PNNL |  | CEC | DEER
| Number of Zones | 5 conditioned (1 core, 4 perm, 1 attic) |  | 5 conditioned (1 core, 4 perm, 1 attic) | 20 (10 per floor: 5 conditioned zones and 5 plenum unconditioned zones)
| Floor area of spaces (ft²) | 1610.9268 |  | 1610.9268 | 1570.6698
|  | 1221.1656 |  | 1221.1656 | 1074.023
|  | 724.4112 |  | 724.4112 | 641.2061
|  | 6113.6858 |  | 6113.6858 | 0
|  | 5502.0804 |  | 5502.0804 | 5001.1819
|  | 5502.0804 |  | 5502.0804 | 10002.3638
| People | 120 |  | 131.9 | 120
0.55556
N

## Envelope
Envelope - OfficeSmall
Element | Prototype | Assembly Type | Construction | Thermal Properties | Vintage | Selected T24 | Note | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
External Wall | OfficeSmall | ExtWall_WoodFramed_NonRes | Wood-frame walls* + insulation + Gypsum board | U-factor IP | Pre 1978 | N/A | ASHRAE 90.1, 2022, Table A3.4.3.1, 3.5", R-0 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292
[5 empty] | 1978-1997 | 1986 | Table 2-53V-16: Package A/ Heat Capacity was considered 10.0-14.99 (BTU/F/ft²) | 0.15083 | 0.15748 | 0.15748 | 0.14368 | 0.14368 | 0.21645 | 0.21645 | 0.21645 | 0.21645 | 0.21645 | 0.18622 | 0.18622 | 0.18622 | 0.15873 | 0.15873 | 0.15083
[5 empty] | 1998-2007 | 2001 | Table 1-H | 0.084 | 0.084 | 0.092 | 0.092 | 0.092 | 0.092 | 0.092 | 0.092 | 0.092 | 0.084 | 0.084 | 0.084 | 0.084 | 0.084 | 0.084 | 0.084
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.102 | 0.059 | 0.11 | 0.059 | 0.102 | 0.11 | 0.11 | 0.102 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.042 | 0.059
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.078 | 0.053 | 0.102 | 0.053 | 0.095 | 0.102 | 0.102 | 0.095 | 0.053 | 0.053 | 0.042 | 0.053 | 0.053 | 0.053 | 0.038 | 0.053
Flat Roof | OfficeSmall | AtticFloor Reversed | Ceiling: Wood-frame roof + insulation + Acoustic tile/Gypsum board (Attic Roof: Asphalt shingle + Plywood) | U-factor IP | Pre 1978 | 1992 | Table 2-53V-16: Considering 30 years for roof/ insulation replacement. | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 1978-1997 | 1992 |  | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 1998-2007 | 2001 | Table 1-H | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.049 | 0.039 | 0.039 | 0.039 | 0.049 | 0.075 | 0.067 | 0.067 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.047 | 0.047 | 0.047 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028
Windows | OfficeSmall | FixedWindow_NonRes | Mix Single and Double: CBECS 2018 shows that ~53% of small offices that were built before 2000 are single pane | U-factor IP | Pre 1978 | N/A | ASHRAE Handbook of Fundamentals (Table 10-Ch15) for single pane & T24, 2013 for double pane(53%-47%)* | 0.8239 | 0.8239 | 0.9743 | 0.9743 | 0.9743 | 0.9743 | 0.9743 | 0.9743 | 0.9743 | 0.8239 | 0.8239 | 0.8239 | 0.8239 | 0.8239 | 0.8239 | 0.8239
[5 empty] | 1978-1997 | N/A |  | 0.8239 | 0.8239 | 0.9743 | 0.9743 | 0.9743 | 0.9743 | 0.9743 | 0.9743 | 0.9743 | 0.8239 | 0.8239 | 0.8239 | 0.8239 | 0.8239 | 0.8239 | 0.8239
|  |  | Double pane |  | 1998-2007 | 2001 | Table 1-H | 0.49 | 0.49 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.34 | 0.36 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.36
| OfficeSmall | FixedWindow_NonRes | Mix Single and Double: CBECS 2018 shows that ~53% of small offices that were built before 2000 are single pane | SHGC | Pre 1978 | N/A | ASHRAE Handbook of Fundamentals (Table 10-Ch15) for single pane & T24, 2013 for double pane(53%-47%)* | 0.6208 | 0.5879 | 0.6114 | 0.6114 | 0.6114 | 0.602 | 0.602 | 0.602 | 0.602 | 0.5879 | 0.5879 | 0.5879 | 0.5879 | 0.5879 | 0.5879 | 0.6208
[5 empty] | 1978-1997 | 1986 |  | 0.6208 | 0.5879 | 0.6114 | 0.6114 | 0.6114 | 0.602 | 0.602 | 0.602 | 0.602 | 0.5879 | 0.5879 | 0.5879 | 0.5879 | 0.5879 | 0.5879 | 0.6208
[5 empty] | 1998-2007 | 2001 | Table 1-H : WWR:20-30 / SHGC non-north | 0.43 | 0.36 | 0.41 | 0.41 | 0.41 | 0.39 | 0.39 | 0.39 | 0.39 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.43
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.22 | 0.25 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.25
Infiltration
[5 empty] | Vintage | I_75 6-sided Infiltration rate @ 75 pa | Note | I-design (cfm/ft²) (4-sided Infiltration rate at normal pressure) (Design flow rate approach and Flow/Exterior Wall Area calculation method)
|  |  |  | Infiltration | Pre 1978 | 1.1 | 2022 CASE report (Table 38) | 0.5667
[5 empty] | 1978-1997 | 1.1 | 2022 CASE report (Table 38) | 0.5667
[5 empty] | 1998-2007 | 1.1 | 2022 CASE report (Table 38) | 0.5667
[5 empty] | 2008-2018 | 1 | 2022 CASE report (Table 38) & T24, 2008-2016 (Table 140.3-C) | 0.5185
[5 empty] | 2019+ | 0.6* | 2022 CASE report (Table 38) & T24, 2025 (Table 140.3-C) | 0.3091
Source: Title 24 air barrier requirements (all editions) and the standardized infiltration rate reported in the 2022 CASE report and Dodge 2023 data
* Better to consider 0.6 for New construction instead of being very stringent align with the Appendix G of ASHRAE 90.1 (which is almost 0.4)
|  |  |  | Air Leakage Memo: |  | Infiltration_rate_report_14May2025-Short-Version.docx
Background Data [To be deleted prior to publication]
Interior wall
Gypsum board
Wood stud |  | R=0.32 | wood stud 2*4, covers 25% of the interior wall volume between two layer of gypsum board , | 0.2
Air (or insulation) |  | R=0.16 | air covers the rest 75%.
Gypsum board
Infiltration | Pre 1978
| 1978-1997 | 1984 | Title 24, 1984/Table 2-53J | 0.5 cfm/ft for sash crack of windows, 0.5 cfm/ft² of door area for single door or 0.1 cfm/ft² of door area for double door
| 1998-2007 | 2001 | Title 24, 2001/116(a)1 | 0.3 cfm/ft² of window area / 0.3 cfm/ft² of door area for nonresidential single doors (swinging and sliding), and 1.0 cfm/ft² for nonresidential double doors (swinging),
| 2008-2018 | 2013 | Title 24, 2013/110.6(a)1 and 140.3(9)(c) | 0.3 cfm/ft² of window area / 0.3 cfm/ft² of door area for nonresidential single doors (swinging and sliding), and 1.0 cfm/ft² for nonresidential double doors (swinging), 0.4 cfm/ft² @ 75 Pa whole building
| 2019+ | 2025 | Title24, 2025/Section 110.6(a)1 and 140.3(9)© | 0.3 cfm/ft² of window area / 0.3 cfm/ft² of door area for nonresidential single doors (swinging and sliding), and 1.0 cfm/ft² for nonresidential double doors (swinging), 0.4 cfm/ft² @ 75 Pa whole building
Infiltration rate in the existing prototypes:
Infiltration features |  | CEC | PNNL | DEER | Comstock |  | Generally | DOE2 Pre 1980 |  |  | NOR
Method and Coefficients |  | Flow/ExteriorWallArea Infiltration=Idesign*Fschedule*(A+B(Tzone-Todb)+C*WindSpd+D*WindSpd^2) (0,0,0.224 for Velocity term,0) |  |  | Flow/ExteriorArea HVAC ON: 0.0209 for constant term,0.0064 for temperature term,0 for velocity term,0.1297 for velocity squared term HVAC OFF: 0,0.0179 for temperature term,0 ,0.1473 for velocity squared term |  |  | Flow/ExteriorArea for Perimeter zones: Constant coefficient=1 other=0 ACH for Core zone: Constant coefficient=1 other=0
Idesign (cfm/sf2) |  | 0.2352 | 0.0392421041 0.0423987889 (Attic) | 0.044801 | 0.4881276 (Case 5307-5500sf-1979-wood) 0.3661 (case 13134-5500sf-2001-wood) 0.1627 (case 13157-5500sf-2004-Mass) 0.122 (Case 4389--5500sf-2000-wood) 0.244 (Case 6213--5500sf-2004-SteelF) |  | tight for vintage 4th and New construction: 1.5 cfm/sf from DOE pre-1980 model, 0.35: 1978-1997 0.2 1997-2008 0.1: 2008-2018 | Flow/Exterior wall: Pre 1980/Post 1980: 0.223 (0.001133 m3/s-m2) New 2004: 0.0594 (0.000302 m3/s-m2) ACH: 0.36 per hour
Schedule | Office space (Weekday/WD) | 0-5am 1 5am-12am 0.25 | 0-7am 1 7am-7pm 0.25 7pm-12am 1 | 1 | 0.00014224 |  |  | 0-6am 1 6am-10pm 0.25 10pm-12am 1
| Office space (Saturday) | 0-5am 1 6am-7pm 0.25 7pm-12am 1 | 0-7am 1 7am-6pm 0.25 6pm-12am 1 | 1 |  |  |  | 0-6am 1 6am-6pm 0.25 6pm-12am 1
| Office space (Sunday) | 1 | 1 | 1 |  |  | 1 | 1
Note |  |  | one infiltration object per perimeter zones (ONLY perimeter) +one object for the entrance door | one infiltration object per each zone | Case 5307, year 1979: TWO objects per zone: one for HVAC Off and another when HAVC is on |  | Four Inf objects for the perimeter spaces + Another Inf. object for the zone with Door : 0.129785425 ft3/min (Same as PNNL) |  |  |  | 0.12978 ft3/min: PNNL value for door infiltration flow/zone
the ON schedule is always 1 and the OFF one is always 0.
Dodge 2023 Construction data
Dodge 2023 data for new small offices |  | vintage 1978-19997 | [5 empty] | Year | Small Office area
|  | 1978-84 | 1985-97 | 1992-1997 |  |  |  | 1967 | 2027
Construction rate |  | 7.75% | 0% | 0% |  |  |  | 1968 | 3870.9
Total Constructed floor area |  | 144615 | [5 empty] | 1969 | 4189.2
[8 empty] | 1970 | 3556.1
[8 empty] | 1972 | 6100
[8 empty] | 1973 | 6863.1
[8 empty] | 1974 | 4880.1
Comstock 2023 | Exterior wall Type | [6 empty] | 1975 | 3714.8
| Steel Framed | Wood Framed | Mass |  |  |  |  | 1976 | 4880.2
Small Office | 39.97% | 30.19% | 29.84% |  |  |  |  | 1977 | 8079.2
Considering 1/3 for each category and having wood frame tilted roof, it's been decided to consider wood framed wall. | [7 empty] | 1978 | 11207.1

## HVAC System
HVAC System - OfficeSmall
Vintage | Heating | Cooling | Air Distribution | Source
Existing | Furnace (Gas) | Packaged (DX) | Single Duct Constant Air Volume | CEUS 2022 | PTAC
New Construction | Packaged SZ HP | Packaged SZ HP | Single Duct Constant Air Volume | T24 2025 | PTHP
Efficiency of HVAC system
Vintage | Upgrade Code | Heating | Cooling | Source |  | COP | Source | R (Adjustment factor)
Pre 1978 | 2008 | Efficiency 80% | EER=9.0 | T24, Part 6, 2007 /CFR Energy 2009 page 12074 |  | 3.0663 | PNNL,2010,"Technical Support Document: 50% Energy Savings for Small Office Buildings" | 0.12
1978-1997 | [5 empty] | 3.0663
1998-2007 | [5 empty] | 3.0663
2008-2018 | 2010 | COP=3 / Efficiency 80% | EER=9.0 SEER=13 | CFR Energy 2010:Title 10- Table 9 10 CFR 2013 (431.97, Table 1) |  | 3.0663
New Construction | 2025 | COP=3.3 / Efficiency 80% | SEER2=13.4 | CFR Energy 2024:Title 10- Table 19 - § 431.97 |  | 3.9952
Fan power
Vintage | Approach | System | Total Static Pressure (TSP) (in w.c.) [PNNL 20405, 2010, Table 5.11] | Fan Efficiency [ACM 2025] | Fan Motor and Drive Efficiency [ACM 2025, Table 13] | W/cfm [ACM 2025, Table 14 and 15] | Data Source
Existing | PNNL TSP | CAV (system < 7,437 cfm) | 1.33 | 0.65 | ~0.9 (The full-load efficiency of the motor serving the fan- will be determined based on ACM 2025, Table 13) |  | PNNL 20405, 2010, Table 5.11
Brake horse power (bhp)=(Supply cfm*TSP in w.c.)/(6356*Fan efficiency)
Fan power (w/cfm) = bhp/motor and drive efficiency *746
New Construction | ACM 2025 | System 3b-SZHP, <5000 | 0 | 0.65 | 0.9 | 0.744 | ACM 2025
|  | PVAV System >10,000 cfm | 0 |  |  | 0.964
* 0.9 is an average fan efficiency according to ACM 2025, Table 13
Fan total eff (E+ input) = 0.65 x Motor_eff
TSP (E+ input) in w.c. = Motor_eff/746 x (6356 x Fan_eff) x W/cfm
Fan_eff=0.65
Background Data [To be deleted prior to publication]
| CEC | PNNL | DEER | ComStock
Zone cooling design supply air temperature (F) | 57.5 | 55 | 55
Air distribution system | CAV | CAV | VAV | CAV
Max air flow rate | Values | Autosize | Autosize | Values
Reference for Efficiency
[11 empty] | FCZ12 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
|  |  | 10CFR 2024 |  | CFR 2025 (not for Hp which is New construction) |  |  | 74 FR 12058 : 2009 | FR-2009-03-23.pdf
ASHRAE 2010 : SEER 13
Referenced Ventilation
Discussion behind HVAC system selection
CEUS 2022 data | Heating | Cooling | Air Distribution
% of total impacted floor area | 91.18% | 89.99% | 93.1%
Dominated system | Package System / Heat Pump | Package System / Heat Pump | Single Duct Constant Air Volume in all vintage
% of impacted floor area covered by the dominant system | 73% | 73.36% | 92%
Fuel and Share | 43.4% Electric and 55.5% Gas | 99.9% by Electric
2% degradation for HVAC system per year
A study measured losses of a median of 1.2 W/m2 (of gross floor area) from the distribution piping in 7 large commercial buildings
Ref: P. Raftery, D. Vernon, R. Singla, M. Nakajima, Measured Space Heating Hot Water Distribution Losses in Large Commercial Buildings, ASHRAE Transactions 129 (1) (2023) 8.
Systems operate far more frequently than expected − 81% of hours annually for the median building. Loads are lower and more skewed than expected, and oversizing is common even accounting for redundancy requirements.
Notably, equipment sized to 30% of the maximum measured load could serve up 84% of the total heating energy consumption for the median building.
boilers operate less efficiently than expected
Ref: Raftery, Paul, et al. "Insights from hydronic heating systems in 259 commercial buildings." Energy and Buildings 321 (2024): 114543.
file:///N:/Prj_SUS/2023/S23668%20SCE%20CA%20Prototypes%20Development/Technical/Database/Papers/Insights%20from%20hydronic%20heating%20systems%20in%20259%20commercial%20buildings/Insights%20from%20hydronic%20heating%20systems%20in%20259%20commercial%20buildings.pdf
Discussion behind efficiency reference selection
For pre-1978: T24, Part 6, version 2008
According to the Comstock dataset, over 50% of small offices that were constructed before 1978, replaced their system between 2003 and 2011 with the following distribution. I think 2008 is a good decision since over 60% of HVAC got replace after 2007.
Comstock 2023 | Comstock dataset 2023: Floor area distribution of small offices built pre-1978 and updated HVAC in year …
Year | 1985 | 1996 | 2003 | 2007 | 2011 | 2014-15 | 2017
% of floor area | 7% | 15% | 17% | 20% | 16% | 15% | 9%
For 1978-1997: T24, Part 6, version 2008
Comstock shows that over 50% of these small offices have their HVAC system align with regulations passed between 2003 and 2011 with the following distribution. Although those buildings constructed between 1992 and1997, mainly updated their HVAC align with DEER 2011 code cycle (around T24 2010), most of the buildings in this vintage were bulti before 1992 and mainly upgraded their HVAC before 2011.
Comstock 2023 | Floor area distribution of small offices built 1978-1997 and their last HVAC align with code …
Year | 1985 | 1996 | 2003 | 2007 | 2011 | 2014-15 | 2017
% of floor area | 6% | 14% | 17% | 20% | 17% | 16% | 10%
Besides, Comstock shows that small offices in this vintage has an average HVAC replacement tie of 20 years .
However, if we consider 15 years for the average HVAC life cycle and consider year 1984 as a reference year (most of small offices in this vintage were constructed between 1978-1989 , and 1984 is almost in the middle of that), we will have T24, version 2013 as the reference code for efficiency selection. 1984+15+15=2014 which is close to Title 24 , 2013.
However, if we consider 15 years for the average HVAC life cycle and consider year 1984 as a reference year (most of small offices in this vintage were constructed between 1978-1989 , and 1984 is almost in the middle of that), we will have T24, version 2013 as the reference code for efficiency selection. 1984+15+15=2014 which is close to Title 24 , 2013.
For 1998-2007 : T24, 20051! (shifted from 2001 to T24 2005 code to consider the impact of the upgraded HVA). However, later it's been decided to select 2008 code to align with the earlier vintages
There is no code between 2001 and 2005. Comstock show that about 70% of these HVAC haven’t been replaced. Those updated their HVAC, update that in an average 14 years mainly around 2015-2017)
For 2008-2018: 2010!
According to Dodge 2023, over 68% of these small office are between 2008 and 2013.

## Thermostat
Thermostat Setpoints - OfficeSmall
Setpoint | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
Heating Setpoint (F) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
Heating Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Cooling Setpoint (F) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
Cooling Setback (F) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
The Small Office prototypes by CEC and DEER both use the same setpoints.
The Small Office prototype by PNNL also uses the same setpoints, except for one of the perimeter zones, which has a heating setpoint of 69 °F and a cooling setpoint of 76 °F during hours of 10:00-11:00, 12:00-13:00, and 14:00-15:00 .
Background Data [To be deleted prior to publication]
| Heating |  |  | Cooling
| Weekday | Saturday | Sunday | Weekday | Saturday | Sunday |  |  | Heating and Cooling setback schedule | Weekday | 12:am-5:00 am
DEER | 0:00 to 5:00 | 0:00 to 5:00 | 0:00 to 24:00 | 0:00 to 5:00 | 0:00 to 5:00 | 0:00 to 24:00 |  |  |  | Saturday | 7:00 pm-5:00 am
| 15.56 | 15.56 | 15.56 | 29.22 | 29.22 | 29.22 |  |  |  | Sunday | All the day
| 5:00 to 24:00 | 5:00 to 19:00 |  | 5:00 to 24:00 | 5:00 to 19:00
| 21.11 | 21.11 |  | 23.88 | 23.88
T24, Appendix JA5-4 : Occupant Controlled Smart Thermostat (OCST)
The findings indicated that households engaged in teleworking raised their winter thermostat setpoints by an average of 0.66 °C and decreased their summer thermostat setpoint by an average of 1.62 °C compared to the period that their home was vacant during office hours
2025, "Analyzing smart thermostat data to uncover trends in remote work behaviors"
https://www.sciencedirect.com/science/article/pii/S0378778825000507

## Ventilation
Outdoor Airflow Rate - OfficeSmall
Space/Thermal Zone | Number of People | Floor Area (ft²) | cfm/person (T24, 2025, Equation 120.1-F and Table 120.1-A) | cfm/ft² (T24, 2025, Equation 120.1-F and Table 120.1-A) | Required Exhaust Rate (T24, 2025, Table 120.1-B – Minimum Exhaust Rates) | Total cfm Driven by People | Total cfm Driven by Area | Total cfm Driven by Exhaust | Total cfm | Note
Open_Office_N | 4.5635 | 912.6975 | 15 | 0.15 |  | 68.4523 | 136.9046 |  | 136.9046 |  |  |  | AHU | cfm
Closed_Office_W | 15 | 0.15 | 15 | 0.15 |  | 225 | 0.0225 |  | 225 |  |  |  | AHU_N | 361.9046
Closed_Office_E | 15 | 0.15 | 15 | 0.15 |  | 225 | 0.0225 |  | 225 |  |  |  | AHU_W | 675
Conference | 15 | 0.15 | 15 | 0.15 |  | 225 | 0.0225 |  | 225 |  |  |  | AHU_E | 675
Lobby_Lounge | 15 | 0.15 | 15 | 0.15 |  | 225 | 0.0225 |  | 225 |  |  |  | AHU_S | 1125
Storage | 15 | 0.15 | 15 | 0.15 |  | 225 | 0.0225 |  | 225
Mechanical_Electrical | 15 | 0.15 | 15 | 0.15 |  | 225 | 0.0225 |  | 225
Restroom | 15 | 0.15 | 15 | 0.15 | 25/50 per unit | 225 | 0.0225 | 50 | 225
Break_CopyRoom | 15 | 0.15 | 15 | 0.15 |  | 225 | 0.0225 |  | 225
Corridor_W | 15 | 0.15 | 15 | 0.15 |  | 225 | 0.0225 |  | 225
Corridor_N | 15 | 0.15 | 15 | 0.15 |  | 225 | 0.0225 |  | 225
Corridor_E | 15 | 0.15 | 15 | 0.15 |  | 225 | 0.0225 |  | 225
Corridor_S | 15 | 0.15 | 15 | 0.15 |  | 225 | 0.0225 |  | 225
Attic | 15 | 0.15
Background Data [To be deleted prior to publication]
CEUS 2022 Data shows that about 50% of the unconditioned floor area belongs to the first vintage bin (Pre-1978)
Ref: CEUS 2022
| Ventilated |  | Ventilated Only |  |  | Conditioned - Floorspace that is heated and/or cooled
Statewide/ Utility/ FCZ | K SqFt | % of Tot. Comm. Floorspace | K SqFt | % of Tot. Comm. Floorspace | Total | Unconditioned - Floorspace that is not heated and/or cooled
Statewide | 717924.2529 | 93.1% | 5720.4277 | 0.7418% | 771153.5227 | Ventilated - Total floorspace that is Conditioned (heated and/or cooled), plus unconditioned spaces that are Ventilated
FCZ01 Tot | 110607.6915 | 92.48% | 110607.6915 | 92.48% | 119595.5776 | Ventilated Only - Unconditioned floorspace that is ventilated
FCZ02 Tot | 28894.0517 | 85.95% | 0 | 0% | 33616.997 | Refrigerated - Floorspace occupied by built-in commercial grade refrigerators (including walk-ins)
FCZ03 Tot | 9152.9953 | 97.32% | 0 | 0% | 9405.1639 | Frozen - Floorspace that is occupied by built-in commercial grade freezers (including walk-ins)
FCZ04 Tot | 40764.035 | 90.09% | 40764.035 | 90.09% | 45249.3283 | Refrigerated & Frozen Combined - Refrigerated and/or Frozen floorspace
FCZ05 Tot | 40651.5365 | 94.2% | 0 | 0% | 43153.1055
FCZ06 Tot | 33601.1545 | 96.13% | 33601.1545 | 96.13% | 34954.825
FCZ07 Tot | 162052.0614 | 96.39% | 162052.0614 | 96.39% | 168128.0774
FCZ08 Tot | 22464.0659 | 92.71% | 0 | 0% | 24229.8711
FCZ09 Tot | 11190.3905 | 95.71% | 0 | 0% | 11692.4715
FCZ10 Tot | 31510.4502 | 93.6% | 0 | 0% | 33664.068
FCZ11 Tot | 34908.6866 | 98.09% | 0 | 0% | 35588.1912
FCZ12c Tot | 60257.3858 | 90.7% | 60257.3858 | 90.7% | 66439.5525
FCZ12i Tot | 18564.5846 | 87.87% | 18564.5846 | 87.87% | 21127.5797
FCZ13 Tot | 25391.2101 | 87.25% | 25391.2101 | 87.25% | 29100.3243
FCZ16 Tot | 35458.8513 | 91.74% | 35458.8513 | 91.74% | 38649.9531
FCZ17 Tot | 13427.3773 | 91.74% | 0 | 0% | 14637.0677
| Ventilated (k SqFt) | [5 empty] | Ventilated-Only (k SqFt)
Statewide/ Utility/ FCZ | Pre-1978 | 1978-1997 | 1998-2007 | 2008-2018 | Not Available | Total | Pre-1978 | 1978-1997 | 1998-2007 | 2008-2018 | Not Available | Total
Statewide | 282213.6856 | 242811.9043 | 96185.0237 | 35649.0276 | 61064.6116 | 717924.2529 | 5143.4965 | 382.5795 | 194.3518 | 0 | 0 | 5720.4277
FCZ01 Tot | 54414.2314 | 32999.722 | 11122.2533 | 4603.0504 | 7468.4345 | 110607.6915 | 54414.2314 | 0 | 11122.2533 | 4603.0504 | 7468.4345 | 110607.6915
FCZ02 Tot | 13141.0984 | 9647.916 | 3659.6977 | 1714.0383 | 731.3014 | 28894.0517 | 0 | 0 | 0 | 0 | 0 | 0
FCZ03 Tot | 3193.2902 | 2796.6371 | 1418.2923 | 560.0588 | 1184.717 | 9152.9953 | 0 | 0 | 0 | 0 | 0 | 0
FCZ04 Tot | 4769.6281 | 13172.6073 | 17791.1299 | 2050.2791 | 2980.3906 | 40764.035 | 0 | 0 | 17791.1299 | 0 | 0 | 40764.035
FCZ05 Tot | 11153.2392 | 13335.8868 | 9354.7826 | 3829.8507 | 2977.7772 | 40651.5365 | 0 | 0 | 0 | 0 | 0 | 0
FCZ06 Tot | 12261.9014 | 10666.3803 | 2831.2619 | 1071.4579 | 6770.1529 | 33601.1545 | 12261.9014 | 10666.3803 | 0 | 0 | 0 | 33601.1545
FCZ07 Tot | 80605.7847 | 49236.975 | 10354.3648 | 5701.2154 | 16153.7214 | 162052.0614 | 80605.7847 | 0 | 0 | 0 | 0 | 162052.0614
FCZ08 Tot | 6525.3199 | 10968.355 | 2306.1579 | 2050.2475 | 613.9856 | 22464.0659 | 0 | 0 | 0 | 0 | 0 | 0
FCZ09 Tot | 2791.1654 | 2824.4311 | 2664.3979 | 951.7997 | 1958.5964 | 11190.3905 | 0 | 0 | 0 | 0 | 0 | 0
FCZ10 Tot | 7579.1686 | 10386.011 | 7421.6188 | 2642.6378 | 3481.0139 | 31510.4502 | 0 | 0 | 0 | 0 | 0 | 0
FCZ11 Tot | 5363.5935 | 12676.2904 | 7990.6575 | 4097.6866 | 4780.4586 | 34908.6866 | 0 | 0 | 0 | 0 | 0 | 0
FCZ12c Tot | 15464.3768 | 33781.6771 | 6158.0383 | 2245.6254 | 2607.6682 | 60257.3858 | 15464.3768 | 33781.6771 | 0 | 0 | 0 | 60257.3858
FCZ12i Tot | 6659.289 | 5922.0061 | 2160.3567 | 143.2159 | 3679.7168 | 18564.5846 | 6659.289 | 0 | 0 | 0 | 3679.7168 | 18564.5846
FCZ13 Tot | 8753.6669 | 10325.8157 | 4770.6935 | 1039.1204 | 501.9135 | 25391.2101 | 8753.6669 | 10325.8157 | 0 | 0 | 0 | 25391.2101
FCZ16 Tot | 25755.6489 | 8207.2074 | 952.5201 | 0 | 543.4749 | 35458.8513 | 25755.6489 | 0 | 0 | 0 | 0 | 35458.8513
FCZ17 Tot | 8440.6119 | 2664.2701 | 0 | 1010.7948 | 1311.7005 | 13427.3773 | 0 | 0 | 0 | 0 | 0 | 0
Calculation Method | Statewide/ Utility/ FCZ | 0% | 0%< X <10% | 10%<= X <20% | 20%<= X <30% | 30%<= X <40% | 40%<= X <50% | 50%<= X <60% | 60%<= X <70% | 70%<= X <80% | 80%<= X <90% | 90%<= X <100% | 100% | Total | ← % Floorspace Conditioned
Floorspace % | Statewide | 1.71% | 1.242% | 0.7935% | 0.8942% | 1.085% | 1.752% | 1.003% | 1.694% | 1.524% | 1.83% | 2.606% | 83.87% | 100%
Floorspace % | FCZ01 Tot | 3.073% | 2.238% | 0% | 1.187% | 0.5147% | 0.3113% | 0.3512% | 1.988% | 1.253% | 1.457% | 3.128% | 84.5% | 100%
Floorspace % | FCZ02 Tot | 0% | 6.081% | 0% | 0.133% | 0.3701% | 6.46% | 2.515% | 3.656% | 2.114% | 2.568% | 2.288% | 73.82% | 100%
Floorspace % | FCZ03 Tot | 0% | 0% | 0% | 0% | 0% | 1.692% | 0% | 3.144% | 2.041% | 0% | 2.4% | 90.72% | 100%
Floorspace % | FCZ04 Tot | 0.06176% | 2.913% | 0.8385% | 0.7206% | 4.274% | 0.4295% | 1.306% | 1.874% | 2.68% | 4.387% | 2.041% | 78.48% | 100%
Floorspace % | FCZ05 Tot | 0% | 0% | 0.3418% | 0.5731% | 0% | 5.448% | 2.525% | 0.8292% | 1.06% | 0.8288% | 4.407% | 83.99% | 100%
Floorspace % | FCZ06 Tot | 1.563% | 0.1456% | 2.536% | 0.5593% | 0% | 2.843% | 0% | 1.68% | 0.3951% | 0.3559% | 6.393% | 83.53% | 100%
Floorspace % | FCZ07 Tot | 0.7558% | 0.2066% | 0.07087% | 0.4003% | 0.9132% | 0.6959% | 0.4908% | 1.669% | 1.557% | 3.19% | 0.9101% | 89.14% | 100%
Floorspace % | FCZ08 Tot | 0% | 0% | 1.644% | 1.171% | 3.589% | 0.9917% | 0.3003% | 2.864% | 1.661% | 0.4461% | 0% | 87.33% | 100%
Floorspace % | FCZ09 Tot | 0% | 0% | 0% | 0% | 0% | 2.379% | 0% | 5.186% | 1.123% | 2.751% | 3.972% | 84.59% | 100%
Floorspace % | FCZ10 Tot | 0% | 0% | 2.076% | 0% | 0.7602% | 5.635% | 0.7852% | 0.5299% | 1.772% | 0.6989% | 1.093% | 86.65% | 100%
Floorspace % | FCZ11 Tot | 0% | 0% | 0.8006% | 0% | 0% | 0% | 1.422% | 1.296% | 0% | 0.5166% | 1.241% | 94.72% | 100%
Floorspace % | FCZ12c Tot | 1.646% | 0.3514% | 1.608% | 2.621% | 3.259% | 0.5685% | 2.056% | 0.8053% | 2.562% | 0.9653% | 2.448% | 81.11% | 100%
Floorspace % | FCZ12i Tot | 0.4117% | 5.507% | 2.603% | 0% | 0% | 3.365% | 2.708% | 1.034% | 2.124% | 0.3804% | 4.312% | 77.55% | 100%
Floorspace % | FCZ13 Tot | 0.1617% | 0.4279% | 2.392% | 5.46% | 1.41% | 1.282% | 2.629% | 3.987% | 3.448% | 4.596% | 6.27% | 67.94% | 100%
Floorspace % | FCZ16 Tot | 14.81% | 2.837% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 5.286% | 77.06% | 100%
Floorspace % | FCZ17 Tot | 0% | 0% | 3.806% | 0% | 0% | 10.15% | 0% | 0% | 0% | 0% | 0% | 86.04% | 100%
Calculation Method | Statewide/ Utility/ FCZ | 0% | 0%< X <10% | 10%<= X <20% | 20%<= X <30% | 30%<= X <40% | 40%<= X <50% | 50%<= X <60% | 60%<= X <70% | 70%<= X <80% | 80%<= X <90% | 90%<= X <100% | 100% | Total | ← % Floorspace Conditioned
Floorspace (k SqFt) | Statewide | 13190.1368 | 9575.6256 | 6119.2702 | 6895.5342 | 8365.1544 | 13510.004 | 7738.4428 | 13065.4804 | 11750.5687 | 14111.439 | 20097.3942 | 646734.4723 | 771153.5227
Floorspace (k SqFt) | FCZ01 Tot | 3675.052 | 2676.861 | 0 | 1420.0908 | 615.5574 | 372.3475 | 420.031 | 2377.5346 | 1498.3385 | 1742.7953 | 3740.432 | 101056.5374 | 119595.5776
Floorspace (k SqFt) | FCZ02 Tot | 0 | 2044.1517 | 0 | 44.7071 | 124.4193 | 2171.6186 | 845.4998 | 1229.1076 | 710.6892 | 863.1584 | 769.2555 | 24814.3897 | 33616.997
Floorspace (k SqFt) | FCZ03 Tot | 0 | 0 | 0 | 0 | 0 | 159.1551 | 0 | 295.7365 | 191.9728 | 0 | 225.6969 | 8532.6027 | 9405.1639
Floorspace (k SqFt) | FCZ04 Tot | 27.946 | 1317.908 | 379.4236 | 326.0645 | 1933.8949 | 194.3517 | 591.103 | 847.7669 | 1212.7893 | 1985.0972 | 923.5369 | 35509.4462 | 45249.3283
Floorspace (k SqFt) | FCZ05 Tot | 0 | 0 | 147.4957 | 247.3025 | 0 | 2351.1785 | 1089.589 | 357.8385 | 457.4944 | 357.6643 | 1901.6772 | 36242.8655 | 43153.1055
Floorspace (k SqFt) | FCZ06 Tot | 546.4687 | 50.8902 | 886.5544 | 195.4882 | 0 | 993.7695 | 0 | 587.1465 | 138.108 | 124.402 | 2234.5356 | 29197.4617 | 34954.825
Floorspace (k SqFt) | FCZ07 Tot | 1270.6427 | 347.3723 | 119.1494 | 673.0197 | 1535.2878 | 1169.945 | 825.2168 | 2806.7018 | 2617.9586 | 5363.2174 | 1530.1294 | 149869.4365 | 168128.0774
Floorspace (k SqFt) | FCZ08 Tot | 0 | 0 | 398.2517 | 283.6531 | 869.6064 | 240.2792 | 72.7717 | 693.9044 | 402.5306 | 108.0903 | 0 | 21160.7836 | 24229.8711
Floorspace (k SqFt) | FCZ09 Tot | 0 | 0 | 0 | 0 | 0 | 278.1164 | 0 | 606.4039 | 131.2819 | 321.6995 | 464.4416 | 9890.5282 | 11692.4715
Floorspace (k SqFt) | FCZ10 Tot | 0 | 0 | 699.0171 | 0 | 255.9127 | 1897.04 | 264.3465 | 178.3734 | 596.553 | 235.2696 | 368.0715 | 29169.4841 | 33664.068
Floorspace (k SqFt) | FCZ11 Tot | 0 | 0 | 284.9205 | 0 | 0 | 0 | 506.075 | 461.0774 | 0 | 183.8424 | 441.826 | 33710.4499 | 35588.1912
Floorspace (k SqFt) | FCZ12c Tot | 1093.4225 | 233.4604 | 1068.4655 | 1741.3581 | 2165.3483 | 377.6777 | 1366.1411 | 535.0183 | 1702.0395 | 641.3536 | 1626.7497 | 53888.5178 | 66439.5525
Floorspace (k SqFt) | FCZ12i Tot | 86.9728 | 1163.5886 | 550.0469 | 0 | 0 | 711.0135 | 572.0832 | 218.3664 | 448.6872 | 80.3592 | 911.0122 | 16385.4496 | 21127.5797
Floorspace (k SqFt) | FCZ13 Tot | 47.0612 | 124.5148 | 696.2057 | 1588.9959 | 410.3819 | 373.1077 | 764.9091 | 1160.2397 | 1003.3424 | 1337.3651 | 1824.5008 | 19769.7001 | 29100.3243
Floorspace (k SqFt) | FCZ16 Tot | 5725.53 | 1096.3295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2042.9965 | 29785.0972 | 38649.9531
Floorspace (k SqFt) | FCZ17 Tot | 0 | 0 | 557.0845 | 0 | 0 | 1485.9741 | 0 | 0 | 0 | 0 | 0 | 12594.0091 | 14637.0677

## Water Heater
Water Heater - OfficeSmall
Vintage | WH Type | Efficiency | Tank Volume (gal) | Tank Loss | Unit | Source
Existing | Gas | 0.8 | 50 | 855.5146 | Btu/hr | Loss per hour, 10 CFR 431.110(a) Table F-4
New Construction | Gas | 0.8 | 50 | 855.5146 | Btu/hr
Peak Hot Water Consumption
Space Name | Baseline WH Type [T24, 2022, Appendix 5.4A , sheet: "2022 SpaceFuncData-Input"] | Total Area (ft²) | Number of People | Hot Water Usage Specification (gal/hr per person) [T24, 2022, Appendix 5.4A , sheet: "2022 SpaceFuncData-Input"] | Peak Hot Water Usage (gal/hr) | Peak Hot Water Usage (gal/min)
Open_Office_N | Gas | 912.6975 | 4.5635 | 0.18 | 0.82143 | 0.01369
Closed_Office_W | Gas | 908.46 | 4.5423 | 0.18 | 0.81761 | 0.013627
Closed_Office_E | Gas | 908.46 | 4.5423 | 0.18 | 0.81761 | 0.013627
Conference | Gas | 456.35 | 15.0596 | 0.09 | 1.3554 | 0.022589
Lobby_Lounge | Gas | 456.35 | 4.5635 | 0.09 | 0.41071 | 0.0068452
Storage | Gas | 743.8879 | 1.4878 | 0 | 0 | 0
Mechanical_Electrical | Gas | 114.23 | 0 | 0.18 | 0 | 0
Restroom | Gas | 224.28 | 0 | 0 | 0 | 0
Break_CopyRoom | Gas | 110.05 | 3.6317 | 0.09 | 0.32685 | 0.0054475
Corridor_W | Gas | 122.26 | 0.6113 | 0 | 0 | 0
Corridor_N | Gas | 211.39 | 1.0569 | 0 | 0 | 0
Corridor_E | Gas | 122.26 | 0.6113 | 0 | 0 | 0
Corridor_S | Gas | 211.39 | 1.0569 | 0 | 0 | 0
Attic | Gas | 6114.3047 | 0 | 0 | 0 | 0
Water Heater Capacity, Tank Capacity, and Tank Loss
WH Type | Peak Hot Water Usage (gal/hr) | Heat Output (Btu/hr) [ACM, 2025, 5.9.2: Rated capacity section] | WH Capacity (Btu/hr) [ACM, 2025, 5.9.2: Rated capacity section] | Required Energy Input (Btu/hr) | Storage Volume (gal) | Standby Loss |  | Off/On Cycle Loss Coefficient to Ambient Temp (Btu/h-F) | Source
Gas Storage WH | 125 | 82877 | 49726.2 | 62157.75 | 50 | 855.5146 | Btu/hr | 12.5811 | Standby loss equation: Title 20, §1605.1 Table F-4 WH capacity equation: ACM, 2025, 5.9.2: Rated capacity section)
Electric resistance WH |  |  | 0 | 0 | 0 | 0 | %/hr | 0
Total | 125 |  |  |  | 50
Design supply temperature (F) | 135 | Ref: T24 2022 - Appendix 5.4B |  |  | Standby Loss for Existing | 855.5146 | (Btu/hr) | 12.5811
Cold Water supply temperature (F) | 55 | Ref: ACM, 2025, 5.9.2: Rated capacity section
WH system factor | 0.6 | Ref: ACM, 2025, 5.9.2: Rated capacity section
Reheat multiplier | 0.4 | Ref: ACM, 2025, 5.9.2: Storage Volume
* The 0.40 multiplier is a storage sizing factor used to account for the fact that the water heater doesn't need to store the full peak hour demand—it can reheat water during that time. This factor assumes that the heater will recover part of the hot water used during the peak hour, so only 40% of the peak hour demand needs to be stored at any given moment.
Ambient temp | 68
Delta T | 67
Background Data [To be deleted prior to publication]
Water use: | PNNL (for Core zone) | DEER | CEC
peak flow rate (gal/min) | 0.06416 | 0.0322 for N&S ZN - 0.0192 for E&W ZN | 0.0242 for Core ZN- 0.0109 for two ZN - 0.0183 for two other ZN | NOR Flow rate schedule follows CEC
Target Temperature | 120 | 135 | 135
Sensible Fraction | 0.2 | 0.2 | N/A
Latent Fraction | 0.05 | 0.05 | N/A
CEUS 2022 data | Water Heater
% of total impacted floor area | 92.96%
Dominated system | Package System / Heat Pump
Fuel and Share | 49.9% Electric and 49.1% Gas

## Interior Lights
Interior Lighting - OfficeSmall
Space Type | New Construction |  |  | Existing |  |  | Note
| LPD (W/ft²) | Additional LPD for Portable Lighting (W/ft²) | Source | LPD (W/ft²) | Additional LPD for Portable Lighting (W/ft²) | Source
Office Area (>250 square feet) | 0.6 |  | T24, part 6, 2025, Table 140.6 C Technology : LED | 0.75 |  | T24, part 6, 2013, Table 140.6 C Technology: 59% LED, 31% halogen, 7% CFL (Comstock 2023)
Convention, Conference, Multipurpose and Meeting Area | 0.75 |  |  | 1.4
Lobby, Main Entry | 0.7 |  |  | 1.5
Storage (General) | 0.4 |  |  | 0.6
Electrical, Mechanical, Telephone Rooms | 0.4 |  |  | 0.7
Restrooms | 0.6 |  |  | 0.6
Lounge, Breakroom, or Waiting Area | 0.55 |  |  | 1.1 |  |  | 2013 LPD is for "Lounge" area
Corridor Area | 0.4 |  |  | 0.6
Attic
According to CEUS, more than 80% of existing small office upgraded their lighting system between 2014-2018 and it conflicts the lighting generation considered by Comstock.
Whole Building method
| 2025 | 2013
LPD for Office Building ((W/ft²) | 0.6 | 0.8 | Ref: T24, Table 140.6 B
Background Data [To be deleted24:77 prior to publication]
Ref: T24- Table 140.6-C (office area >250nSF)
T24 Code cycle | Lighting density for office Buildings: (complete building Method) | Lighting density for office area >250 sf Floor area Method | Table | Note
2025 | 0.6 | 0.6, 0.2 (additional) | Table 140.6 C
2022 | 0.6 | 0.6, 0.2 (additional)
2019 | 0.65
2016 | 0.8
2013 | 0.8 | 0.75
2010 | 0.85
2008 | 0.085 | 0.9 | Table 146-E
2005 |  | 1.2
TBD: Review the CASE report on 2016 for lighting
| Lighting density for office area >250 sf (Watts/ft²) | Additional lighting power for Table lighting (Watts/ft²) |  | T24, part 6 2022 | file://carcgl.com/amer/NOR/Groups/CodesStds/Standards/California/2022%20Building%20Energy%20Efficiency%20Standards%20for%20Residential%20and%20Nonresidential%20Buildings.pdf
Title 24, 2016 | 0.8 |  |  | T24, part 6 2019 | file://carcgl.com/amer/NOR/Groups/CodesStds/Standards/California/2016-CEC-400-2015-037-CMF.pdf
| 0.75 (1 for office <=250) |  |  | T24, part 6 2016 | file://carcgl.com/amer/NOR/Groups/CodesStds/Standards/California/2016-CEC-400-2015-037-CMF.pdf
1.2
0.6
0.55
| 0.95 | 0.5
| 0.9 | 0.5
0.6
0.6
0.6
Review of existing prototype
Prototype/Source | Downloaded on | Zone | Light Intensity | Unit | Total intensity multipliers | Total lighting intensity | Core/Perims area ratio |  |  | Working days | 249
DEER | 2024-07-01 | Core | 6.7006 | W/m2 | 2238.1 | 14996.5719 | 45.79% |  |  | Saturday | 52
|  | Perimeter zone | 13.4605 | W/m2 | 2238.1 | 30125.9728 |  |  |  | Sunday | 52
PNNL | 2024-02-01 | All | 6.1813 | W/m2 | 2468.4141 | 15257.8945 | 41.4% |  |  | Holiday | 11
CEC (CBECC 2023) | 2024-06-01 | All | 6.4583 | W/m2 | 2238.1 | 14454.4247 | 41.4%
Interior lighting Schedules (existing prototypes extracted from the idf files (presented below)
| CEC |  |  |  | DEER |  |  |  | PNNL
Hour | CEC-Weekday | CEC-Saturday | CEC-Sunday |  | DEER- Weekday | DEER- Saturday | DEER-Otherday |  | PNNL-Weekday | PNNL-Saturday | PNNL-Otherday
1 | 0.05 | 0.05 | 0.05 |  | 0.05 | 0.05 | 0.05 |  | 0.12093 | 0.12093 | 0.12093
2 | 0.05 | 0.05 | 0.05 |  | 0.05 | 0.05 | 0.05 |  | 0.12093 | 0.12093 | 0.12093
3 | 0.05 | 0.05 | 0.05 |  | 0.05 | 0.05 | 0.05 |  | 0.12093 | 0.12093 | 0.12093
4 | 0.05 | 0.05 | 0.05 |  | 0.05 | 0.05 | 0.05 |  | 0.12093 | 0.12093 | 0.12093
5 | 0.05 | 0.05 | 0.05 |  | 0.05 | 0.05 | 0.05 |  | 0.12093 | 0.12093 | 0.12093
6 | 0.1 | 0.05 | 0.05 |  | 0.1 | 0.05 | 0.05 |  | 0.15453 | 0.12093 | 0.12093
7 | 0.1 | 0.1 | 0.05 |  | 0.1 | 0.1 | 0.05 |  | 0.15453 | 0.12093 | 0.12093
8 | 0.3 | 0.1 | 0.05 |  | 0.3 | 0.1 | 0.05 |  | 0.60466 | 0.12093 | 0.12093
9 | 0.65 | 0.3 | 0.05 |  | 0.65 | 0.3 | 0.05 |  | 0.60466 | 0.12093 | 0.12093
10 | 0.65 | 0.3 | 0.05 |  | 0.65 | 0.3 | 0.05 |  | 0.60466 | 0.12093 | 0.12093
11 | 0.65 | 0.3 | 0.05 |  | 0.65 | 0.3 | 0.05 |  | 0.60466 | 0.12093 | 0.12093
12 | 0.65 | 0.3 | 0.05 |  | 0.65 | 0.3 | 0.05 |  | 0.60466 | 0.12093 | 0.12093
13 | 0.65 | 0.15 | 0.05 |  | 0.65 | 0.15 | 0.05 |  | 0.53748 | 0.12093 | 0.12093
14 | 0.65 | 0.15 | 0.05 |  | 0.65 | 0.15 | 0.05 |  | 0.60466 | 0.12093 | 0.12093
15 | 0.65 | 0.15 | 0.05 |  | 0.65 | 0.15 | 0.05 |  | 0.60466 | 0.12093 | 0.12093
16 | 0.65 | 0.15 | 0.05 |  | 0.65 | 0.15 | 0.05 |  | 0.60466 | 0.12093 | 0.12093
17 | 0.65 | 0.15 | 0.05 |  | 0.65 | 0.15 | 0.05 |  | 0.60466 | 0.12093 | 0.12093
18 | 0.35 | 0.05 | 0.05 |  | 0.35 | 0.05 | 0.05 |  | 0.40983 | 0.12093 | 0.12093
19 | 0.3 | 0.05 | 0.05 |  | 0.3 | 0.05 | 0.05 |  | 0.28218 | 0.12093 | 0.12093
20 | 0.3 | 0.05 | 0.05 |  | 0.3 | 0.05 | 0.05 |  | 0.28218 | 0.12093 | 0.12093
21 | 0.2 | 0.05 | 0.05 |  | 0.2 | 0.05 | 0.05 |  | 0.21499 | 0.12093 | 0.12093
22 | 0.2 | 0.05 | 0.05 |  | 0.2 | 0.05 | 0.05 |  | 0.21499 | 0.12093 | 0.12093
23 | 0.1 | 0.05 | 0.05 |  | 0.1 | 0.05 | 0.05 |  | 0.15453 | 0.12093 | 0.12093
24 | 0.05 | 0.05 | 0.05 |  | 0.05 | 0.05 | 0.05 |  | 0.12093 | 0.12093 | 0.12093
Sum of intensity multiplier | 8.1 | 2.8 | 1.2 |  | 8.1 | 2.8 | 1.2 |  | 8.5728 | 2.9024 | 2.9024
[8 empty] | gen5_led | gen2_t8_halogen | gen4_led | gen3_t5_cfl | gen1_t12_incandescent
ComStock 2023 | Lighting Generation | [5 empty] | lumen per w | 130 | 20 | 110 | 70 | 15
| gen5_led | gen2_t8_halogen | gen4_led | gen3_t5_cfl | gen1_t12_incandescent |  | W/sf | 0.50769 | 3.3 | 0.6 | 0.94286 | 4.4
Floor area Fraction | 9.437% | 33.99% | 47.06% | 6.528% | 2.99% |  | equivalent W/sf to provide lumen like LED gen 4 | 0.04791 | 1.1216 | 0.28235 | 0.061552 | 0.13156 | 1.6449
CEUS 2022 ( Mostly gathered in 2018) | % LED
| 0% | <=10% | <=20% | <=30% | <=40% | <=50% | <=60% | <=70% | <=80% | <=90% | <100% | 100% | Not Available
Floorspace (statewide) | 45.38% | 3.898% | 2.567% | 3.829% | 1.303% | 3.954% | 0.5909% | 2.02% | 4.495% | 3.835% | 0.5117% | 27.3% | 0.3106%
CEUS 2022 ( Mostly gathered in 2018) | % LED 0%: % Upgraded
| Before2004 | 2004-2013 | 2014-2018 | Not Available
Floorspace (statewide) | % LED 0%: 0%; % LED <=10%: 0.6172%; % LED <=20%: 79.32%; % LED <=30%: 20.07%; % LED <=40%: It shows lighting has been upgraded in less than 5 years
Note on B46: Yousefi, Fatemeh: Interface area probably got updated with new technologies

## Ext Lighting
Exterior Lighting - OfficeSmall
Motion Controlled Luminaires (W) | Non-motion Controlled Luminaires (W) | Total (W) | Source
382.2628 | 155.1514 | 537.4142 | T24, 2022 & 2025 2019 Outdoor Lighting CASE report PNNL 90.1-2010 TSD
Exterior Lighting
Items (Assume LZ2) | Assumptions [2019 Outdoor Lighting CASE Report & PNNL 90.1-2010 TSD] |  | Unit | Lighting Power Allowance [T24, 2025, Table 140.7-A & 140.7-B] | Unit | Exterior Lighting Power (W)
IWA (Initial Wage Allowance) |  |  |  | 200 | (W) | 200
Parking area | 400 ft² for every parking space 1 parking space per 250 ft² of gross building area | 8803.3047 | (ft²) | 0.019 | (W/ft²) | 167.2628
Building Entrance | 2 building entrance (1 per 10,000 ft² footprint) | 1 | (count) | 15 | (W/ea) | 15
Hardscape Ornamental Light | 0.1 ft² per 1 ft² of gross building area for hardscape ornamental light | 550.2065 | (ft²) | 0.007 | (W/ft²) | 3.8514
Building façade | 0.1 W per ft² of facade area Façade Area* = Perimeter × 0.5 × height (30 ft is the max height that is lit) The 0.5 factor assumes that only half of the perimeter walls are lit. -Formula ia developed based on the 2019 Outdoor Lighting CASE report | 1513 | (ft²) | 0.1 | (W/ft²) | 151.3
Motion controlled Luminaires | [5 empty] | 382.2628
Non-motion-controlled Luminaires | [5 empty] | 155.1514
Total | [5 empty] | 537.4142
*Developed based on 2019 Outdoor Lighting CASE Report
Perimeter (ft) | 302.6
Total floor area (ft²) | 5502.0654
Floors (above ground) | 1
Background Data [To be deleted prior to publication]
PNNL
NonMotion Control | Motion Control
from 6:00 am until 12 am: 1 Rest: 0 | from 6 am-until 7 pm: 1 Rest: 0.5
Exterior Lighting
Ref: T24- Table 140.6-C (office area >250 SF)
T24 Code cycle | Lighting for parking area | Daylight Adaptation Zones**
2022 | 0.1 | 1
2019 | 0.1 | 0.5
2016 | 0.14 | 0.6
**Daylight Adaptation Zones shall be no farther than 66 feet from the entrance to the parking garage
Exterior Lighting - OfficeSmall (CEUS 2022 data)
Prototype | CZ | Exterior Lighting Saturation
OfficeSmall | 1 | 71.92%
| 2 | 79.76%
| 3 | 68.67%
| 4 | 68.67%
| 5 | 66.51%
| 6 | 61.36%
| 7 | 55.43%
| 8 | 60.37%
| 9 | 63.2%
| 10 | 53.26%
| 11 | 67.98%
| 12 | 69.87%
| 13 | 69.52%
| 14 | 58.74%
| 15 | 51.51%
| 16 | 61.77%
penetration for exterior lighting in small office is 83% according to CEUS 2022 (Appendix K). We set the schedule to fulfill something around 0.75 .
Ref: CEUS 2022 dataset
| DEER OFS Prototype -7/2024 | PNNL OfficeSmall 02-2024 |  |  | CEC | Comstock (Case 5307)
Exterior Lights W | None | 514.92 | 144.07 | 88.49 | None | 667.46 (Façade) | 264 (Main entry) | 88 (Doors) | 162.57 (parking area and drivers)
Schedule |  | 0-6: 0.5 | 0-6: 0.5 | 0-5:0 |  | Always On | Always On | Always On | Always On
|  | 6-19:1 | 6-24: 1 | 6-24: 1
20-24: 0.5

## Equipment
Equipment - OfficeSmall
Space Name | Plug load Power Density (W/ft²) | Gas Power Density (Btu/hr-ft²) | Refrigeration Power Density (W/ft²) | Source
Office Area (>250 square feet) | 0.7 |  |  | Plug load and schedules project with CEC, 2025
Convention, Conference, Multipurpose and Meeting Area | 0.8 |  |  | T24 2022 - Appendix 5.4A
Lobby, Main Entry | 0.5
Storage (General) | 0.2
Electrical, Mechanical, Telephone Rooms | 3
Restrooms | 0
Lounge, Breakroom, or Waiting Area | 0.5
Corridor Area | 0

## Schedules
Schedules - OfficeSmall
Zone | Schedule Category | Schedule | Source | Type | Hour
[5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
All zones | Office | Occupancy | T24 2022 - Appendix 5.4B, [Office] Updated base on Plug load and schedules project with CEC, 2025 | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
All zones | Office | Lights | T24 2022 - Appendix 5.4B, [Office] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.35 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
All zones | Office | ElecEquipment | Plug load and schedules project with CEC, 2025 | Weekday | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.74 | 0.87 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.5 | 0.45 | 0.45 | 0.45
|  |  |  | Saturday | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43
|  |  |  | Sunday | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43
All zones | Office | HVACAvail | T24 2022 - Appendix 5.4B, [Office] Updated base on Plug load and schedules project with CEC, 202 | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
All zones | Office | ServiceHotWater | T24 2022 - Appendix 5.4B, [Office] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.12 | 0.14 | 0.07 | 0.07 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05
|  |  |  | Sunday | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04
All zones | Office | Infiltration | T24 2022 - Appendix 5.4B, [Office] Updated base on Plug load and schedules project with CEC, 202 | Weekday | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
All zones | Office | HtgSetpt |  | Weekday | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
|  |  |  | Saturday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  |  | Sunday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
All zones | Office | ClgSetpt |  | Weekday | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
|  |  |  | Saturday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
|  |  |  | Sunday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
Corridors | Office | HtgSetpt_Corridor |  | Weekday | 60 | 60 | 60 | 60 | 60 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65
|  |  |  | Saturday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  |  | Sunday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Corridors | Office | ClgSetpt_Corridor |  | Weekday | 85 | 85 | 85 | 85 | 85 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78
|  |  |  | Saturday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
|  |  |  | Sunday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
Other
| Building | ExtLightingNonMotionCtrl |  | Weekday | bar: Hour 1 to Hour 24
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
| Building | ExtLightingMotionCtrl |  | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Office | Building | FunctionalAreaPeopleActivityLevel | Based on Activilty level schedules in CEC Prototypes | Weekday | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
|  |  |  | Saturday | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
|  |  |  | Sunday | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
Conference room | Building | MeetingAreaPeopleActivityLevel | Based on Activilty level schedules in CEC Prototypes | Weekday | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2
|  |  |  | Saturday | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2
|  |  |  | Sunday | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2
Corridor, Lobby, Restroom, Mech, Storage, Break | Building | CommonAreaPeopleActivityLevel | Based on Activilty level schedules in CEC Prototypes | Weekday | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5
|  |  |  | Saturday | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5
|  |  |  | Sunday | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5
Background Data [To be deleted prior to publication] | bar: Hour 1
| Equipment | PNNL | Office Zones | Weekday | 0.40948 | 0.40948 | 0.40948 | 0.40948 | 0.40948 | 0.40948 | 0.47975 | 0.47975 | 0.95951 | 0.95951 | 0.95951 | 0.95951 | 0.90193 | 0.95951 | 0.95951 | 0.95951 | 0.95951 | 0.47975 | 0.1919 | 0.1919 | 0.1919 | 0.1919 | 0.1919 | 0.16379
|  |  |  | Saturday | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379
|  |  |  | Sunday | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379
Operating Schedule
| System Capacity fraction | Developed based on CEC and CEUS | Office Zones | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.7 | 0.5 | 0.3 | 0.2 | 0.2 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.005 | 0 | 0 | 0 | 0 | 0
Sunday
Alternative HVAC System Operating
| Alternative HVAC System Operating | Developed based on CEC schedules and CEUS operating hours | Office Closed Zones | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Office Open Zones | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | ElecEquipment | CEC Small Office | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  | ElecEquipment | PNNL Small Office | Weekday | 0.40948 | 0.40948 | 0.40948 | 0.40948 | 0.40948 | 0.40948 | 0.47975 | 0.47975 | 0.95951 | 0.95951 | 0.95951 | 0.95951 | 0.90193 | 0.95951 | 0.95951 | 0.95951 | 0.95951 | 0.47975 | 0.1919 | 0.1919 | 0.1919 | 0.1919 | 0.1919 | 0.16379
|  |  |  | Saturday | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379
|  |  |  | Sunday | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379 | 0.16379
|  | ElecEquipment | DEER Small Office | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05

## Energy Usage
CalBEM Energy Consumption - OfficeSmall | [7 empty] | National Average (EnergyStar Portfolio Manager) |  |  |  |  | CEUS Energy Consumption - OfficeSmall
Prototype | CZ | CalBEM Electricity EUI (KBTU/ft²) | CalBEM Gas EUI (KBTU/ft²) | CalBEM Total EUI (KBTU/ft²) | New Construction Electricity EUI (KBTU/ft²) | New Construction Gas EUI (KBTU/ft²) | New Construction Total EUI (KBTU/ft²) | National Average | Acceptable RangeRange (25% Higher) | Acceptable RangeRange (25% Lower) | National Average Acceptable Range | Zip code | Prototype | CZ | Total Floorspace (Thousand of ft2) | CEUS 2022 Electric Energy Intensity (kWh/ft²) | CEUS 2022 Annual Gas Intensity (kWh/ft²) | CEUS 2022 Total EUI (kBtu/ft²) | Acceptable Range (25% Higher) | Acceptable Range (25% Lower) | CEUS 2022 Acceptable Range
HotelSmall | 1 | 37.4 | 33.4 | 70.8 | 33.6 | 2.8 | 36.4 | 61.7 | 77.125 | 46.275 | 30.85 | 95521 | OfficeSmall | 1 | 12266 | 9.77 | 4.88 | 49.9858 | 62.4822 | 37.4893 | 24.9929
| 2 | 45 | 23.6 | 68.6 | 35.3 | 2.7 | 38 | 67.5 | 84.375 | 50.625 | 33.75 | 95476 |  | 2 | 27044 | 7.5 | 5.6 | 44.6972 | 55.8715 | 33.5229 | 22.3486
| 3 | 38.7 | 16.5 | 55.3 | 32.9 | 2.7 | 35.6 | 64.2 | 80.25 | 48.15 | 32.1 | 94612 |  | 3 | 84735 | 8.62 | 7.47 | 54.8991 | 68.6239 | 41.1743 | 27.4495
| 4 | 47.6 | 20.7 | 68.3 | 37.8 | 2.7 | 40.5 | 69.7 | 87.125 | 52.275 | 34.85 | 93446 |  | 4 | 41723 | 8.85 | 7.21 | 54.7967 | 68.4959 | 41.0975 | 27.3984
| 5 | 35.2 | 14.6 | 49.8 | 33.4 | 2.7 | 36.1 | 61.6 | 77 | 46.2 | 30.8 | 93455 |  | 5 | 11347 | 6.73 | 10.64 | 59.2664 | 74.0831 | 44.4498 | 29.6332
| 6 | 43.2 | 6.8 | 50 | 34.2 | 2.6 | 36.8 | 71 | 88.75 | 53.25 | 35.5 | 93550 |  | 6 | 59004 | 8.01 | 3.98 | 40.9099 | 51.1373 | 30.6824 | 20.4549
| 7 | 43.4 | 5.5 | 48.9 | 34.7 | 2.6 | 37.3 | 66.9 | 83.625 | 50.175 | 33.45 | 92101 |  | 7 | 54999 | 10.61 | 6.8 | 59.4029 | 74.2537 | 44.5522 | 29.7015
| 8 | 50.4 | 7 | 57.4 | 41.3 | 2.6 | 43.9 | 67.8 | 84.75 | 50.85 | 33.9 | 92831 |  | 8 | 86435 | 7.9 | 3.79 | 39.8863 | 49.8579 | 29.9147 | 19.9431
| 9 | 50 | 8.6 | 58.5 | 39.4 | 2.6 | 42 | 67.9 | 84.875 | 50.925 | 33.95 | 91505 |  | 9 | 113713 | 8.3 | 4.16 | 42.5135 | 53.1419 | 31.8851 | 21.2568
| 10 | 47.6 | 8.6 | 56.2 | 41.1 | 2.6 | 43.7 | 68.3 | 85.375 | 51.225 | 34.15 | 92501 |  | 10 | 79023 | 9.01 | 4.25 | 45.2431 | 56.5539 | 33.9323 | 22.6216
| 11 | 49.8 | 21.8 | 71.6 | 43.3 | 2.7 | 45.9 | 70.5 | 88.125 | 52.875 | 35.25 | 96080 |  | 11 | 37485 | 11.12 | 5.05 | 55.172 | 68.965 | 41.379 | 27.586
| 12 | 46.1 | 20.8 | 66.9 | 39.9 | 2.7 | 42.6 | 69.8 | 87.25 | 52.35 | 34.9 | 95814 |  | 12 | 150207 | 10.53 | 5.82 | 55.7862 | 69.7327 | 41.8396 | 27.8931
| 13 | 50.1 | 16.1 | 66.2 | 43.1 | 2.6 | 45.8 | 70.2 | 87.75 | 52.65 | 35.1 | 93721 |  | 13 | 50089 | 10.6 | 4.34 | 50.9753 | 63.7191 | 38.2315 | 25.4876
| 14 | 49.7 | 20.7 | 70.4 | 43.9 | 2.7 | 46.5 | 71 | 88.75 | 53.25 | 35.5 | 93550 |  | 14 | 17716 | 7.65 | 3.93 | 39.511 | 49.3887 | 29.6332 | 19.7555
| 15 | 57.5 | 4.6 | 62.2 | 49.6 | 2.5 | 52 | 69.7 | 87.125 | 52.275 | 34.85 | 92262 |  | 15 | 41833 | 9 | 2.08 | 37.805 | 47.2562 | 28.3537 | 18.9025
| 16 | 43.9 | 34 | 77.9 | 42.3 | 2.8 | 45 | 72.5 | 90.625 | 54.375 | 36.25 | 95715 |  | 16 | 74950 | 9.33 | 4.53 | 47.2903 | 59.1129 | 35.4677 | 23.6452
Ref: CEUS 2022 Report
And converted FZ level data to CZ level
Background Data [To be deleted prior to publication]
[13 empty] | Building-type | Planning Area | Floorspace (ksqft) | Electric Energy Intensity (kWh/sqft) | Electricity Usage (GWh) | Percent of Total | Annual Gas Intensity (kBTU/ft²) | Gas Usage (Therms) | Percent of Therms
[13 empty] | Office, Small | Statewide | 729220.6429 | 8.9108 | 6497.9293 | 6.947% | 18.4127 | 134268858.3189 | 5.967%
[13 empty] | Office, Small | FCZ1 | 119595.5776 | 9.1607 | 1095.5807 | 5.112% | 22.8529 | 27331076.8434 | 6.133%
[13 empty] | Office, Small | FCZ2 | 33616.997 | 7.4854 | 251.6359 | 9.627% | 19.118 | 6426897.9091 | 9.685%
[13 empty] | Office, Small | FCZ3 | 9405.1639 | 12.2478 | 115.1927 | 13.49% | 28.2865 | 2660392.7332 | 15.55%
[13 empty] | Office, Small | FCZ4 | 45237.8174 | 10.2381 | 463.1475 | 8.697% | 12.1512 | 5496954.8477 | 5.829%
[13 empty] | Office, Small | FCZ5 | 43153.1055 | 11.1201 | 479.8668 | 8.515% | 15.1928 | 6556179.8848 | 6.967%
[13 empty] | Office, Small | FCZ6 | 34954.825 | 6.7295 | 235.2296 | 10.09% | 36.4148 | 12728730.9275 | 16.68%
[13 empty] | Office, Small | FCZ7 | 168128.0774 | 7.4809 | 1257.7502 | 6.468% | 10.4627 | 17590769.119 | 3.302%
[13 empty] | Office, Small | FCZ8 | 24229.8711 | 7.0998 | 172.0269 | 8.293% | 9.9915 | 2420917.8031 | 4.093%
[13 empty] | Office, Small | FCZ9 | 11692.4715 | 8.278 | 96.7898 | 7.394% | 13.051 | 1525983.122 | 5.307%
[13 empty] | Office, Small | FCZ10 | 33664.068 | 7.4908 | 252.1703 | 4.752% | 15.5313 | 5228482.7789 | 4.02%
[13 empty] | Office, Small | FCZ11 | 35588.1912 | 8.9209 | 317.4788 | 7.214% | 6.7586 | 2405260.6733 | 2.306%
[13 empty] | Office, Small | FCZ12c | 66439.5525 | 10.7565 | 714.6554 | 10.32% | 24.2601 | 16118298.1771 | 8.124%
[13 empty] | Office, Small | FCZ12i | 21127.5797 | 10.1661 | 214.7859 | 7.938% | 19.8576 | 4195435.2736 | 7.714%
[13 empty] | Office, Small | FCZ13 | 29100.3243 | 10.4593 | 304.3703 | 7.134% | 28.2419 | 10874612.0991 | 12.15%
[13 empty] | Office, Small | FCZ16 | 38649.9531 | 10.3339 | 399.4066 | 5.739% | 12.2524 | 10915477.8402 | 5.086%
[13 empty] | Office, Small | FCZ17 | 14637.0677 | 8.7341 | 127.842 | 6.566% | 37.3694 | 1793388.2869 | 4.017%
Office, Small
[15 empty] | Floor Stock (kft²) |  |  |  | Annual Electric Usage (GWh) |  |  |  | Annual Gas Usage (MTherms) |  |  | Annual Electric Intensity (kWh/ft²) |  |  | Annual Gas Intensity (kBTU/ft²) |  |  | Annual Gas Intensity (kBTU/ft²)
[13 empty] | Planning Area & Forecast Zone | Building Type | Participating Utilities Only | Nonparticipating Utilities | Total |  | Participating Utilities Only | Nonparticipating Utilities | Total |  | Participating Utilities Only | Nonparticipating Utilities | Total | Participating Utilities Only | Nonparticipating Utilities | Total | Participating Utilities Only | Nonparticipating Utilities | Total | Participating Utilities Only | Nonparticipating Utilities | Total
[13 empty] | Statewide | Office, Small | 670485.3266 | 58735.3163 | 729220.6429 |  | 5984.2374 | 513.6919 | 6497.9293 |  | 125.3133 | 8.9555 | 134.2689 | 8.9252 | 8.7459 | 8.9108 | 18.6899 | 15.4769 | 18.4127 | 18.6899 | 15.2473 | 18.4127
[13 empty] | FCZ1 | Office, Small | 97897.9634 | 21697.6141 | 119595.5776 |  | 896.8151 | 198.7656 | 1095.5807 |  | 22.3725 | 4.9585 | 27.3311 | 9.1607 | 9.1607 | 9.1607 | 22.8529 | 22.8529 | 22.8529 | 22.8529 | 22.8529 | 22.8529
[13 empty] | FCZ2 | Office, Small | 31544.7817 | 2072.2154 | 33616.997 |  | 236.1246 | 15.5113 | 251.6359 |  | 6.0307 | 0.39617 | 6.4269 | 7.4854 | 7.4854 | 7.4854 | 19.118 | 19.118 | 19.118 | 19.118 | 19.118 | 19.118
[13 empty] | FCZ3 | Office, Small | 9125.8806 | 279.2833 | 9405.1639 |  | 111.7721 | 3.4206 | 115.1927 |  | 2.5814 | 0.079 | 2.6604 | 12.2478 | 12.2478 | 12.2478 | 28.2865 | 28.2865 | 28.2865 | 28.2865 | 28.2865 | 28.2865
[13 empty] | FCZ4 | Office, Small | 38145.1802 | 7092.6372 | 45237.8174 |  | 390.5326 | 72.6148 | 463.1475 |  | 4.6351 | 0.86184 | 5.497 | 10.2381 | 10.2381 | 10.2381 | 12.1512 | 12.1512 | 12.1512 | 12.1512 | 12.1512 | 12.1512
[13 empty] | FCZ5 | Office, Small | 43068.6356 | 84.4699 | 43153.1055 |  | 478.9275 | 0.93931 | 479.8668 |  | 6.5433 | 0.012833 | 6.5562 | 11.1201 | 11.1201 | 11.1201 | 15.1928 | 15.1928 | 15.1928 | 15.1928 | 15.1928 | 15.1928
[13 empty] | FCZ6 | Office, Small | 34382.498 | 572.327 | 34954.825 |  | 231.3781 | 3.8515 | 235.2296 |  | 12.5203 | 0.20841 | 12.7287 | 6.7295 | 6.7295 | 6.7295 | 36.4148 | 36.4148 | 36.4148 | 36.4148 | 36.4148 | 36.4148
[13 empty] | FCZ7 | Office, Small | 154214.4222 | 13913.6553 | 168128.0774 |  | 1153.6634 | 104.0867 | 1257.7502 |  | 16.135 | 1.4557 | 17.5908 | 7.4809 | 7.4809 | 7.4809 | 10.4627 | 10.4627 | 10.4627 | 10.4627 | 10.4627 | 10.4627
[13 empty] | FCZ8 | Office, Small | 24229.8711 | 0 | 24229.8711 |  | 172.0269 | 0 | 172.0269 |  | 2.4209 | 0 | 2.4209 | 7.0998 | na | 7.0998 | 9.9915 | na | 9.9915 | 9.9915 | na | 9.9915
[13 empty] | FCZ9 | Office, Small | 11692.4715 | 0 | 11692.4715 |  | 96.7898 | 0 | 96.7898 |  | 1.526 | 0 | 1.526 | 8.278 | na | 8.278 | 13.051 | na | 13.051 | 13.051 | na | 13.051
[13 empty] | FCZ10 | Office, Small | 32492.2018 | 1171.8661 | 33664.068 |  | 243.3921 | 8.7782 | 252.1703 |  | 5.0465 | 0.18201 | 5.2285 | 7.4908 | 7.4908 | 7.4908 | 15.5313 | 15.5313 | 15.5313 | 15.5313 | 15.5313 | 15.5313
[13 empty] | FCZ11 | Office, Small | 23736.9431 | 11851.248 | 35588.1912 |  | 211.755 | 105.7238 | 317.4788 |  | 1.6043 | 0.80098 | 2.4053 | 8.9209 | 8.9209 | 8.9209 | 6.7586 | 6.7586 | 6.7586 | 6.7586 | 6.7586 | 6.7586
[13 empty] | FCZ12c | Office, Small | 66439.5525 | 0 | 66439.5525 |  | 714.6554 | 0 | 714.6554 |  | 16.1183 | 0 | 16.1183 | 10.7565 | na | 10.7565 | 24.2601 | na | 24.2601 | 24.2601 | na | 24.2601
[13 empty] | FCZ12i | Office, Small | 21127.5797 | 0 | 21127.5797 |  | 214.7859 | 0 | 214.7859 |  | 4.1954 | 0 | 4.1954 | 10.1661 | na | 10.1661 | 19.8576 | na | 19.8576 | 19.8576 | na | 19.8576
[13 empty] | FCZ13 | Office, Small | 29100.3243 | 0 | 29100.3243 |  | 304.3703 | 0 | 304.3703 |  | 10.8746 | 0 | 10.8746 | 10.4593 | na | 10.4593 | 37.3694 | na | 37.3694 | 37.3694 | na | 37.3694
[13 empty] | FCZ16 | Office, Small | 38649.9531 | 0 | 38649.9531 |  | 399.4066 | 0 | 399.4066 |  | 10.9155 | 0 | 10.9155 | 10.3339 | na | 10.3339 | 28.2419 | na | 28.2419 | 28.2419 | na | 28.2419
[13 empty] | FCZ17 | Office, Small | 14637.0677 | 0 | 14637.0677 |  | 127.842 | 0 | 127.842 |  | 1.7934 | 0 | 1.7934 | 8.7341 | na | 8.7341 | 12.2524 | na | 12.2524 | 12.2524 | na | 12.2524
[13 empty] | Statewide | Office, Small | 670485.3266 | 58735.3163 | 729220.6429 |  | 5984.2374 | 513.6919 | 6497.9293 |  | 125.3133 | 8.9555 | 134.2689 | 8.9252 | 8.7459 | 8.9108 | 18.6899 | 15.4769 | 18.4127 | 18.6899 | 15.2473 | 18.4127
[13 empty] | End Use | Planning Are | Sector | Percent Floorspace with End Use | Electric Fuel Share | Gas Fuel Share | Other Fuel Share | Saturation (Elect) | Saturations (Gas) | Saturations (Other Fuels) | <= The saturations here are the % of total floorspace with for each combination of end-use and fuel type.
[13 empty] | Air Compressors | Statewide | Office, Small | 15.53% | NA | NA | NA | 15.53% | 0% | 0%
[13 empty] | Cooking, Major | Statewide | Office, Small | 0.4289% | 37.36% | 62.22% | 0.4119% | 0.1603% | 0.2669% | 0.001767%
[13 empty] | Cooking, Minor | Statewide | Office, Small | 94.91% | 99.06% | 0.9397% | 0% | 94.02% | 0.8919% | 0%
[13 empty] | Cooling | Statewide | Office, Small | 89.97% | 99.95% | 0.03523% | 0.01201% | 89.93% | 0.0317% | 0.0108%
[13 empty] | Exterior Lighting | Statewide | Office, Small | 66.3% | NA | NA | NA | 66.3% | 0% | 0%
[13 empty] | Freezers, Commercial | Statewide | Office, Small | 5.974% | NA | NA | NA | 5.974% | 0% | 0%
[13 empty] | Frozen Floor Space | Statewide | Office, Small | 0.03089% | NA | NA | NA | 0.03089% | 0% | 0%
[13 empty] | Heating | Statewide | Office, Small | 91.16% | 43.38% | 55.53% | 1.095% | 39.54% | 50.62% | 0.9982% |  | 43=40/(40+51+1)
[13 empty] | Miscellaneous | Statewide | Office, Small | 93.41% | NA | NA | NA | 93.41% | 0% | 0%
[13 empty] | Motors | Statewide | Office, Small | 12.78% | NA | NA | NA | 12.78% | 0% | 0%
[13 empty] | Office Equipment | Statewide | Office, Small | 100% | NA | NA | NA | 100% | 0% | 0%
[13 empty] | Refrigerated Floor Space | Statewide | Office, Small | 0.009426% | NA | NA | NA | 0.009426% | 0% | 0%
[13 empty] | Refrigerators, Commercial | Statewide | Office, Small | 84.56% | NA | NA | NA | 84.56% | 0% | 0%
[13 empty] | Refrigerators, Residential | Statewide | Office, Small | 92.63% | NA | NA | NA | 92.63% | 0% | 0%
[13 empty] | Ventilation | Statewide | Office, Small | 93.07% | NA | NA | NA | 93.07% | 0% | 0%
[13 empty] | Water Heating | Statewide | Office, Small | 92.75% | 49.93% | 49.12% | 0.9491% | 46.31% | 45.56% | 0.8803%
[13 empty] | Utility & Forecast Zone | Building Type |  | Pre-1978 | 1978-1997 | 1998-2007 | 2008-2017 | 2018 | Year-Built Not Available
[13 empty] | Statewide | Office, Small | Gas | 39.51% | 26.43% | 15.46% | 9.386% | 0% | 9.217%
[13 empty] | 1 | Office, Small | Gas | 38.63% | 15.43% | 14.37% | 26.43% | 0% | 5.144%
[13 empty] | 2 | Office, Small | Gas | 44.3% | 30.62% | 14.13% | 6.289% | 0% | 4.664%
[13 empty] | 3 | Office, Small | Gas | 42.1% | 26.19% | 16.45% | 3.275% | 0% | 11.98%
[13 empty] | 4 | Office, Small | Gas | 10.8% | 31.17% | 47.61% | 5.425% | 0% | 4.99%
[13 empty] | 5 | Office, Small | Gas | 22.76% | 37.81% | 22.08% | 12.03% | 0% | 5.32%
[13 empty] | 6 | Office, Small | Gas | 33.76% | 14.06% | 19.78% | 1.255% | 0% | 31.14%
[13 empty] | 7 | Office, Small | Gas | 58.54% | 23.51% | 3.71% | 0.8445% | 0% | 13.4%
[13 empty] | 8 | Office, Small | Gas | 28.1% | 39.4% | 11.83% | 7.012% | 0% | 13.67%
[13 empty] | 9 | Office, Small | Gas | 14.87% | 23.01% | 27.81% | 12.04% | 0% | 22.27%
[13 empty] | 10 | Office, Small | Gas | 31.5% | 20.22% | 22.95% | 6.257% | 0% | 19.07%
[13 empty] | 11 | Office, Small | Gas | 42.2% | 15.52% | 18.17% | 6.39% | 0% | 17.72%
[13 empty] | 12c | Office, Small | Gas | 46.4% | 31.19% | 11.9% | 9.033% | 0% | 1.484%
[13 empty] | 12i | Office, Small | Gas | 31.29% | 43.82% | 4.71% | 6.68% | 0% | 13.5%
[13 empty] | 13 | Office, Small | Gas | 32.77% | 29.31% | 28.12% | 6.705% | 0.002414% | 3.098%
[13 empty] | 16 | Office, Small | Gas | 45.18% | 47.84% | 6.606% | 0% | 0.002414% | 0.374%
[13 empty] | 17 | Office, Small | Gas | 55.52% | 26.37% | 0% | 10.82% | 0.002414% | 7.291%
[13 empty] | Utility & Forecast Zone | Building Type |  | Pre-1978 | 1978-1997 | 1998-2007 | 2008-2017 | 2018 | Year-Built Not Available
[13 empty] | Statewide | Office, Small | Elec | 35.9% | 32.14% | 15.43% | 6.26% | 0.02232% | 10.25%
[13 empty] | 1 | Office, Small | Elec | 45.23% | 29.57% | 10.15% | 6.305% | 0% | 8.749%
[13 empty] | 2 | Office, Small | Elec | 36.15% | 36.91% | 15.94% | 6.388% | 0% | 4.609%
[13 empty] | 3 | Office, Small | Elec | 34.03% | 29.83% | 17.26% | 8.03% | 0% | 10.85%
[13 empty] | 4 | Office, Small | Elec | 10.03% | 32.47% | 45.12% | 4.515% | 0% | 7.868%
[13 empty] | 5 | Office, Small | Elec | 21.54% | 30.3% | 23.92% | 17.88% | 0% | 6.352%
[13 empty] | 6 | Office, Small | Elec | 30.27% | 32.86% | 8.135% | 5.906% | 0% | 22.83%
[13 empty] | 7 | Office, Small | Elec | 48.35% | 27.79% | 7.25% | 3.285% | 0.1153% | 13.21%
[13 empty] | 8 | Office, Small | Elec | 23.55% | 54.3% | 7.566% | 8.581% | 0% | 6.003%
[13 empty] | 9 | Office, Small | Elec | 21.81% | 21.84% | 19.02% | 11.07% | 0% | 26.27%
[13 empty] | 10 | Office, Small | Elec | 16.81% | 38.55% | 23.79% | 6.999% | 0% | 13.84%
[13 empty] | 11 | Office, Small | Elec | 16.56% | 28% | 29.46% | 9.732% | 0% | 16.25%
[13 empty] | 12c | Office, Small | Elec | 23.88% | 47.37% | 13.99% | 6.674% | 0% | 8.081%
[13 empty] | 12i | Office, Small | Elec | 30.49% | 30.47% | 12.63% | 2.558% | 0% | 23.86%
[13 empty] | 13 | Office, Small | Elec | 30.89% | 37.77% | 20.4% | 6.705% | 0% | 4.241%
[13 empty] | 16 | Office, Small | Elec | 75.65% | 17.54% | 5.738% | 0% | 0% | 1.076%
[13 empty] | 17 | Office, Small | Elec | 69.45% | 19.84% | 0% | 2.213% | 0% | 8.497%
Note on P46: Weighted & scaled to 2022 economy
Note on T46: Weighted & scaled to 2022 economy
Note on X46: Weighted & scaled to 2022 economy
Note on AF46: Mohsen Abrishami: Reported in Appdx K
Note on U70: The saturations here are the % of total floorspace for each combination of end-use and fuel.
Note on V70: The saturations here are the % of total floorspace for each combination of end-use and fuel.
Note on W70: The saturations here are the % of total floorspace for each combination of end-use and fuel.

## EV Charger (hidden)
EV Charger - OfficeSmall (TBD)
According To CEUS 2022 and their survey around 2018-2020, almost 92% of small office buildings have no EV charger
Background Data [To be deleted prior to publication]
CEUS 2022 (Base on Survey 2018) | [7 empty] | The data presented in this worksheet represents the projected number of EV charger ports, or the number of cars that can be charged at the same time, for the year 2022 (last year of CEUC)
|  |  | Has EV Chargers |  |  |  |  | Level 1, 120 volt Charger (No. ports/SqFT) | [8 empty] | Level 2, 240 volt Charger (No. ports/SqFT) | [8 empty] | Level 3, DC fast (No. ports/SqFT) | [8 empty] | Charger Type Unkown (No. ports/SqFT) | [8 empty] | All Chargers Totals (No. ports/SqFT)
Calculation Method | Statewide/ Utility/ FCZ | Building Type | No | Yes | Total | Statewide/ Utility/ FCZ | Building Type | Public Only | Public & Employee | Public & Fleet | Employee Only | Employee & Fleet | Fleet Only | All 3 Types | Unknown | Level 1 Total | Public Only | Public & Employee | Public & Fleet | Employee Only | Employee & Fleet | Fleet Only | All 3 Types | Unknown | Level 2 Total | Public Only | Public & Employee | Public & Fleet | Employee Only | Employee & Fleet | Fleet Only | All 3 Types | Unknown | Level 3 Total | Public Only | Public & Employee | Public & Fleet | Employee Only | Employee & Fleet | Fleet Only | All 3 Types | Unknown | Unkonwn Total | Public Only | Public & Employee | Public & Fleet | Employee Only | Employee & Fleet | Fleet Only | All 3 Types | Unknown | Total
Floorspace-Based | Statewide | Office, Small | 91.63% | 8.371% | 100% | Statewide | Office, Small | 234.6311 | 257.2607 | 0 | 514.2646 | 0 | 22.2217 | 197.9831 | 0 | 1226.3611 | 108.945 | 831.3199 | 0 | 1332.4399 | 101.1641 | 78.5024 | 360.406 | 0 | 2812.7774 | 21.3759 | 0 | 0 | 15.7138 | 0 | 0 | 0 | 0 | 37.0897 | 56.9499 | 42.1476 | 0 | 212.1101 | 0 | 25.742 | 0 | 0 | 336.9496 | 421.9019 | 1130.7282 | 0 | 2074.5284 | 101.1641 | 126.466 | 558.3891 | 0 | 4413.1778
Floorspace-Based | FCZ01 Tot | Office, Small | 88.47% | 11.53% | 100% | FCZ01 Tot | Office, Small | 0 | 0 | 0 | 92.1148 | 0 | 0 | 5.6273 | 0 | 97.7421 | 0 | 290.1537 | 0 | 73.0277 | 95.6646 | 65.7399 | 24.3426 | 0 | 548.9286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9748 | 0 | 24.3426 | 0 | 0 | 52.3174 | 0 | 290.1537 | 0 | 193.1173 | 95.6646 | 90.0824 | 29.9699 | 0 | 698.988
Floorspace-Based | FCZ02 Tot | Office, Small | 87.66% | 12.34% | 100% | FCZ02 Tot | Office, Small | 0 | 0 | 0 | 0 | 0 | 21.0137 | 0 | 0 | 21.0137 | 0 | 189.1229 | 0 | 21.1561 | 0 | 0 | 0 | 0 | 210.279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189.1229 | 0 | 21.1561 | 0 | 21.0137 | 0 | 0 | 231.2926
Floorspace-Based | FCZ03 Tot | Office, Small | 93.39% | 6.61% | 100% | FCZ03 Tot | Office, Small | 0 | 78.751 | 0 | 0 | 0 | 0 | 0 | 0 | 78.751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.8719 | 0 | 0 | 0 | 0 | 0 | 0 | 12.8719 | 0 | 91.6228 | 0 | 0 | 0 | 0 | 0 | 0 | 91.6228
Floorspace-Based | FCZ04 Tot | Office, Small | 82.7% | 17.3% | 100% | FCZ04 Tot | Office, Small | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.11 | 0 | 0 | 0 | 0 | 44.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.9845 | 0 | 0 | 0 | 0 | 0 | 0 | 26.9845 | 0 | 26.9845 | 0 | 44.11 | 0 | 0 | 0 | 0 | 71.0945
Floorspace-Based | FCZ05 Tot | Office, Small | 96.4% | 3.601% | 100% | FCZ05 Tot | Office, Small | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.6347 | 0 | 0 | 0 | 0 | 19.6347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.6347 | 0 | 0 | 0 | 0 | 19.6347
Floorspace-Based | FCZ06 Tot | Office, Small | 93.41% | 6.592% | 100% | FCZ06 Tot | Office, Small | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2848 | 0 | 0 | 0 | 0 | 50.2848 | 0 | 0 | 0 | 50.2848 | 0 | 0 | 0 | 0 | 50.2848
Floorspace-Based | FCZ07 Tot | Office, Small | 91.77% | 8.231% | 100% | FCZ07 Tot | Office, Small | 0 | 0 | 0 | 199.1172 | 0 | 0 | 0 | 0 | 199.1172 | 0 | 229.2222 | 0 | 397.4995 | 0 | 0 | 0 | 0 | 626.7218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229.2222 | 0 | 596.6167 | 0 | 0 | 0 | 0 | 825.839
Floorspace-Based | FCZ08 Tot | Office, Small | 86.72% | 13.28% | 100% | FCZ08 Tot | Office, Small | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.6289 | 0 | 0 | 0 | 0 | 0 | 0 | 77.6289 | 0 | 0 | 0 | 14.8596 | 0 | 0 | 0 | 0 | 14.8596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.6289 | 0 | 14.8596 | 0 | 0 | 0 | 0 | 92.4885
Floorspace-Based | FCZ09 Tot | Office, Small | 90.94% | 9.064% | 100% | FCZ09 Tot | Office, Small | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Floorspace-Based | FCZ10 Tot | Office, Small | 95.6% | 4.399% | 100% | FCZ10 Tot | Office, Small | 0 | 0 | 0 | 27.5268 | 0 | 0 | 0 | 0 | 27.5268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.1608 | 0 | 0 | 0 | 0 | 50.1608 | 0 | 0 | 0 | 77.6876 | 0 | 0 | 0 | 0 | 77.6876
Floorspace-Based | FCZ11 Tot | Office, Small | 87.59% | 12.41% | 100% | FCZ11 Tot | Office, Small | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.1762 | 0 | 0 | 0 | 0 | 89.1762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.1762 | 0 | 0 | 0 | 0 | 89.1762
Floorspace-Based | FCZ12c Tot | Office, Small | 84.94% | 15.06% | 100% | FCZ12c Tot | Office, Small | 148.2736 | 164.5245 | 0 | 144.7477 | 0 | 0 | 181.593 | 0 | 639.1388 | 6.1825 | 0 | 0 | 246.2021 | 0 | 8.495 | 316.4711 | 0 | 577.3507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.3574 | 0 | 0 | 0 | 0 | 49.3574 | 154.456 | 164.5245 | 0 | 440.3072 | 0 | 8.495 | 498.0641 | 0 | 1265.8469
Floorspace-Based | FCZ12i Tot | Office, Small | 94.56% | 5.436% | 100% | FCZ12i Tot | Office, Small | 73.6026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.6026 | 0 | 0 | 0 | 369.1995 | 0 | 0 | 0 | 0 | 369.1995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.854 | 127.4565 | 0 | 0 | 369.1995 | 0 | 0 | 0 | 0 | 496.6561
Floorspace-Based | FCZ13 Tot | Office, Small | 96.48% | 3.519% | 100% | FCZ13 Tot | Office, Small | 0 | 0 | 0 | 22.8017 | 0 | 0 | 0 | 0 | 22.8017 | 36.1985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.1985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8017 | 0 | 0 | 0 | 0 | 22.8017 | 36.1985 | 0 | 0 | 45.6034 | 0 | 0 | 0 | 0 | 81.802
Floorspace-Based | FCZ16 Tot | Office, Small | 99.34% | 0.6613% | 100% | FCZ16 Tot | Office, Small | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.6415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.6415 | 20.2138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.2138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.8554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.8554
Floorspace-Based | FCZ17 Tot | Office, Small | 98.53% | 1.474% | 100% | FCZ17 Tot | Office, Small | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Weights
% of floor area per CZ and vintage bin - OfficeSmall | [8 empty] | % of floor area per CZ and vintage bin - OfficeSmall
Prototype | CZ | Vintage Bin | [6 empty] | Prototype | Vintage Bin | CZ
|  | Pre-1978 | 1978-1997 | 1998-2007 | 2008-2018 | Not available |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
OfficeSmall | 1 | 34.58% | 34.03% | 18.67% | 7.477% | 5.245% | 100% |  | OfficeSmall | Pre-1978 | 1.22% | 3.592% | 11.49% | 5.911% | 1.209% | 7.663% | 4.772% | 13.08% | 17.92% | 5.068% | 2.668% | 12.2% | 3.966% | 1.796% | 1.869% | 5.577% | 100%
| 2 | 46.17% | 33.96% | 12.32% | 5.11% | 2.445% | 100% |  |  | 1978-1997 | 1.326% | 2.916% | 7.84% | 3.79% | 1.138% | 6.7% | 8.382% | 8.135% | 10.06% | 9.707% | 3.918% | 16.49% | 5.138% | 1.781% | 4.752% | 7.928% | 100%
| 3 | 47.14% | 29.14% | 10.44% | 4.01% | 9.274% | 100% |  |  | 1998-2007 | 1.595% | 2.32% | 6.156% | 2.874% | 0.6446% | 2.945% | 3.805% | 3.61% | 3.407% | 10.78% | 7% | 26.01% | 7.875% | 1.993% | 6.835% | 12.14% | 100%
| 4 | 49.26% | 28.61% | 9.897% | 4.065% | 8.164% | 100% |  |  | 2008-2018 | 1.68% | 2.531% | 6.222% | 3.106% | 0.6721% | 4.771% | 3.255% | 4.694% | 8.557% | 11.72% | 4.869% | 17.3% | 8.162% | 1.91% | 9.215% | 11.34% | 100%
| 5 | 37.02% | 31.58% | 8.159% | 3.234% | 20% | 100% |  |  | Not available | 0.7869% | 0.8085% | 9.609% | 4.165% | 2.776% | 5.392% | 5.841% | 9.273% | 12.45% | 10.95% | 3.868% | 11.07% | 5.333% | 2.395% | 6.756% | 8.525% | 100%
| 6 | 45.16% | 35.77% | 7.171% | 4.417% | 7.475% | 100% |  |  | Total | 1.301% | 2.869% | 8.989% | 4.426% | 1.204% | 6.258% | 5.836% | 9.169% | 12.06% | 8.385% | 3.978% | 15.94% | 5.315% | 1.88% | 4.439% | 7.953%
| 7 | 30.16% | 47.99% | 9.935% | 3.231% | 8.684% | 100%
| 8 | 52.62% | 29.64% | 6% | 2.966% | 8.774% | 100%
| 9 | 54.78% | 27.85% | 4.304% | 4.109% | 8.954% | 100%
| 10 | 22.29% | 38.68% | 19.6% | 8.094% | 11.33% | 100%
| 11 | 24.74% | 32.91% | 26.82% | 7.091% | 8.437% | 100%
| 12 | 28.24% | 34.58% | 24.87% | 6.287% | 6.027% | 100%
| 13 | 27.52% | 32.3% | 22.58% | 8.896% | 8.705% | 100%
| 14 | 35.25% | 31.66% | 16.16% | 5.886% | 11.05% | 100%
| 15 | 15.53% | 35.77% | 23.47% | 12.03% | 13.21% | 100%
| 16 | 25.86% | 33.31% | 23.27% | 8.263% | 9.3% | 100%
| Statewide | 39.77% | 33.44% | 13.44% | 4.818% | 8.526%
Ref: CEUS 2022 dataset
Background Data [To be deleted prior to publication]
CEUS 2022
FZ | Building Type | Pre-1978 | 1978-1997 | 1998-2007 | 2008-2017 | 2018 | Year-Built Not Available | Total |  | 2008-2018 | CZ 1: Total floor area of the CA stock (kft²)
Statewide | Office, Small | 39.06% | 32.05% | 13.2% | 4.653% | 0.0468% | 10.99% | 100% |  | 4.7% | CZ 1: 729220.6429
1 | Office, Small | 49.23% | 27.62% | 10.19% | 4.19% | 0% | 8.773% | 100% |  | 4.19% | CZ 1: 119595.5776
2 | Office, Small | 46.17% | 33.78% | 12.29% | 5.038% | 0% | 2.727% | 100% |  | 5.038% | CZ 1: 33616.997
3 | Office, Small | 35.13% | 29.74% | 15.97% | 5.955% | 0% | 13.2% | 100% |  | 5.955% | CZ 1: 9405.1639
4 | Office, Small | 10.54% | 33.09% | 44.09% | 4.576% | 0% | 7.701% | 100% |  | 4.576% | CZ 1: 45237.8174
5 | Office, Small | 27.17% | 34.07% | 22.42% | 8.875% | 0% | 7.452% | 100% |  | 8.875% | CZ 1: 43153.1055
6 | Office, Small | 36.79% | 31.17% | 7.323% | 3.211% | 0% | 21.5% | 100% |  | 3.211% | CZ 1: 34954.825
7 | Office, Small | 49.36% | 27.61% | 6.424% | 2.731% | 0.203% | 13.68% | 100% |  | 2.934% | CZ 1: 168128.0774
8 | Office, Small | 26.93% | 48.4% | 9.788% | 9.046% | 0% | 5.832% | 100% |  | 9.046% | CZ 1: 24229.8711
9 | Office, Small | 26.61% | 24.38% | 23.27% | 8.989% | 0% | 16.75% | 100% |  | 8.989% | CZ 1: 11692.4715
10 | Office, Small | 23.33% | 31.24% | 22.63% | 7.85% | 0% | 14.95% | 100% |  | 7.85% | CZ 1: 33664.068
11 | Office, Small | 15.07% | 31.83% | 23.53% | 12.16% | 0% | 17.41% | 100% |  | 12.16% | CZ 1: 35588.1912
12c | Office, Small | 27.13% | 51.71% | 8.664% | 3.942% | 0% | 8.553% | 100% |  | 3.942% | CZ 1: 66439.5525
12i | Office, Small | 33.1% | 25.23% | 10.31% | 0.6977% | 0% | 30.67% | 100% |  | 0.6977% | CZ 1: 21127.5797
13 | Office, Small | 32.63% | 41.75% | 18.75% | 3.655% | 0% | 3.214% | 100% |  | 3.655% | CZ 1: 29100.3243
16 | Office, Small | 74.89% | 21.23% | 2.464% | 0% | 0% | 1.406% | 100% |  | 0% | CZ 1: 38649.9531
17 | Office, Small | 57.67% | 21.32% | 0% | 6.906% | 0% | 14.11% | 100% |  | 6.906% | CZ 1: 14637.0677
Floor area
Dodge 2023 | STC 7:305,405 Area/Project><25 Constructed after 1967 before 1978 |  |  | 61112.2
| STC 7:305,405 Area/Project><25 Constructed after 1967 |  |  | 297298.7
CEUS 2022 | Total Floor are for small office(<30 ksf) |  |  | 771141.35
| Total Floor area for small office (<30 ksf) Pre-1978 |  |  | 304706.3558 | 39.51%
| Small office (1967-1977)/All Pre 1878 |  |  | 20.06%
CEUS 2022 |  | Conditioned (k SqFt) | [5 empty] | Unconditioned (k SqFt) |  |  | CZ 4: Total
Statewide/ Utility/ FCZ | Building Type | Pre-1978 | 1978-1997 | 1998-2007 | 2008-2018 | Not Available | Total | Pre-1978 | 1978-1997 | 1998-2007 | CZ 1: 2008-2018; CZ 2: Not Available; CZ 3: Total; CZ 4: Pre-1978; CZ 5: 1978-1997; CZ 6: 1998-2007; CZ 7: 2008-2018; CZ 8: Not Available; CZ 9: Total
Statewide | Office, Small | 276678.5094 | 241828.1124 | 95988.8599 | 35630.2995 | 61102.0249 | 711227.8061 | 29971.0802 | 16040.6231 | 7634.2167 | CZ 1: 1514.2893; CZ 2: 4638.4938; CZ 3: 59798.7031; CZ 4: 306649.5896; CZ 5: 257868.7354; CZ 6: 103623.0766; CZ 7: 37144.5888; CZ 8: 65740.5187; CZ 9: 771026.5092
FCZ01 Tot | Office, Small | 53784.8718 | 32999.722 | 10936.7534 | 4585.3403 | 7468.4345 | 109775.1219 | 7268.2041 | 694.3961 | 1204.1481 | CZ 1: 425.8628; CZ 2: 186.1316; CZ 3: 9778.7429; CZ 4: 61053.0759; CZ 5: 33694.1181; CZ 6: 12140.9015; CZ 7: 5011.2031; CZ 8: 7654.5661; CZ 9: 119553.8648
FCZ02 Tot | Office, Small | 13352.8176 | 9647.916 | 3659.6977 | 1714.0383 | 731.3014 | 29105.7709 | 2187.068 | 1767.3587 | 470.9351 | CZ 1: 0; CZ 2: 85.8558; CZ 3: 4511.2176; CZ 4: 15539.8856; CZ 5: 11415.2747; CZ 6: 4130.6328; CZ 7: 1714.0383; CZ 8: 817.1571; CZ 9: 33616.9885
FCZ03 Tot | Office, Small | 3193.2902 | 2796.6371 | 1418.2923 | 560.0588 | 1184.717 | 9152.9953 | 111.0918 | 0 | 83.9181 | CZ 1: 0; CZ 2: 57.1589; CZ 3: 252.1689; CZ 4: 3304.382; CZ 5: 2796.6371; CZ 6: 1502.2104; CZ 7: 560.0588; CZ 8: 1241.8759; CZ 9: 9405.1641
FCZ04 Tot | Office, Small | 4769.6281 | 13172.6073 | 17791.1299 | 2050.2791 | 3043.2603 | 40826.9046 | 0 | 1794.6778 | 2167.3135 | CZ 1: 19.8606; CZ 2: 440.5661; CZ 3: 4422.418; CZ 4: 4769.6281; CZ 5: 14967.2851; CZ 6: 19958.4434; CZ 7: 2070.1397; CZ 8: 3483.8264; CZ 9: 45249.3226
FCZ05 Tot | Office, Small | 11153.2392 | 13330.8801 | 9354.7826 | 3829.8507 | 2977.7772 | 40646.5298 | 811.2778 | 1373.1991 | 322.106 | CZ 1: 0; CZ 2: 0; CZ 3: 2506.5828; CZ 4: 11964.5169; CZ 5: 14704.0791; CZ 6: 9676.8886; CZ 7: 3829.8507; CZ 8: 2977.7772; CZ 9: 43153.1126
FCZ06 Tot | Office, Small | 11881.9367 | 10003.9162 | 2831.2619 | 1071.4579 | 6770.1529 | 32558.7257 | 1071.7011 | 1012.7016 | 18.4667 | CZ 1: 50.8934; CZ 2: 242.3333; CZ 3: 2396.0961; CZ 4: 12953.6378; CZ 5: 11016.6178; CZ 6: 2849.7286; CZ 7: 1122.3513; CZ 8: 7012.4862; CZ 9: 34954.8218
FCZ07 Tot | Office, Small | 79852.4879 | 49086.8184 | 10354.3648 | 5701.2154 | 16153.7214 | 161148.6079 | 3985.9001 | 2093.1092 | 446.0465 | CZ 1: 0; CZ 2: 403.5343; CZ 3: 6928.5901; CZ 4: 83838.388; CZ 5: 51179.9276; CZ 6: 10800.4113; CZ 7: 5701.2154; CZ 8: 16557.2558; CZ 9: 168077.1981
FCZ08 Tot | Office, Small | 6673.1279 | 10968.355 | 2306.1579 | 2050.2475 | 586.4954 | 22584.3837 | 0 | 877.8407 | 65.4541 | CZ 1: 141.5591; CZ 2: 533.1405; CZ 3: 1617.9945; CZ 4: 6673.1279; CZ 5: 11846.1958; CZ 6: 2371.612; CZ 7: 2191.8066; CZ 8: 1119.6359; CZ 9: 24202.3782
FCZ09 Tot | Office, Small | 2791.1654 | 2824.4311 | 2664.3979 | 951.7997 | 1958.5964 | 11190.3905 | 320.2188 | 26.2891 | 56.283 | CZ 1: 99.2948; CZ 2: 0; CZ 3: 502.0858; CZ 4: 3111.3842; CZ 5: 2850.7203; CZ 6: 2720.6809; CZ 7: 1051.0945; CZ 8: 1958.5964; CZ 9: 11692.4763
FCZ10 Tot | Office, Small | 7579.1686 | 10386.011 | 7421.6188 | 2642.6378 | 3481.0139 | 31510.4502 | 336.4407 | 681.7303 | 795.9888 | CZ 1: 0; CZ 2: 339.4477; CZ 3: 2153.6075; CZ 4: 7915.6093; CZ 5: 11067.7413; CZ 6: 8217.6077; CZ 7: 2642.6378; CZ 8: 3820.4616; CZ 9: 33664.0576
FCZ11 Tot | Office, Small | 5363.5935 | 12676.2904 | 7990.6575 | 4097.6866 | 4780.4586 | 34908.6866 | 0 | 64.8924 | 385.0221 | CZ 1: 229.5883; CZ 2: 0; CZ 3: 679.5028; CZ 4: 5363.5935; CZ 5: 12741.1828; CZ 6: 8375.6796; CZ 7: 4327.2749; CZ 8: 4780.4586; CZ 9: 35588.1895
FCZ12c Tot | Office, Small | 15294.6456 | 33670.86 | 6158.0383 | 2245.6254 | 2607.6682 | 59976.8376 | 3368.2914 | 2076.6406 | 362.9596 | CZ 1: 436.235; CZ 2: 218.5892; CZ 3: 6462.7158; CZ 4: 18662.937; CZ 5: 35747.5006; CZ 6: 6520.9979; CZ 7: 2681.8604; CZ 8: 2826.2574; CZ 9: 66439.5534
FCZ12i Tot | Office, Small | 6659.289 | 5920.1396 | 2160.3567 | 143.2159 | 3679.7168 | 18562.7181 | 1088.5205 | 355.3802 | 18.0884 | CZ 1: 4.1885; CZ 2: 1098.6842; CZ 3: 2564.8619; CZ 4: 7747.8096; CZ 5: 6275.5198; CZ 6: 2178.4451; CZ 7: 147.4044; CZ 8: 4778.4011; CZ 9: 21127.58
FCZ13 Tot | Office, Small | 8736.9077 | 10325.8157 | 4770.6935 | 1039.1204 | 501.9135 | 25374.4509 | 957.2899 | 1894.5277 | 822.4761 | CZ 1: 24.4871; CZ 2: 27.0852; CZ 3: 3725.866; CZ 4: 9694.1976; CZ 5: 12220.3434; CZ 6: 5593.1696; CZ 7: 1063.6076; CZ 8: 528.9987; CZ 9: 29100.3169
FCZ16 Tot | Office, Small | 22110.9596 | 8207.2074 | 952.5201 | 0 | 543.4749 | 31814.162 | 6835.7912 | 0 | 0 | CZ 1: 0; CZ 2: 0; CZ 3: 6835.7912; CZ 4: 28946.7507; CZ 5: 8207.2074; CZ 6: 952.5201; CZ 7: 0; CZ 8: 543.4749; CZ 9: 38649.9531
FCZ17 Tot | Office, Small | 8440.6119 | 2664.2701 | 0 | 1010.7948 | 1311.7005 | 13427.3773 | 0 | 455.8808 | 0 | CZ 1: 0; CZ 2: 753.8096; CZ 3: 1209.6904; CZ 4: 8440.6119; CZ 5: 3120.1509; CZ 6: 0; CZ 7: 1010.7948; CZ 8: 2065.5101; CZ 9: 14637.0677

## PV (hidden)
PV - TBD

## Data (hidden)
Space Function | Electric Equipment Load Intensity | Electric Equipment Load Intensity | LPD
Aging Eye/Low-vision (Corridor Area) |  |  | 2013 | 2016 | 2019 | 2025
Aging Eye/Low-vision (Dining)
Aging Eye/Low-vision (Lobby, Main Entry)
Aging Eye/Low-vision (Lounge/Waiting Area)
Aging Eye/Low-vision (Multipurpose Room)
Aging Eye/Low-vision (Religious Worship Area)
Aging Eye/Low-vision (Restroom)
Aging Eye/Low-vision (Stairwell)
Audience Seating Area
Auditorium Area
Auto Repair / Maintenance Area
Barber, Beauty Salon, Spa Area
Civic Meeting Place Area
Classroom, Lecture, Training, Vocational Areas
Concourse and Atria Area
Convention, Conference, Multipurpose and Meeting Area
Copy Room
Corridor Area
Dining Area (Bar/Lounge and Fine Dining)
Dining Area (Cafeteria/Fast Food)
Dining Area (Family and Leisure)
Electrical, Mechanical, Telephone Rooms
Exercise/Fitness Center and Gymnasium Areas
Financial Transaction Area
Healthcare Facility and Hospitals (Exam/Treatment Room)
Healthcare Facility and Hospitals (Imaging Room)
Healthcare Facility and Hospitals (Medical Supply Room)
Healthcare Facility and Hospitals (Nursery)
Healthcare Facility and Hospitals (Nurse's Station)
Healthcare Facility and Hospitals (Operating Room)
Healthcare Facility and Hospitals (Patient Room)
Healthcare Facility and Hospitals (Physical Therapy Room)
Healthcare Facility and Hospitals (Recovery Room)
Hotel Function Area
Kitchen/Food Preparation Area
Kitchenette or Residential Kitchen
Laboratory, Scientific
Laundry Area
Library (Reading Area)
Library (Stacks Area)
Lobby, Main Entry
Locker Room
Lounge, Breakroom, or Waiting Area
Manufacturing, Commercial & Industrial Work Area (Low Bay)
Manufacturing, Commercial & Industrial Work Area (High Bay)
Manufacturing, Commercial & Industrial Work Area (Precision)
Museum Area (Exhibition/Display)
Museum Area (Restoration Room)
Office Area (>250 square feet)
Office Area (<250 square feet)
Parking Garage Area (Parking Zone and Ramps)
Parking Garage Area (Daylight Adaptation Zones)
Pharmacy Area
Retail Sales Area (Grocery Sales)
Retail Sales Area (Retail Merchandise Sales)
Retail Sales Area (Fitting Room)
Religious Worship Area
Restrooms
Stairwell
Storage, Commercial/Industrial (Warehouse)
Storage, Commercial/Industrial (Refrigerated)
Storage, Commercial/Industrial (Shipping & Handling)
Storage (General)
Sports Arena - Playing Area (> 5,000 Spectators)
Sports Arena - Playing Area (2,000 - 5,000 Spectators)
Sports Arena - Playing Area (< 2,000 Spectators)
Sports Arena - Playing Area (Recreational)
Theater Area (Motion Picture)
Theater Area (Performance)
Transportation Function (Baggage Area)
Transportation Function (Ticketing Area)
Videoconferencing Studio
High-Rise Residential Living Spaces
Hotel/Motel Guest Room
All other
Attic
Reception Area
Elevator
Plenum
IT Room (EPD 12)
Computer Room (EPD 20)
Server Room (EPD 45)