## Notes
Data Sources
Dataset | Dodge 2023
CEUS 2022
ComStock 2023
Prototype | PNNL Outpatient prototype (90.1-2022) | https://www.energycodes.gov/prototype-building-models#Commercial
Codes | Title 24, part 6, referred to as T24 (1984, 2001, 2007, 2013, 2016, 2022, 2025)
ASHRAE 90.1 (2022)
CFR Title 10 (2008, 2010, 2025)
ASHRAE 170/OSHPD
2022 California Mechanical Code (Title 24, Part 4)
ACM 2022
| T24 2022 - Appendix 5.4A and Appendix 5.4B | https://www.energy.ca.gov/publications/2022/2022-nonresidential-and-multifamily-alternative-calculation-method-reference
Other | 2022 Reduced infiltration CASE report | https://title24stakeholders.com/wp-content/uploads/2020/10/2022-T24-Final-CASE-Report_Reduce-Infiltration.pdf
| 2019 Outdoor Lighting CASE Report | https://title24stakeholders.com/wp-content/uploads/2016/10/T24-2019-CASE-Study-Results-Report-Outdoor-Sources_Final_with-Attachments.pdf
| PNNL 20405, 2010 | https://www.pnnl.gov/main/publications/external/technical_reports/PNNL-20405.pdf
| Air leakage Memo, NORESCO, 2025 | https://2050partners.sharepoint.com/:w:/r/sites/CalBEMCollaborativeEfforts/_layouts/15/Doc.aspx?sourcedoc=%7B3BEF8F74-7FAC-44F2-A70C-D76617660066%7D&file=Infiltration_rate_report_14May2025-Short-Version.docx&wdLOR=c494C5A60-5F8A-438B-874B-578DCB850072&action=default&mobileredirect=true
| 2019 High Efficiency Fume Hoods in Laboratory Spaces CASE Report | https://title24stakeholders.com/wp-content/uploads/2017/09/2019-T24-CASE-Report_Fume-Hoods_Final_September-2017.pdf?
Construction Rate
Notes
Outpatient | An outpatient facility, is a medical building that provides scheduled, non-emergency services such as diagnostic imaging, minor procedures, and consultations without overnight stays. It operates during standard business hours and includes exam rooms, procedure rooms, labs, waiting areas, and administrative spaces. HVAC systems are typically partial outdoor air systems, with moderate ventilation and pressurization controls tailored to specific healthcare spaces.
EIA, 2018 CBECS | On average, hospitals were 264,800 square feet per building, but outpatient health care buildings averaged 13,700 square feet.
Source | https://www.eia.gov/consumption/commercial/

## Prototype
NORESCO, Updated August 2025
Outpatient
Characteristic | Value | Data Sources
Building Type | Outpatient
Building Category | Nonresidential
Vintages | 4 Vintages: Pre-1978 , 1978-1997 ,1998-2007 , 2008-2018 New Construction (2019+) | Based on the vintage bin analysis | NonRes-Vintage bins-Draft Report-30Nov2023-Final.docx
Shape |  | The analysis uses prototype geometry originally developed by PNNL.
Total Floor Area (ft²) | 40950 | Same as PNNL
Aspect Ratio | n/a | Same as PNNL
Number of Floors | 3 | Same as PNNL
Roof type | Flat roof | Same as PNNL
WWR | North: 20.5%, East:19.1%, South: 24.1%, West: 12.9% Average Total: 20%
Shading Geometry | No Shades | Same as PNNL
Floor to floor height (feet) | 10 ft | Same as PNNL
Floor to ceiling height (feet) | 10 ft | Same as PNNL
Glazing sill height (feet) | 3 ft (4 ft high windows) | Same as PNNL
Above grade wall area (ft²) | 16716.3529
Gross wall area (ft²) | 16716.3529
Roof area (ft²) | 14778.849
Underground Gross Wall Area (ft²) | 0

## Zones
Proposed Layout - Outpatient
Space Type | Space/ Thermal Zone | HVAC System Name/AHU Name | Schedule Category | Conditioned (Y/N) | Area Fraction | Area (ft²) | Volume (ft³) | Multipliers | Number of People | People (Persons/1,000 ft²) [T24, 2025,Table 120.1-A]
Healthcare Facility and Hospitals (Exam/Treatment Room) | Floor 1 Anesthesia | AHU-1 | Health | Yes | 0.2638% | 108 | 1080 | 1 | 1.08 | 10
Healthcare Facility and Hospitals (Medical Supply Room) | Floor 1 Bio Haz | AHU-1 | Health | Yes | 0.1368% | 56 | 560 | 1 | 0.56 | 10
Dining Area (Cafeteria/Fast Food) | Floor 1 Café | AHU-1 | Health | Yes | 1.026% | 420 | 4200 | 1 | 13.86 | 33
Healthcare Facility and Hospitals (Medical Supply Room) | Floor 1 Clean | AHU-1 | Health | Yes | 0.3077% | 126 | 1260 | 1 | 1.26 | 10
Healthcare Facility and Hospitals (Medical Supply Room) | Floor 1 Clean Work | AHU-1 | Health | Yes | 0.403% | 165 | 1650 | 1 | 1.65 | 10
Office Area (<250 square feet) | Floor 1 Dictation | AHU-1 | Office | Yes | 0.3077% | 126 | 1260 | 1 | 0.63 | 5
Office Area (<250 square feet) | Floor 1 Dressing Room | AHU-1 | Office | Yes | 0.1099% | 45 | 450 | 1 | 0.225 | 5
Electrical, Mechanical, Telephone Rooms | Floor 1 Electrical Room | AHU-1 | Health | Yes | 0.2393% | 98 | 980 | 1 | 0.294 | 3
Electrical, Mechanical, Telephone Rooms | Floor 1 Elevator Pump Room | AHU-1 | Health | Yes | 0.2222% | 91 | 910 | 1 | 0.273 | 3
Office Area (<250 square feet) | Floor 1 Humid | AHU-1 | Office | Yes | 0.1319% | 54 | 540 | 1 | 0.27 | 5
Corridor Area | Floor 1 IT Hall | AHU-1 | Health | Yes | 0.3419% | 140 | 1400 | 1 | 0.7 | 5
Office Area (<250 square feet) | Floor 1 IT Room | AHU-1 | Office | Yes | 0.2735% | 112 | 1120 | 1 | 0.56 | 5
Lobby, Main Entry | Floor 1 Lobby | AHU-1 | Health | Yes | 1.519% | 622 | 6220 | 1 | 20.526 | 33
Corridor Area | Floor 1 Lobby Hall | AHU-1 | Health | Yes | 0.5861% | 240 | 2400 | 1 | 1.2 | 5
Restrooms | Floor 1 Lobby Toilet | AHU-1 | Health | Yes | 0.1319% | 54 | 540 | 1 | 0.27 | 5
Locker Room | Floor 1 Locker Room | AHU-1 | Health | Yes | 1.612% | 660 | 6600 | 1 | 13.2 | 20
Corridor Area | Floor 1 Locker Room Hall | AHU-1 | Health | Yes | 1.211% | 496 | 4960 | 1 | 2.48 | 5
Lounge, Breakroom, or Waiting Area | Floor 1 Lounge | AHU-1 | Health | Yes | 0.8792% | 360 | 3600 | 1 | 11.88 | 33
Healthcare Facility and Hospitals (Medical Supply Room) | Floor 1 Med Gas | AHU-1 | Health | Yes | 0.1368% | 56 | 560 | 1 | 0.56 | 10
Healthcare Facility and Hospitals (Imaging Room) | Floor 1 MRI Control Room | AHU-1 | Health | Yes | 0.4103% | 168 | 1680 | 1 | 1.68 | 10
Corridor Area | Floor 1 MRI Hall | AHU-1 | Health | Yes | 0.359% | 147 | 1470 | 1 | 0.735 | 5
Healthcare Facility and Hospitals (Imaging Room) | Floor 1 MRI Room | AHU-1 | Health | Yes | 1.075% | 440 | 4400 | 1 | 4.4 | 10
Restrooms | Floor 1 MRI Toilet | AHU-1 | Health | Yes | 0.1319% | 54 | 540 | 1 | 0.27 | 5
Kitchen/Food Preparation Area | Floor 1 Nourishment | AHU-1 | Health | Yes | 0.4445% | 182 | 1820 | 1 | 0.546 | 3
Corridor Area | Floor 1 Nurse Hall | AHU-1 | Health | Yes | 1.211% | 496 | 4960 | 1 | 2.48 | 5
Storage (General) | Floor 1 Nurse Janitor | AHU-1 | Health | Yes | 0.1319% | 54 | 540 | 1 | 0.108 | 2
Healthcare Facility and Hospitals (Nurse's Station) | Floor 1 Nurse Station | AHU-1 | Health | Yes | 0.6374% | 261 | 2610 | 1 | 2.61 | 10
Restrooms | Floor 1 Nurse Toilet | AHU-1 | Health | Yes | 0.1319% | 54 | 540 | 1 | 0.27 | 5
Office Area (>250 square feet) | Floor 1 Office | AHU-1 | Office | Yes | 1.18% | 483 | 4830 | 1 | 2.415 | 5
Healthcare Facility and Hospitals (Operating Room) | Floor 1 Operating Room 1 | AHU-1 | Health | Yes | 1.123% | 460 | 4600 | 1 | 4.6 | 10
Healthcare Facility and Hospitals (Operating Room) | Floor 1 Operating Room 2 | AHU-1 | Health | Yes | 1.172% | 480 | 4800 | 1 | 4.8 | 10
Healthcare Facility and Hospitals (Operating Room) | Floor 1 Operating Room 3 | AHU-1 | Health | Yes | 1.163% | 476 | 4760 | 1 | 4.76 | 10
Healthcare Facility and Hospitals (Recovery Room) | Floor 1 PACU | AHU-1 | Health | Yes | 0.2638% | 108 | 1080 | 1 | 1.08 | 10
Corridor Area | Floor 1 Pre-Op Hall | AHU-1 | Health | Yes | 1.29% | 528 | 5280 | 1 | 2.64 | 5
Healthcare Facility and Hospitals (Patient Room) | Floor 1 Pre-Op Room 1 | AHU-1 | Health | Yes | 0.4616% | 189 | 1890 | 1 | 1.89 | 10
Healthcare Facility and Hospitals (Patient Room) | Floor 1 Pre-Op Room 2 | AHU-1 | Health | Yes | 0.8255% | 338 | 3380 | 1 | 3.38 | 10
Restrooms | Floor 1 Pre-Op Toilet | AHU-1 | Health | Yes | 0.1319% | 54 | 540 | 1 | 0.27 | 5
Healthcare Facility and Hospitals (Exam/Treatment Room) | Floor 1 Procedure Room | AHU-1 | Health | Yes | 0.696% | 285 | 2850 | 1 | 2.85 | 10
Reception area | Floor 1 Reception | AHU-1 | Office | Yes | 1.243% | 509 | 5090 | 1 | 2.545 | 5
Corridor Area | Floor 1 Reception Hall | AHU-1 | Health | Yes | 0.3126% | 128 | 1280 | 1 | 0.64 | 5
Healthcare Facility and Hospitals (Recovery Room) | Floor 1 Recovery Room | AHU-1 | Health | Yes | 1.319% | 540 | 5400 | 1 | 5.4 | 10
Office Area (<250 square feet) | Floor 1 Scheduling | AHU-1 | Office | Yes | 0.2906% | 119 | 1190 | 1 | 0.595 | 5
Corridor Area | Floor 1 Scrub | AHU-1 | Health | Yes | 0.2051% | 84 | 840 | 1 | 0.42 | 5
Healthcare Facility and Hospitals (Medical Supply Room) | Floor 1 Soil | AHU-1 | Health | Yes | 0.3077% | 126 | 1260 | 1 | 1.26 | 10
Healthcare Facility and Hospitals (Medical Supply Room) | Floor 1 Soil Hold | AHU-1 | Health | Yes | 0.1368% | 56 | 560 | 1 | 0.56 | 10
Healthcare Facility and Hospitals (Medical Supply Room) | Floor 1 Soil Work | AHU-1 | Health | Yes | 0.4396% | 180 | 1800 | 1 | 1.8 | 10
Healthcare Facility and Hospitals (Recovery Room) | Floor 1 Step Down | AHU-1 | Health | Yes | 0.7327% | 300 | 3000 | 1 | 3 | 10
Corridor Area | Floor 1 Sterile Hall | AHU-1 | Health | Yes | 1.504% | 616 | 6160 | 1 | 3.08 | 5
Storage (General) | Floor 1 Sterile Storage | AHU-1 | Health | Yes | 0.9671% | 396 | 3960 | 1 | 0.792 | 2
Storage (General) | Floor 1 Storage | AHU-1 | Health | Yes | 2.247% | 920 | 9200 | 1 | 1.84 | 2
Corridor Area | Floor 1 Sub-Sterile | AHU-1 | Health | Yes | 0.4787% | 196 | 1960 | 1 | 0.98 | 5
Corridor Area | Floor 1 Utility Hall | AHU-1 | Health | Yes | 0.6252% | 256 | 2560 | 1 | 1.28 | 5
Storage (General) | Floor 1 Utility Janitor | AHU-1 | Health | Yes | 0.1026% | 42 | 420 | 1 | 0.084 | 2
Storage (General) | Floor 1 Utility Room | AHU-1 | Health | Yes | 0.8792% | 360 | 3600 | 1 | 0.72 | 2
Corridor Area | Floor 1 Vestibule | AHU-1 | Health | Yes | 0.1758% | 72 | 720 | 1 | 0.36 | 5
Convention, Conference, Multipurpose and Meeting Area | Floor 2 Conference | AHU-2 | Office | Yes | 0.8206% | 336 | 3360 | 1 | 11.088 | 33
Restrooms | Floor 2 Conference Toilet | AHU-2 | Health | Yes | 0.1563% | 64 | 640 | 1 | 0.32 | 5
Office Area (<250 square feet) | Floor 2 Dictation | AHU-2 | Office | Yes | 0.171% | 70 | 700 | 1 | 0.35 | 5
Healthcare Facility and Hospitals (Exam/Treatment Room) | Floor 2 Exam 1 | AHU-2 | Health | Yes | 0.8792% | 360 | 3600 | 1 | 3.6 | 10
Healthcare Facility and Hospitals (Exam/Treatment Room) | Floor 2 Exam 2 | AHU-2 | Health | Yes | 1.319% | 540 | 5400 | 1 | 5.4 | 10
Healthcare Facility and Hospitals (Exam/Treatment Room) | Floor 2 Exam 3 | AHU-2 | Health | Yes | 1.758% | 720 | 7200 | 1 | 7.2 | 10
Healthcare Facility and Hospitals (Exam/Treatment Room) | Floor 2 Exam 4 | AHU-2 | Health | Yes | 0.2051% | 84 | 840 | 1 | 0.84 | 10
Healthcare Facility and Hospitals (Exam/Treatment Room) | Floor 2 Exam 5 | AHU-2 | Health | Yes | 0.8548% | 350 | 3500 | 1 | 3.5 | 10
Healthcare Facility and Hospitals (Exam/Treatment Room) | Floor 2 Exam 6 | AHU-2 | Health | Yes | 0.5495% | 225 | 2250 | 1 | 2.25 | 10
Healthcare Facility and Hospitals (Exam/Treatment Room) | Floor 2 Exam 7 | AHU-2 | Health | Yes | 1.934% | 792 | 7920 | 1 | 7.92 | 10
Healthcare Facility and Hospitals (Exam/Treatment Room) | Floor 2 Exam 8 | AHU-2 | Health | Yes | 0.6594% | 270 | 2700 | 1 | 2.7 | 10
Healthcare Facility and Hospitals (Exam/Treatment Room) | Floor 2 Exam 9 | AHU-2 | Health | Yes | 0.9671% | 396 | 3960 | 1 | 3.96 | 10
Corridor Area | Floor 2 Exam Hall 1 | AHU-2 | Health | Yes | 0.4396% | 180 | 1800 | 1 | 0.9 | 5
Corridor Area | Floor 2 Exam Hall 2 | AHU-2 | Health | Yes | 0.4396% | 180 | 1800 | 1 | 0.9 | 5
Corridor Area | Floor 2 Exam Hall 3 | AHU-2 | Health | Yes | 0.4396% | 180 | 1800 | 1 | 0.9 | 5
Corridor Area | Floor 2 Exam Hall 4 | AHU-2 | Health | Yes | 0.4836% | 198 | 1980 | 1 | 0.99 | 5
Corridor Area | Floor 2 Exam Hall 5 | AHU-2 | Health | Yes | 0.4836% | 198 | 1980 | 1 | 0.99 | 5
Corridor Area | Floor 2 Exam Hall 6 | AHU-2 | Health | Yes | 0.4836% | 198 | 1980 | 1 | 0.99 | 5
Storage (General) | Floor 2 Janitor | AHU-2 | Health | Yes | 0.1539% | 63 | 630 | 1 | 0.126 | 2
Lounge, Breakroom, or Waiting Area | Floor 2 Lounge | AHU-2 | Health | Yes | 0.1954% | 80 | 800 | 1 | 2.64 | 33
Healthcare Facility and Hospitals (Nurse's Station) | Floor 2 Nurse Station 1 | AHU-2 | Health | Yes | 0.3663% | 150 | 1500 | 1 | 1.5 | 10
Healthcare Facility and Hospitals (Nurse's Station) | Floor 2 Nurse Station 2 | AHU-2 | Health | Yes | 0.4396% | 180 | 1800 | 1 | 1.8 | 10
Office Area (>250 square feet) | Floor 2 Office | AHU-2 | Office | Yes | 1.368% | 560 | 5600 | 1 | 2.8 | 5
Corridor Area | Floor 2 Office Hall | AHU-2 | Health | Yes | 1.084% | 444 | 4440 | 1 | 2.22 | 5
Reception area | Floor 2 Reception | AHU-2 | Office | Yes | 2.403% | 984 | 9840 | 1 | 4.92 | 5
Corridor Area | Floor 2 Reception Hall | AHU-2 | Health | Yes | 1.377% | 564 | 5640 | 1 | 2.82 | 5
Restrooms | Floor 2 Reception Toilet | AHU-2 | Health | Yes | 0.3077% | 126 | 1260 | 1 | 0.63 | 5
Office Area (>250 square feet) | Floor 2 Scheduling 1 | AHU-2 | Office | Yes | 0.7913% | 324 | 3240 | 1 | 1.62 | 5
Office Area (>250 square feet) | Floor 2 Scheduling 2 | AHU-2 | Office | Yes | 0.8352% | 342 | 3420 | 1 | 1.71 | 5
Storage (General) | Floor 2 Storage 1 | AHU-2 | Health | Yes | 0.1368% | 56 | 560 | 1 | 0.112 | 2
Storage (General) | Floor 2 Storage 2 | AHU-2 | Health | Yes | 0.2931% | 120 | 1200 | 1 | 0.24 | 2
Storage (General) | Floor 2 Storage 3 | AHU-2 | Health | Yes | 0.3517% | 144 | 1440 | 1 | 0.288 | 2
Storage (General) | Floor 2 Utility | AHU-2 | Health | Yes | 0.3077% | 126 | 1260 | 1 | 0.252 | 2
Office Area (>250 square feet) | Floor 2 Work | AHU-2 | Office | Yes | 4.127% | 1690 | 16900 | 1 | 8.45 | 5
Corridor Area | Floor 2 Work Hall | AHU-2 | Health | Yes | 2.037% | 834 | 8340 | 1 | 4.17 | 5
Restrooms | Floor 2 Work Toilet | AHU-2 | Health | Yes | 0.1319% | 54 | 540 | 1 | 0.27 | 5
Healthcare Facility and Hospitals (Imaging Room) | Floor 2 X-Ray | AHU-2 | Health | Yes | 2.198% | 900 | 9000 | 1 | 9 | 10
Office Area (<250 square feet) | Floor 3 Dressing Room | AHU-3 | Office | Yes | 0.1026% | 42 | 420 | 1 | 0.21 | 5
Corridor Area | Floor 3 Elevator Hall | AHU-3 | Health | Yes | 0.9036% | 370 | 3700 | 1 | 1.85 | 5
Office Area (<250 square feet) | Floor 3 Humid | AHU-3 | Office | Yes | 0.2638% | 108 | 1080 | 1 | 0.54 | 5
Storage (General) | Floor 3 Janitor | AHU-3 | Health | Yes | 0.1539% | 63 | 630 | 1 | 0.126 | 2
Locker Room | Floor 3 Locker | AHU-3 | Health | Yes | 0.2931% | 120 | 1200 | 1 | 2.4 | 20
Lounge, Breakroom, or Waiting Area | Floor 3 Lounge | AHU-3 | Health | Yes | 1.854% | 759 | 7590 | 1 | 25.047 | 33
Restrooms | Floor 3 Lounge Toilet | AHU-3 | Health | Yes | 0.4689% | 192 | 1920 | 1 | 0.96 | 5
Electrical, Mechanical, Telephone Rooms | Floor 3 Mechanical | AHU-3 | Health | Yes | 0.8548% | 350 | 3500 | 1 | 1.05 | 3
Corridor Area | Floor 3 Mechanical Hall | AHU-3 | Health | Yes | 0.7327% | 300 | 3000 | 1 | 1.5 | 5
Office Area (>250 square feet) | Floor 3 Office | AHU-3 | Office | Yes | 7.415% | 3036 | 30360 | 1 | 15.18 | 5
Corridor Area | Floor 3 Office Hall | AHU-3 | Health | Yes | 2.037% | 834 | 8340 | 1 | 4.17 | 5
Restrooms | Floor 3 Office Toilet | AHU-3 | Health | Yes | 0.1319% | 54 | 540 | 1 | 0.27 | 5
Healthcare Facility and Hospitals (Physical Therapy Room) | Floor 3 Physical Therapy 1 | AHU-3 | Health | Yes | 3.175% | 1300 | 13000 | 1 | 13 | 10
Healthcare Facility and Hospitals (Physical Therapy Room) | Floor 3 Physical Therapy 2 | AHU-3 | Health | Yes | 1.446% | 592 | 5920 | 1 | 5.92 | 10
Restrooms | Floor 3 Physical Therapy Toilet | AHU-3 | Health | Yes | 0.2051% | 84 | 840 | 1 | 0.42 | 5
Storage (General) | Floor 3 Storage 1 | AHU-3 | Health | Yes | 0.2638% | 108 | 1080 | 1 | 0.216 | 2
Storage (General) | Floor 3 Storage 2 | AHU-3 | Health | Yes | 0.2051% | 84 | 840 | 1 | 0.168 | 2
Healthcare Facility and Hospitals (Exam/Treatment Room) | Floor 3 Treatment | AHU-3 | Health | Yes | 1.163% | 476 | 4760 | 1 | 4.76 | 10
Storage (General) | Floor 3 Undeveloped 1 | AHU-3 | Health | Yes | 5.539% | 2268 | 22680 | 1 | 4.536 | 2
Storage (General) | Floor 3 Undeveloped 2 | AHU-3 | Health | Yes | 2.813% | 1152 | 11520 | 1 | 2.304 | 2
Storage (General) | Floor 3 Utility | AHU-3 | Health | Yes | 0.5275% | 216 | 2160 | 1 | 0.432 | 2
Office Area (>250 square feet) | Floor 3 Work | AHU-3 | Office | Yes | 1.402% | 574 | 5740 | 1 | 2.87 | 5
Stairwell | NE Stair | AHU-3 | Health | Yes | 0.4103% | 168 | 5040 | 1 | 0.84 | 5
Elevator | NW Elevator | AHU-3 | Health | Yes | 0.3419% | 140 | 4200 | 1 | 0 | 0
Stairwell | NW Stair | AHU-3 | Health | Yes | 0.4689% | 192 | 5760 | 1 | 0.96 | 5
Stairwell | SW Stair | AHU-3 | Health | Yes | 0.2345% | 96 | 2880 | 1 | 0.48 | 5
Total (23 Space types) | Total ( 118 spaces) | Total ( Thermal Zones) |  | Total ( 118 Conditioned zones) |  | 40946 |  | 118 | 329.193
Background Data [To be deleted prior to publication]
N

## Envelope
Envelope - Outpatient
Element | Prototype | Assembly Type | Construction | Unit | Vintage | Selected T24 | Note | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
External Wall | Outpatient | ExtWall_MetalFramed_NonRes | Metal frame + insulation + gypsum board | U-value IP | Pre 1978 | N/A | ASHRAE 90.1,2022 Table A3.3.3.1, 3.5", R-0 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352
[5 empty] | 1978-1997 | 1986 | Package A with heat capacity around 10 (Btu/F/ft²) | 0.213 | 0.227 | 0.227 | 0.217 | 0.256 | 0.256 | 0.256 | 0.256 | 0.256 | 0.256 | 0.238 | 0.238 | 0.238 | 0.208 | 0.208 | 0.213
[5 empty] | 1998-2007 | 2001 | Table 1-H | 0.182 | 0.182 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.098 | 0.062 | 0.082 | 0.062 | 0.062 | 0.098 | 0.098 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.06 | 0.055 | 0.071 | 0.055 | 0.055 | 0.06 | 0.06 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055
Roof | Outpatient | FlatRoof_WoodFramedAndOther_NonRes | Built-up Roof (Metal Decking Roof): Roof membrane + roof insulation + metal decking | U-value IP | Pre 1978 | N/A | Considering 30 years for roof/ insulation replacement. | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 1978-1997 | 1992 |  | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 1998-2007 | 2001 | Table 1-H | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.049 | 0.039 | 0.039 | 0.039 | 0.049 | 0.075 | 0.067 | 0.067 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038
Windows | Outpatient | FixedWindow_NonRes | Single pane | U-value IP | Pre 1978 | N/A | ASHRAE Handbook of Fundamentals (Table 4-Ch15) for single pane & T24, 2013 for double pane(88%-12%)* | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288
[5 empty] | 1978-1997 | N/A |  | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288
|  |  | Double pane |  | 1998-2007 | 2001 | Table 1-H | 0.49 | 0.49 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.34 | 0.36 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.36
| Outpatient | FixedWindow_NonRes | Single pane | SHGC | Pre 1978 | N/A | ASHRAE Handbook of Fundamentals (Table 10-Ch15) for single pane & T24, 2013 for double pane(88%-12%)* | 0.7252 | 0.7252 | 0.7252 | 0.7252 | 0.7252 | 0.7252 | 0.7252 | 0.7252 | 0.7252 | 0.7252 | 0.7252 | 0.7252 | 0.7252 | 0.7252 | 0.7252 | 0.7252
[5 empty] | 1978-1997 | N/A |  | 0.7252 | 0.7252 | 0.7252 | 0.7252 | 0.7252 | 0.7252 | 0.7252 | 0.7252 | 0.7252 | 0.7252 | 0.7252 | 0.7252 | 0.7252 | 0.7252 | 0.7252 | 0.7252
|  |  | Double pane |  | 1998-2007 | 2001 | Table 1-H - WWR:10-20% / SHGC non-north | 0.43 | 0.36 | 0.55 | 0.55 | 0.55 | 0.61 | 0.61 | 0.61 | 0.61 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.43
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.22 | 0.25 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.25
PNNL models have steel-framed walls.
Infiltration
[5 empty] | Vintage | I_75 6-sdied Infiltration rate @ 75 pa | Note | I-design (cfm/ft²) (4-sided Infiltration rate at normal pressure) (Design flow rate approach and Flow/Exterior Wall Area calculation method)
|  |  |  | Infiltration | Pre 1978 | 1.1 | 2022 CASE report (Table 38) | 0.341
[5 empty] | 1978-1997 | 1.1 | 2022 CASE report (Table 38) | 0.341
[5 empty] | 1998-2007 | 1.1 | 2022 CASE report (Table 38) | 0.341
[5 empty] | 2008-2018 | 1 | 2022 CASE report (Table 38) & T24, 2008-2016 (Table 140.3-B)--Air barrier is required in CZ 10-16 | 0.3121
[5 empty] | 2019+ | 0.6 | 2022 CASE report (Table 38) & T24, 2025 (Table 140.3-B)--Air barrier is required in all CZs | 0.186
Source: Title 24 air barrier requirements (all editions) and the standardized infiltration rate reported in the 2022 CASE report and Dodge 2023 data
|  |  |  | Air Leakage Memo: |  | Infiltration_rate_report_14May2025-Short-Version.docx

## Thermostat
Thermostat - Outpatient
Setpoint | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16 | Source | Note
Health Heating Setpoint (F) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | T24 2022 - Appendix 5.4B | PNNL Healthcare-Outpatient prototype use this setpoints: Administration zones: 72°F Cooling/70°F Heating, Critical zones: 72°F Cooling/70°F Heating, Operating rooms: 65°F Cooling/65°F Heating---PNNL Healthcare-Outpatient prototype use this setbacks: 77°F Cooling/65°F Heating, Critical zones: no setback, Operating rooms: 72°F Cooling/65°F Heating
Health Heating Setback (F) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
Health Cooling Setpoint (F) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
Health Cooling Setback (F) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
Kitchen Heating Setpoint (F) | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | PNNL 09.1, 2022 Restaurant prototype
Kitchen Heating Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Kitchen Cooling Setpoint (F) | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79
Kitchen Cooling Setback (F) | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86

## HVAC System
HVAC System - Outpatient
Vintage | Spaces | Heating | Cooling | Air Distribution | Source | Note
Existing | Conditioned zones | Gas Boiler for Hydronic Reheat and Gas Furnace for Heating | RTU DX | Single Duct CAV--Outdoor air often supplied through RTU economizers or dedicated OA section | CEUS 2022 (Other system based on T24 and Engineering judgement) | Packaged RTU
New Construction | Conditioned zones | Gas Boiler for Hydronic Reheat and Gas Furnace for Heating | RTU DX | VAV + Hydronic Reheat | T24 2025 ACM 2025, Table 2 and 3 | System 5 – PVAV
Efficiency of HVAC system
Vintage | Upgrade/Installed year | DX Cooling | Gas Furnace | Gas Boiler | Source | Note
Pre 1978 | 2008 | EER=9.5 (≥ 240,000 Btu/h and < 760,000 Btu/h) | . Gas-fired forced air furnaces with input ratings ≥225,000 Btu/h--75% of the input rating | n/a | T24, 2008 , Table 112-A (for DX Coil)
1978-1997
1998-2007
2008-2018 | 2013 | EER=10 (≥ 240,000 Btu/h and < 760,000 Btu/h) | Warm-Air Duct Furnaces, Gas-Fired-All Capacities--80% Ec | n/a | T24, 2013 , Table 110.2-D (for DX Coil) -Table 110.2-I (for Gas Furnace thermal efficiency)
New Construction | 2025 | EER=10 (≥ 240,000 Btu/h and < 760,000 Btu/h) | Warm-Air Duct Furnaces, Gas-Fired-All Capacities--80% Ec | Gas-Fired Boiler ≥ 300,000 Btu/h and ≤ 2,500,000 Btu/h-- 84% Et | T24, 2013 , Table 110.2-A (for DX Coil) - Table 110.2-J (for Boiler thermal efficiency)-Table 110.2-I (for Gas Furnace thermal efficiency)
|  | * Et = Combustion efficiency | * Et = Thermal efficiency
Fan power
Vintage | Approach | System | Total Static Pressure (TSP) in w.c. [PNNL 20405, 2010, Table 5.11] | Fan Efficiency [ACM, 2025] | Fan Motor and Drive Efficiency [ACM 2025, Table 13] | W/cfm [ACM 2025, Table 14 and 15] | Data Source | Note
Existing | PNNL TSP | Packaged RTU-CAV | 4.09 | 0.65 | 0.9 |  | ACM 2025, PNNL 2010 TSD
Brake horse power (bhp)=(Supply cfm*TSP in w.c.)/(6356*Fan efficiency)
Fan power (w/cfm) = bhp/motor and drive efficiency *746
New Construction | ACM 2025 | Packaged RTU-CAV | 3.8877 | 0.65 | 0.9 | 0.78 | 2025 ACM, PNNL 2010 TSD
|  | System 5-PVAV System >5,000 cfm; < 10,000 cfm | 5.0939 |  |  | 1.022
|  | System 5-PVAV System >10,000 cfm | 4.8048 |  |  | 0.964
* 0.9 is an average fan efficiency according to ACM 2025, Table 13
Fan total eff (E+ input) = 0.65 x Motor_eff
TSP (E+ input) in w.c. = Motor_eff/746 x (6356 x Fan_eff) x W/cfm
Fan_eff=0.65
Background Data [To be deleted prior to publication]
CEUS 2022 data | Heating |  |  |  | Cooling |  | Air Distribution | Water Heater
| Floorspace Heated | Primary Heating | Fuel Type |  | Floorspace Cooled | Primary Cooling | Primary Air Dis | Fuel Type
|  | The default is the floorspace method unless otherwise specified | Elec | Gas |  | The default is the floorspace method unless otherwise specified | The default is the floorspace method unless otherwise specified | Elec | Gas
Health Care | 99% | Floorspace method: | 17% | 81% | 98% | Floorspace method: | Floorspace method: | 10% | 85%
|  | Boiler/ Hydronic (43.9%) |  |  |  | Central Plant (Chiller) (43.5%) | Single Duct CAV (53.4%)
|  | Package System / Heat Pump (40.8%) |  |  |  | Package System / Heat Pump (40.7%) | Fan Coil/Unit Ventilator (21.3%)
|  | Site method: |  |  |  | Site method: | Site method:
|  | Boiler/ Hydronic (6.8%) |  |  |  | Central Plant (Chiller) (6.5%) | Single Duct CAV (91.4%)
|  | Package System / Heat Pump (72.1%) |  |  |  | Package System / Heat Pump (71.5%) | Fan Coil/Unit Ventilator (5.7%)

## Ventilation
Outdoor Airflow Rate - Outpatient
Space Type | Space/Thermal Zone | Number of People | Floor Area (ft²) | cfm/person [T24, 2025, Equation 120.1-F and Table 120.1-A] | cfm/ft² [T24, 2025, Equation 120.1-F and Table 120.1-A] | Required Exhaust Rate (cfm/ft²) [T24, 2025, Table 120.1-B – minimum exhaust rates] | Required Exhaust Rate (cfm) [T24, 2025, Table 120.1-B – minimum exhaust rates] | Min OA Ventilation Requirement (cfm/ft²) [Table 4-A, 2022 California Mechanical Code] | Total cfm Driven by People | Total cfm Driven by Area | Total cfm Driven by Exhaust | Total cfm | Note
Healthcare Facility and Hospitals (Exam/Treatment Room) | Floor 1 Anesthesia | 1.08 | 108 | 15 | n/a | 1.37 |  | 0.33333 | 16.2 | 36 | 147.96 | 147.96 | All Room air exhausted directly to the outdoor, according to Table 4-A, 2022 California Mechanical Code)
Healthcare Facility and Hospitals (Medical Supply Room) | Floor 1 Bio Haz | 0.56 | 56 | 15 | n/a |  |  | 0.33333 | 8.4 | 18.6667 | 0 | 18.6667
Dining Area (Cafeteria/Fast Food) | Floor 1 Café | 13.86 | 420 | 15 | 0.15 |  |  | 0 | 207.9 | 63 | 0 | 207.9
Healthcare Facility and Hospitals (Medical Supply Room) | Floor 1 Clean | 1.26 | 126 | 15 | n/a |  |  | 0.33333 | 18.9 | 42 | 0 | 42
Healthcare Facility and Hospitals (Medical Supply Room) | Floor 1 Clean Work | 1.65 | 165 | 15 | n/a |  |  | 0.33333 | 24.75 | 55 | 0 | 55
Office Area (<250 square feet) | Floor 1 Dictation | 0.63 | 126 | 15 | 0.15 |  |  | 0 | 9.45 | 18.9 | 0 | 18.9
Office Area (<250 square feet) | Floor 1 Dressing Room | 0.225 | 45 | 15 | 0.15 |  |  | 0 | 3.375 | 6.75 | 0 | 6.75
Electrical, Mechanical, Telephone Rooms | Floor 1 Electrical Room | 0.294 | 98 | 15 | 0.15 |  |  | 0 | 4.41 | 14.7 | 0 | 14.7
Electrical, Mechanical, Telephone Rooms | Floor 1 Elevator Pump Room | 0.273 | 91 | 15 | 0.15 |  |  | 0 | 4.095 | 13.65 | 0 | 13.65
Office Area (<250 square feet) | Floor 1 Humid | 0.27 | 54 | 15 | 0.15 |  |  | 0 | 4.05 | 8.1 | 0 | 8.1
Corridor Area | Floor 1 IT Hall | 0.7 | 140 | 15 | 0.15 |  |  | 0 | 10.5 | 21 | 0 | 21
Office Area (<250 square feet) | Floor 1 IT Room | 0.56 | 112 | 15 | 0.15 |  |  | 0 | 8.4 | 16.8 | 0 | 16.8
Lobby, Main Entry | Floor 1 Lobby | 20.526 | 622 | 15 | 0.15 |  |  | 0 | 307.89 | 93.3 | 0 | 307.89
Corridor Area | Floor 1 Lobby Hall | 1.2 | 240 | 15 | 0.15 |  |  | 0 | 18 | 36 | 0 | 36
Restrooms | Floor 1 Lobby Toilet | 0.27 | 54 | 15 | 0 |  | 50 | 0 | 4.05 | 0 | 50 | 0 | *Restrooms in California per 2025 T24 and CALGreen (Part 11) require mechanical exhaust ventilation, but they do not require additional dedicated outdoor air (OA) beyond that local exhaust. Bathroom exhaust and exhaust fan energy will be captured in the models. We will assume make-up air is drawn from adjacent spaces.
Locker Room | Floor 1 Locker Room | 13.2 | 660 | 15 | 0.15 | 0.25 |  | 0 | 198 | 99 | 165 | 198
Corridor Area | Floor 1 Locker Room Hall | 2.48 | 496 | 15 | 0.15 |  |  | 0 | 37.2 | 74.4 | 0 | 74.4
Lounge, Breakroom, or Waiting Area | Floor 1 Lounge | 11.88 | 360 | 15 | 0.15 |  |  | 0 | 178.2 | 54 | 0 | 178.2
Healthcare Facility and Hospitals (Medical Supply Room) | Floor 1 Med Gas | 0.56 | 56 | 15 | n/a |  |  | 0.33333 | 8.4 | 18.6667 | 0 | 18.6667
Healthcare Facility and Hospitals (Imaging Room) | Floor 1 MRI Control Room | 1.68 | 168 | 15 | n/a | 2.02 |  | 0.33333 | 25.2 | 56 | 339.36 | 339.36 | Exhaust Rate assumed according to PNNL outpatient model.
Corridor Area | Floor 1 MRI Hall | 0.735 | 147 | 15 | 0.15 |  |  | 0 | 11.025 | 22.05 | 0 | 22.05
Healthcare Facility and Hospitals (Imaging Room) | Floor 1 MRI Room | 4.4 | 440 | 15 | n/a | 2.02 |  | 0.33333 | 66 | 146.6667 | 888.8 | 888.8 | Exhaust Rate assumed according to PNNL outpatient model.
Restrooms | Floor 1 MRI Toilet | 0.27 | 54 | 15 | 0 |  | 50 | 0 | 4.05 | 0 | 50 | 50 | Toilet rooms, intermittent exhaust 50 cfm per toilet
Kitchen/Food Preparation Area | Floor 1 Nourishment | 0.546 | 182 | 15 | 0.15 | 0.3 |  | 0 | 8.19 | 27.3 | 54.6 | 54.6
Corridor Area | Floor 1 Nurse Hall | 2.48 | 496 | 15 | 0.15 |  |  | 0 | 37.2 | 74.4 | 0 | 74.4
Storage (General) | Floor 1 Nurse Janitor | 0.108 | 54 | 15 | 0.15 |  |  | 0 | 1.62 | 8.1 | 0 | 8.1
Healthcare Facility and Hospitals (Nurse's Station) | Floor 1 Nurse Station | 2.61 | 261 | 15 | n/a |  |  | 0.33333 | 39.15 | 87 | 0 | 87
Restrooms | Floor 1 Nurse Toilet | 0.27 | 54 | 15 | 0 |  | 50 | 0 | 4.05 | 0 | 50 | 50 | Toilet rooms, intermittent exhaust 50 cfm per toilet
Office Area (>250 square feet) | Floor 1 Office | 2.415 | 483 | 15 | 0.15 |  |  | 0 | 36.225 | 72.45 | 0 | 72.45
Healthcare Facility and Hospitals (Operating Room) | Floor 1 Operating Room 1 | 4.6 | 460 | 15 | n/a |  |  | 0.33333 | 69 | 153.3333 | 0 | 153.3333
Healthcare Facility and Hospitals (Operating Room) | Floor 1 Operating Room 2 | 4.8 | 480 | 15 | n/a |  |  | 0.33333 | 72 | 160 | 0 | 160
Healthcare Facility and Hospitals (Operating Room) | Floor 1 Operating Room 3 | 4.76 | 476 | 15 | n/a |  |  | 0.33333 | 71.4 | 158.6667 | 0 | 158.6667
Healthcare Facility and Hospitals (Recovery Room) | Floor 1 PACU | 1.08 | 108 | 15 | n/a |  |  | 0.33333 | 16.2 | 36 | 0 | 36
Corridor Area | Floor 1 Pre-Op Hall | 2.64 | 528 | 15 | 0.15 |  |  | 0 | 39.6 | 79.2 | 0 | 79.2
Healthcare Facility and Hospitals (Patient Room) | Floor 1 Pre-Op Room 1 | 1.89 | 189 | 15 | n/a |  |  | 0.33333 | 28.35 | 63 | 0 | 63
Healthcare Facility and Hospitals (Patient Room) | Floor 1 Pre-Op Room 2 | 3.38 | 338 | 15 | n/a |  |  | 0.33333 | 50.7 | 112.6667 | 0 | 112.6667
Restrooms | Floor 1 Pre-Op Toilet | 0.27 | 54 | 15 | 0 |  | 50 | 0 | 4.05 | 0 | 50 | 50 | Toilet rooms, intermittent exhaust 50 cfm per toilet
Healthcare Facility and Hospitals (Exam/Treatment Room) | Floor 1 Procedure Room | 2.85 | 285 | 15 | n/a |  |  | 0.33333 | 42.75 | 95 | 0 | 95
Reception area | Floor 1 Reception | 2.545 | 509 | 15 | 0.15 |  |  | 0 | 38.175 | 76.35 | 0 | 76.35
Corridor Area | Floor 1 Reception Hall | 0.64 | 128 | 15 | 0.15 |  |  | 0 | 9.6 | 19.2 | 0 | 19.2
Healthcare Facility and Hospitals (Recovery Room) | Floor 1 Recovery Room | 5.4 | 540 | 15 | n/a |  |  | 0.33333 | 81 | 180 | 0 | 180
Office Area (<250 square feet) | Floor 1 Scheduling | 0.595 | 119 | 15 | 0.15 |  |  | 0 | 8.925 | 17.85 | 0 | 17.85
Corridor Area | Floor 1 Scrub | 0.42 | 84 | 15 | 0.15 |  |  | 0 | 6.3 | 12.6 | 0 | 12.6
Healthcare Facility and Hospitals (Medical Supply Room) | Floor 1 Soil | 1.26 | 126 | 15 | n/a | 1.68 |  | 0.33333 | 18.9 | 42 | 211.68 | 211.68 | Exhaust Rate assumed according to PNNL outpatient model.
Healthcare Facility and Hospitals (Medical Supply Room) | Floor 1 Soil Hold | 0.56 | 56 | 15 | n/a | 1.51 |  | 0.33333 | 8.4 | 18.6667 | 84.56 | 84.56 | Exhaust Rate assumed according to PNNL outpatient model.
Healthcare Facility and Hospitals (Medical Supply Room) | Floor 1 Soil Work | 1.8 | 180 | 15 | n/a | 1.65 |  | 0.33333 | 27 | 60 | 297 | 297 | Exhaust Rate assumed according to PNNL outpatient model.
Healthcare Facility and Hospitals (Recovery Room) | Floor 1 Step Down | 3 | 300 | 15 | n/a |  |  | 0.33333 | 45 | 100 | 0 | 100
Corridor Area | Floor 1 Sterile Hall | 3.08 | 616 | 15 | 0.15 |  |  | 0 | 46.2 | 92.4 | 0 | 92.4
Storage (General) | Floor 1 Sterile Storage | 0.792 | 396 | 15 | 0.15 |  |  | 0 | 11.88 | 59.4 | 0 | 59.4
Storage (General) | Floor 1 Storage | 1.84 | 920 | 15 | 0.15 |  |  | 0 | 27.6 | 138 | 0 | 138
Corridor Area | Floor 1 Sub-Sterile | 0.98 | 196 | 15 | 0.15 |  |  | 0 | 14.7 | 29.4 | 0 | 29.4
Corridor Area | Floor 1 Utility Hall | 1.28 | 256 | 15 | 0.15 |  |  | 0 | 19.2 | 38.4 | 0 | 38.4
Storage (General) | Floor 1 Utility Janitor | 0.084 | 42 | 15 | 0.15 |  |  | 0 | 1.26 | 6.3 | 0 | 6.3
Storage (General) | Floor 1 Utility Room | 0.72 | 360 | 15 | 0.15 |  |  | 0 | 10.8 | 54 | 0 | 54
Corridor Area | Floor 1 Vestibule | 0.36 | 72 | 15 | 0.15 |  |  | 0 | 5.4 | 10.8 | 0 | 10.8
Convention, Conference, Multipurpose and Meeting Area | Floor 2 Conference | 11.088 | 336 | 15 | 0.15 |  |  | 0 | 166.32 | 50.4 | 0 | 166.32
Restrooms | Floor 2 Conference Toilet | 0.32 | 64 | 15 | 0 |  | 50 | 0 | 4.8 | 0 | 50 | 50 | Toilet rooms, intermittent exhaust 50 cfm per toilet
Office Area (<250 square feet) | Floor 2 Dictation | 0.35 | 70 | 15 | 0.15 |  |  | 0 | 5.25 | 10.5 | 0 | 10.5
Healthcare Facility and Hospitals (Exam/Treatment Room) | Floor 2 Exam 1 | 3.6 | 360 | 15 | n/a |  |  | 0.33333 | 54 | 120 | 0 | 120
Healthcare Facility and Hospitals (Exam/Treatment Room) | Floor 2 Exam 2 | 5.4 | 540 | 15 | n/a |  |  | 0.33333 | 81 | 180 | 0 | 180
Healthcare Facility and Hospitals (Exam/Treatment Room) | Floor 2 Exam 3 | 7.2 | 720 | 15 | n/a |  |  | 0.33333 | 108 | 240 | 0 | 240
Healthcare Facility and Hospitals (Exam/Treatment Room) | Floor 2 Exam 4 | 0.84 | 84 | 15 | n/a |  |  | 0.33333 | 12.6 | 28 | 0 | 28
Healthcare Facility and Hospitals (Exam/Treatment Room) | Floor 2 Exam 5 | 3.5 | 350 | 15 | n/a |  |  | 0.33333 | 52.5 | 116.6667 | 0 | 116.6667
Healthcare Facility and Hospitals (Exam/Treatment Room) | Floor 2 Exam 6 | 2.25 | 225 | 15 | n/a |  |  | 0.33333 | 33.75 | 75 | 0 | 75
Healthcare Facility and Hospitals (Exam/Treatment Room) | Floor 2 Exam 7 | 7.92 | 792 | 15 | n/a |  |  | 0.33333 | 118.8 | 264 | 0 | 264
Healthcare Facility and Hospitals (Exam/Treatment Room) | Floor 2 Exam 8 | 2.7 | 270 | 15 | n/a |  |  | 0.33333 | 40.5 | 90 | 0 | 90
Healthcare Facility and Hospitals (Exam/Treatment Room) | Floor 2 Exam 9 | 3.96 | 396 | 15 | n/a |  |  | 0.33333 | 59.4 | 132 | 0 | 132
Corridor Area | Floor 2 Exam Hall 1 | 0.9 | 180 | 15 | 0.15 |  |  | 0 | 13.5 | 27 | 0 | 27
Corridor Area | Floor 2 Exam Hall 2 | 0.9 | 180 | 15 | 0.15 |  |  | 0 | 13.5 | 27 | 0 | 27
Corridor Area | Floor 2 Exam Hall 3 | 0.9 | 180 | 15 | 0.15 |  |  | 0 | 13.5 | 27 | 0 | 27
Corridor Area | Floor 2 Exam Hall 4 | 0.99 | 198 | 15 | 0.15 |  |  | 0 | 14.85 | 29.7 | 0 | 29.7
Corridor Area | Floor 2 Exam Hall 5 | 0.99 | 198 | 15 | 0.15 |  |  | 0 | 14.85 | 29.7 | 0 | 29.7
Corridor Area | Floor 2 Exam Hall 6 | 0.99 | 198 | 15 | 0.15 |  |  | 0 | 14.85 | 29.7 | 0 | 29.7
Storage (General) | Floor 2 Janitor | 0.126 | 63 | 15 | 0.15 |  |  | 0 | 1.89 | 9.45 | 0 | 9.45
Lounge, Breakroom, or Waiting Area | Floor 2 Lounge | 2.64 | 80 | 15 | 0.15 |  |  | 0 | 39.6 | 12 | 0 | 39.6
Healthcare Facility and Hospitals (Nurse's Station) | Floor 2 Nurse Station 1 | 1.5 | 150 | 15 | n/a |  |  | 0.33333 | 22.5 | 50 | 0 | 50
Healthcare Facility and Hospitals (Nurse's Station) | Floor 2 Nurse Station 2 | 1.8 | 180 | 15 | n/a |  |  | 0.33333 | 27 | 60 | 0 | 60
Office Area (>250 square feet) | Floor 2 Office | 2.8 | 560 | 15 | 0.15 |  |  | 0 | 42 | 84 | 0 | 84
Corridor Area | Floor 2 Office Hall | 2.22 | 444 | 15 | 0.15 |  |  | 0 | 33.3 | 66.6 | 0 | 66.6
Reception area | Floor 2 Reception | 4.92 | 984 | 15 | 0.15 |  |  | 0 | 73.8 | 147.6 | 0 | 147.6
Corridor Area | Floor 2 Reception Hall | 2.82 | 564 | 15 | 0.15 |  |  | 0 | 42.3 | 84.6 | 0 | 84.6
Restrooms | Floor 2 Reception Toilet | 0.63 | 126 | 15 | 0 |  | 150 | 0 | 9.45 | 0 | 150 | 150 | Toilet rooms, intermittent exhaust 50 cfm per toilet
Office Area (>250 square feet) | Floor 2 Scheduling 1 | 1.62 | 324 | 15 | 0.15 |  |  | 0 | 24.3 | 48.6 | 0 | 48.6
Office Area (>250 square feet) | Floor 2 Scheduling 2 | 1.71 | 342 | 15 | 0.15 |  |  | 0 | 25.65 | 51.3 | 0 | 51.3
Storage (General) | Floor 2 Storage 1 | 0.112 | 56 | 15 | 0.15 |  |  | 0 | 1.68 | 8.4 | 0 | 8.4
Storage (General) | Floor 2 Storage 2 | 0.24 | 120 | 15 | 0.15 |  |  | 0 | 3.6 | 18 | 0 | 18
Storage (General) | Floor 2 Storage 3 | 0.288 | 144 | 15 | 0.15 |  |  | 0 | 4.32 | 21.6 | 0 | 21.6
Storage (General) | Floor 2 Utility | 0.252 | 126 | 15 | 0.15 |  |  | 0 | 3.78 | 18.9 | 0 | 18.9
Office Area (>250 square feet) | Floor 2 Work | 8.45 | 1690 | 15 | 0.15 |  |  | 0 | 126.75 | 253.5 | 0 | 253.5
Corridor Area | Floor 2 Work Hall | 4.17 | 834 | 15 | 0.15 |  |  | 0 | 62.55 | 125.1 | 0 | 125.1
Restrooms | Floor 2 Work Toilet | 0.27 | 54 | 15 | 0 |  | 50 | 0 | 4.05 | 0 | 50 | 50 | Toilet rooms, intermittent exhaust 50 cfm per toilet
Healthcare Facility and Hospitals (Imaging Room) | Floor 2 X-Ray | 9 | 900 | 15 | n/a | 2.02 |  | 0.33333 | 135 | 300 | 1818 | 1818 | Exhaust Rate assumed according to PNNL outpatient model.
Office Area (<250 square feet) | Floor 3 Dressing Room | 0.21 | 42 | 15 | 0.15 |  |  | 0 | 3.15 | 6.3 | 0 | 6.3
Corridor Area | Floor 3 Elevator Hall | 1.85 | 370 | 15 | 0.15 |  |  | 0 | 27.75 | 55.5 | 0 | 55.5
Office Area (<250 square feet) | Floor 3 Humid | 0.54 | 108 | 15 | 0.15 |  |  | 0 | 8.1 | 16.2 | 0 | 16.2
Storage (General) | Floor 3 Janitor | 0.126 | 63 | 15 | 0.15 |  |  | 0 | 1.89 | 9.45 | 0 | 9.45
Locker Room | Floor 3 Locker | 2.4 | 120 | 15 | 0.15 | 0.25 |  | 0 | 36 | 18 | 30 | 36
Lounge, Breakroom, or Waiting Area | Floor 3 Lounge | 25.047 | 759 | 15 | 0.15 |  |  | 0 | 375.705 | 113.85 | 0 | 375.705
Restrooms | Floor 3 Lounge Toilet | 0.96 | 192 | 15 | 0 |  | 200 | 0 | 14.4 | 0 | 200 | 200 | Toilet rooms, intermittent exhaust 50 cfm per toilet
Electrical, Mechanical, Telephone Rooms | Floor 3 Mechanical | 1.05 | 350 | 15 | 0.15 |  |  | 0 | 15.75 | 52.5 | 0 | 52.5
Corridor Area | Floor 3 Mechanical Hall | 1.5 | 300 | 15 | 0.15 |  |  | 0 | 22.5 | 45 | 0 | 45
Office Area (>250 square feet) | Floor 3 Office | 15.18 | 3036 | 15 | 0.15 |  |  | 0 | 227.7 | 455.4 | 0 | 455.4
Corridor Area | Floor 3 Office Hall | 4.17 | 834 | 15 | 0.15 |  |  | 0 | 62.55 | 125.1 | 0 | 125.1
Restrooms | Floor 3 Office Toilet | 0.27 | 54 | 15 | 0 |  | 50 | 0 | 4.05 | 0 | 50 | 50 | Toilet rooms, intermittent exhaust 50 cfm per toilet
Healthcare Facility and Hospitals (Physical Therapy Room) | Floor 3 Physical Therapy 1 | 13 | 1300 | 15 | n/a |  |  | 0.33333 | 195 | 433.3333 | 0 | 433.3333
Healthcare Facility and Hospitals (Physical Therapy Room) | Floor 3 Physical Therapy 2 | 5.92 | 592 | 15 | n/a |  |  | 0.33333 | 88.8 | 197.3333 | 0 | 197.3333
Restrooms | Floor 3 Physical Therapy Toilet | 0.42 | 84 | 15 | 0.15 |  | 100 | 0 | 6.3 | 12.6 | 100 | 100 | Toilet rooms, intermittent exhaust 50 cfm per toilet
Storage (General) | Floor 3 Storage 1 | 0.216 | 108 | 15 | 0.15 |  |  | 0 | 3.24 | 16.2 | 0 | 16.2
Storage (General) | Floor 3 Storage 2 | 0.168 | 84 | 15 | 0.15 |  |  | 0 | 2.52 | 12.6 | 0 | 12.6
Healthcare Facility and Hospitals (Exam/Treatment Room) | Floor 3 Treatment | 4.76 | 476 | 15 | n/a |  |  | 0.33333 | 71.4 | 158.6667 | 0 | 158.6667
Storage (General) | Floor 3 Undeveloped 1 | 4.536 | 2268 | 15 | 0.15 |  |  | 0 | 68.04 | 340.2 | 0 | 340.2
Storage (General) | Floor 3 Undeveloped 2 | 2.304 | 1152 | 15 | 0.15 |  |  | 0 | 34.56 | 172.8 | 0 | 172.8
Storage (General) | Floor 3 Utility | 0.432 | 216 | 15 | 0.15 |  |  | 0 | 6.48 | 32.4 | 0 | 32.4
Office Area (>250 square feet) | Floor 3 Work | 2.87 | 574 | 15 | 0.15 |  |  | 0 | 43.05 | 86.1 | 0 | 86.1
Stairwell | NE Stair | 0.84 | 168 | 15 | 0.15 |  |  | 0 | 12.6 | 25.2 | 0 | 25.2
Elevator | NW Elevator | 0 | 140 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0
Stairwell | NW Stair | 0.96 | 192 | 17 | 0.15 |  |  | 0 | 16.32 | 28.8 | 0 | 28.8
Stairwell | SW Stair | 0.48 | 96 | 18 | 0.15 |  |  | 0 | 8.64 | 14.4 | 0 | 14.4
Total (23 Space types) | Total ( 118 spaces) | 329.193 | 40946 | 19 |  |  |  |  | 6254.667 | 0 | 0 | 6254.667
Background Data [To be deleted prior to publication]
Outdoor Airflow Rate - Outpatient
Space Type | Total Floor Area (ft²) | Min. Occupancy Load (persons/1000 ft²) | Total Number of Occupants | cfm/ft² (Table 120.1-A – Minimum Ventilation Rates) | Required Exhaust Rate-cfm/ft² (Table 120.1-B – Minimum Exhaust Rates) | Min OA Ventilation Requirement-ACH-(Table 4-A, 2022 California Mechanical Code) | Min OA Ventilation Requirement-cfm/ft²-(Table 4-A, 2022 California Mechanical Code) | cfm
Healthcare Facility and Hospitals (Exam/Treatment Room) | 4606 | 10 | 46.06 | n/a | Floor 1 Anesthesia | 2 | 0.33333 | 1647
Healthcare Facility and Hospitals (Medical Supply Room) | 765 | 10 | 7.65 | n/a | Floor 1 Soil, Floor 1 Soil Hold, and Floor 1 Soil Work | 2 | 0.33333 | 728
Healthcare Facility and Hospitals (Imaging Room) | 1508 | 10 | 15.08 | n/a | Floor 1 MRI Room, Floor 1 MRI Control Room, Floor 2 X-Ray | 2 | 0.33333 | 3046
Healthcare Facility and Hospitals (Nurse's Station) | 591 | 10 | 5.91 | n/a |  | 2 | 0.33333 | 197
Healthcare Facility and Hospitals (Operating Room) | 1416 | 10 | 14.16 | n/a |  | 2 | 0.33333 | 472
Healthcare Facility and Hospitals (Recovery Room) | 948 | 10 | 9.48 | n/a |  | 2 | 0.33333 | 316
Healthcare Facility and Hospitals (Physical Therapy Room) | 1892 | 10 | 18.92 | n/a |  | 2 | 0.33333 | 630.6667
Healthcare Facility and Hospitals (Patient Room) | 527 | 10 | 5.27 | n/a |  | 2 | 0.33333 | 175.6667
Dining Area (Cafeteria/Fast Food) | 420 | 33 | 13.86 | 0.15 |  |  |  | 207.9
Office Area (<250 square feet) | 676 | 5 | 3.38 | 0.15 |  |  |  | 101.4
Office Area (>250 square feet) | 7009 | 5 | 35.045 | 0.15 |  |  |  | 1051.35
Convention, Conference, Multipurpose and Meeting Area | 0 | 33 | 0 | 0.15 |  |  |  | 0
Lobby, Main Entry | 622 | 33 | 20.526 | 0.15 |  |  |  | 307.89
Corridor Area | 7879 | 5 | 39.395 | 0.15 |  |  |  | 1181.85
Restrooms | 790 | 5 | 3.95 | 0.15 | 50/70 cfm/Unit |  |  | 0
Locker Room | 0 | 20 | 0 | 0.15 | 0.25 |  |  | 0
Kitchen/Food Preparation Area | 182 | 3 | 0.546 | 0.15 | 0.7 |  |  | 127.4
Storage (General) | 6172 | 2 | 12.344 | 0.15 |  |  |  | 925.8
Lounge, Breakroom, or Waiting Area | 0 | 33 | 0 | 0.15 |  |  |  | 0
Reception area | 1493 | 5 | 7.465 | 0.15 |  |  |  | 223.95
Stairwell | 456 | 5 | 2.28 | 0.15 |  |  |  | 68.4
Electrical, Mechanical, Telephone Rooms | 0 | 3 | 0 | 0.15 |  |  |  | 0
Total | 37952 |  | 261.321 |  |  |  |  | 11408.2733

## Water Heater
Water Heater - Outpatient
Vintage | WH Type | Efficiency | Tank Volume (gal) | Tank Loss |  | Note
Existing | Gas | 80% | 30 | 649.1131 | (Btu/hr)
New Construction | Gas | 80% | 30 | 649.1131 | (Btu/hr)
Peak Hot Water Consumption
Space Name | Baseline WH Type [CEUS 2022] | Total Area (ft²) | Number of People | Hot Water Usage Specification (gal/hr per person) [T24, 2022, Appendix 5.4A , sheet: "2022 SpaceFuncData-Input"] | Peak Hot Water Usage (gal/hr) | Peak Hot Water Usage (gal/min)
Floor 1 Anesthesia | Gas | 108 | 1.08 | 0.24 | 0.2592 | 0.00432
Floor 1 Bio Haz | Gas | 56 | 0.56 | 0.24 | 0.1344 | 0.00224
Floor 1 Café | Gas | 420 | 13.86 | 0.578 | 8.0111 | 0.13352
Floor 1 Clean | Gas | 126 | 1.26 | 0.24 | 0.3024 | 0.00504
Floor 1 Clean Work | Gas | 165 | 1.65 | 0.24 | 0.396 | 0.0066
Floor 1 Dictation | Gas | 126 | 0.63 | 0.18 | 0.1134 | 0.00189
Floor 1 Dressing Room | Gas | 45 | 0.225 | 0.18 | 0.0405 | 0.000675
Floor 1 Electrical Room | Gas | 98 | 0.294 | 0.18 | 0.05292 | 0.000882
Floor 1 Elevator Pump Room | Gas | 91 | 0.273 | 0.18 | 0.04914 | 0.000819
Floor 1 Humid | Gas | 54 | 0.27 | 0.18 | 0.0486 | 0.00081
Floor 1 IT Hall | Gas | 140 | 0.7 | 0 | 0 | 0
Floor 1 IT Room | Gas | 112 | 0.56 | 0.18 | 0.1008 | 0.00168
Floor 1 Lobby | Gas | 622 | 20.526 | 0.09 | 1.8473 | 0.030789
Floor 1 Lobby Hall | Gas | 240 | 1.2 | 0 | 0 | 0
Floor 1 Lobby Toilet | Gas | 54 | 0.27 | 0 | 0 | 0
Floor 1 Locker Room | Gas | 660 | 13.2 | 0.578 | 7.6296 | 0.12716
Floor 1 Locker Room Hall | Gas | 496 | 2.48 | 0 | 0 | 0
Floor 1 Lounge | Gas | 360 | 11.88 | 0.09 | 1.0692 | 0.01782
Floor 1 Med Gas | Gas | 56 | 0.56 | 0.24 | 0.1344 | 0.00224
Floor 1 MRI Control Room | Gas | 168 | 1.68 | 0.24 | 0.4032 | 0.00672
Floor 1 MRI Hall | Gas | 147 | 0.735 | 0 | 0 | 0
Floor 1 MRI Room | Gas | 440 | 4.4 | 0.24 | 1.056 | 0.0176
Floor 1 MRI Toilet | Gas | 54 | 0.27 | 0 | 0 | 0
Floor 1 Nourishment | Gas | 182 | 0.546 | 0.578 | 0.31559 | 0.0052598
Floor 1 Nurse Hall | Gas | 496 | 2.48 | 0 | 0 | 0
Floor 1 Nurse Janitor | Gas | 54 | 0.108 | 0 | 0 | 0
Floor 1 Nurse Station | Gas | 261 | 2.61 | 0.24 | 0.6264 | 0.01044
Floor 1 Nurse Toilet | Gas | 54 | 0.27 | 0 | 0 | 0
Floor 1 Office | Gas | 483 | 2.415 | 0.18 | 0.4347 | 0.007245
Floor 1 Operating Room 1 | Gas | 460 | 4.6 | 0.24 | 1.104 | 0.0184
Floor 1 Operating Room 2 | Gas | 480 | 4.8 | 0.24 | 1.152 | 0.0192
Floor 1 Operating Room 3 | Gas | 476 | 4.76 | 0.24 | 1.1424 | 0.01904
Floor 1 PACU | Gas | 108 | 1.08 | 0.24 | 0.2592 | 0.00432
Floor 1 Pre-Op Hall | Gas | 528 | 2.64 | 0 | 0 | 0
Floor 1 Pre-Op Room 1 | Gas | 189 | 1.89 | 0.24 | 0.4536 | 0.00756
Floor 1 Pre-Op Room 2 | Gas | 338 | 3.38 | 0.24 | 0.8112 | 0.01352
Floor 1 Pre-Op Toilet | Gas | 54 | 0.27 | 0 | 0 | 0
Floor 1 Procedure Room | Gas | 285 | 2.85 | 0.24 | 0.684 | 0.0114
Floor 1 Reception | Gas | 509 | 2.545 | 0.18 | 0.4581 | 0.007635
Floor 1 Reception Hall | Gas | 128 | 0.64 | 0 | 0 | 0
Floor 1 Recovery Room | Gas | 540 | 5.4 | 0.24 | 1.296 | 0.0216
Floor 1 Scheduling | Gas | 119 | 0.595 | 0.18 | 0.1071 | 0.001785
Floor 1 Scrub | Gas | 84 | 0.42 | 0 | 0 | 0
Floor 1 Soil | Gas | 126 | 1.26 | 0.24 | 0.3024 | 0.00504
Floor 1 Soil Hold | Gas | 56 | 0.56 | 0.24 | 0.1344 | 0.00224
Floor 1 Soil Work | Gas | 180 | 1.8 | 0.24 | 0.432 | 0.0072
Floor 1 Step Down | Gas | 300 | 3 | 0.24 | 0.72 | 0.012
Floor 1 Sterile Hall | Gas | 616 | 3.08 | 0 | 0 | 0
Floor 1 Sterile Storage | Gas | 396 | 0.792 | 0 | 0 | 0
Floor 1 Storage | Gas | 920 | 1.84 | 0 | 0 | 0
Floor 1 Sub-Sterile | Gas | 196 | 0.98 | 0 | 0 | 0
Floor 1 Utility Hall | Gas | 256 | 1.28 | 0 | 0 | 0
Floor 1 Utility Janitor | Gas | 42 | 0.084 | 0 | 0 | 0
Floor 1 Utility Room | Gas | 360 | 0.72 | 0 | 0 | 0
Floor 1 Vestibule | Gas | 72 | 0.36 | 0 | 0 | 0
Floor 2 Conference | Gas | 336 | 11.088 | 0.09 | 0.99792 | 0.016632
Floor 2 Conference Toilet | Gas | 64 | 0.32 | 0 | 0 | 0
Floor 2 Dictation | Gas | 70 | 0.35 | 0.18 | 0.063 | 0.00105
Floor 2 Exam 1 | Gas | 360 | 3.6 | 0.24 | 0.864 | 0.0144
Floor 2 Exam 2 | Gas | 540 | 5.4 | 0.24 | 1.296 | 0.0216
Floor 2 Exam 3 | Gas | 720 | 7.2 | 0.24 | 1.728 | 0.0288
Floor 2 Exam 4 | Gas | 84 | 0.84 | 0.24 | 0.2016 | 0.00336
Floor 2 Exam 5 | Gas | 350 | 3.5 | 0.24 | 0.84 | 0.014
Floor 2 Exam 6 | Gas | 225 | 2.25 | 0.24 | 0.54 | 0.009
Floor 2 Exam 7 | Gas | 792 | 7.92 | 0.24 | 1.9008 | 0.03168
Floor 2 Exam 8 | Gas | 270 | 2.7 | 0.24 | 0.648 | 0.0108
Floor 2 Exam 9 | Gas | 396 | 3.96 | 0.24 | 0.9504 | 0.01584
Floor 2 Exam Hall 1 | Gas | 180 | 0.9 | 0 | 0 | 0
Floor 2 Exam Hall 2 | Gas | 180 | 0.9 | 0 | 0 | 0
Floor 2 Exam Hall 3 | Gas | 180 | 0.9 | 0 | 0 | 0
Floor 2 Exam Hall 4 | Gas | 198 | 0.99 | 0 | 0 | 0
Floor 2 Exam Hall 5 | Gas | 198 | 0.99 | 0 | 0 | 0
Floor 2 Exam Hall 6 | Gas | 198 | 0.99 | 0 | 0 | 0
Floor 2 Janitor | Gas | 63 | 0.126 | 0 | 0 | 0
Floor 2 Lounge | Gas | 80 | 2.64 | 0.09 | 0.2376 | 0.00396
Floor 2 Nurse Station 1 | Gas | 150 | 1.5 | 0.24 | 0.36 | 0.006
Floor 2 Nurse Station 2 | Gas | 180 | 1.8 | 0.24 | 0.432 | 0.0072
Floor 2 Office | Gas | 560 | 2.8 | 0.18 | 0.504 | 0.0084
Floor 2 Office Hall | Gas | 444 | 2.22 | 0 | 0 | 0
Floor 2 Reception | Gas | 984 | 4.92 | 0.18 | 0.8856 | 0.01476
Floor 2 Reception Hall | Gas | 564 | 2.82 | 0 | 0 | 0
Floor 2 Reception Toilet | Gas | 126 | 0.63 | 0 | 0 | 0
Floor 2 Scheduling 1 | Gas | 324 | 1.62 | 0.18 | 0.2916 | 0.00486
Floor 2 Scheduling 2 | Gas | 342 | 1.71 | 0.18 | 0.3078 | 0.00513
Floor 2 Storage 1 | Gas | 56 | 0.112 | 0 | 0 | 0
Floor 2 Storage 2 | Gas | 120 | 0.24 | 0 | 0 | 0
Floor 2 Storage 3 | Gas | 144 | 0.288 | 0 | 0 | 0
Floor 2 Utility | Gas | 126 | 0.252 | 0 | 0 | 0
Floor 2 Work | Gas | 1690 | 8.45 | 0.18 | 1.521 | 0.02535
Floor 2 Work Hall | Gas | 834 | 4.17 | 0 | 0 | 0
Floor 2 Work Toilet | Gas | 54 | 0.27 | 0 | 0 | 0
Floor 2 X-Ray | Gas | 900 | 9 | 0.24 | 2.16 | 0.036
Floor 3 Dressing Room | Gas | 42 | 0.21 | 0.18 | 0.0378 | 0.00063
Floor 3 Elevator Hall | Gas | 370 | 1.85 | 0 | 0 | 0
Floor 3 Humid | Gas | 108 | 0.54 | 0.18 | 0.0972 | 0.00162
Floor 3 Janitor | Gas | 63 | 0.126 | 0 | 0 | 0
Floor 3 Locker | Gas | 120 | 2.4 | 0.578 | 1.3872 | 0.02312
Floor 3 Lounge | Gas | 759 | 25.047 | 0.09 | 2.2542 | 0.03757
Floor 3 Lounge Toilet | Gas | 192 | 0.96 | 0 | 0 | 0
Floor 3 Mechanical | Gas | 350 | 1.05 | 0.18 | 0.189 | 0.00315
Floor 3 Mechanical Hall | Gas | 300 | 1.5 | 0 | 0 | 0
Floor 3 Office | Gas | 3036 | 15.18 | 0.18 | 2.7324 | 0.04554
Floor 3 Office Hall | Gas | 834 | 4.17 | 0 | 0 | 0
Floor 3 Office Toilet | Gas | 54 | 0.27 | 0 | 0 | 0
Floor 3 Physical Therapy 1 | Gas | 1300 | 13 | 0.24 | 3.12 | 0.052
Floor 3 Physical Therapy 2 | Gas | 592 | 5.92 | 0.24 | 1.4208 | 0.02368
Floor 3 Physical Therapy Toilet | Gas | 84 | 0.42 | 0 | 0 | 0
Floor 3 Storage 1 | Gas | 108 | 0.216 | 0 | 0 | 0
Floor 3 Storage 2 | Gas | 84 | 0.168 | 0 | 0 | 0
Floor 3 Treatment | Gas | 476 | 4.76 | 0.24 | 1.1424 | 0.01904
Floor 3 Undeveloped 1 | Gas | 2268 | 4.536 | 0 | 0 | 0
Floor 3 Undeveloped 2 | Gas | 1152 | 2.304 | 0 | 0 | 0
Floor 3 Utility | Gas | 216 | 0.432 | 0 | 0 | 0
Floor 3 Work | Gas | 574 | 2.87 | 0.18 | 0.5166 | 0.00861
NE Stair | Gas | 168 | 0.84 | 0 | 0 | 0
NW Elevator | Gas | 140 | 0 | 0 | 0 | 0
NW Stair | Gas | 192 | 0.96 | 0 | 0 | 0
SW Stair | Gas | 96 | 0.48 | 0 | 0 | 0
Total ( 118 spaces) | Gas | 40946 | 329.193 |  | 61.7082 | 1.0285
Water Heater Capacity, Tank Capacity, and Tank Loss
WH Type | Peak Hot Water Usage (gal/hr) | Heat Output (Btu/hr) [ACM, 2025, 5.9.2: Rated capacity section] | WH Capacity (Btu/hr) [ACM, 2025, 5.9.2: Rated capacity section] | Required Energy Input (Btu/hr) | Storage Volume (gal) | Standby Loss |  | Off/On Cycle Loss Coefficient to Ambient Temp (Btu/h-F) | Source
Gas Storage WH | 75 | 49726.2 | 29835.72 | 37294.65 | 30 | 649.1131 | Btu/hr | 9.6883 | Standby loss equation: Title 20, §1605.1 Table F-4 WH capacity equation: ACM, 2025, 5.9.2: Rated capacity section)
Electric resistance WH | 0 | 0 | 0 | 0 | 0 |  | %hr | 0
Total | 75 | 49726.2 | 29835.72 | 37294.65 | 30
Design supply temperature (F) | 135 | Ref: T24 2022 - Appendix 5.4B |  |  | Standby Loss for Existing | 649.1131 | Btu/hr | 9.6883
Cold Water supply temperature (F) | 55 | Ref: ACM, 2025, 5.9.2: Rated capacity section
WH system factor | 0.6 | Ref: ACM, 2025, 5.9.2: Rated capacity section
Reheat multiplier | 0.4
* The 0.40 multiplier is a storage sizing factor used to account for the fact that the water heater doesn't need to store the full peak hour demand—it can reheat water during that time. This factor assumes that the heater will recover part of the hot water used during the peak hour, so only 40% of the peak hour demand needs to be stored at any given moment.
**For Gas Water Heater: UA(Btu/h-°F)​=Q˙​SL​ (Btu/h)/ΔT (∘F)​
Ambient temp | 68
Delta T | 67
** For Electric Water Heater: UA(Btu/h-°F)​= 0.0834 *SL​ (%/hr)*V gal
Background Data [To be deleted prior to publication]
Space Type | Hot Water Usage Specification (gal/hr per person) [T24, 2022, Appendix 5.4A , sheet: "2022 SpaceFuncData-Input"]
Healthcare Facility and Hospitals (Exam/Treatment Room) | 0.24
Healthcare Facility and Hospitals (Medical Supply Room) | 0.24
Healthcare Facility and Hospitals (Imaging Room) | 0.24
Healthcare Facility and Hospitals (Nurse's Station) | 0.24
Healthcare Facility and Hospitals (Operating Room) | 0.24
Healthcare Facility and Hospitals (Recovery Room) | 0.24
Healthcare Facility and Hospitals (Physical Therapy Room) | 0.24
Healthcare Facility and Hospitals (Patient Room) | 0.24
Dining Area (Cafeteria/Fast Food) | 0.578
Office Area (<250 square feet) | 0.18
Office Area (>250 square feet) | 0.18
Convention, Conference, Multipurpose and Meeting Area | 0.09
Lobby, Main Entry | 0.09
Corridor Area | 0
Restrooms | 0
Locker Room | 0.578
Kitchen/Food Preparation Area | 0.578
Storage (General) | 0
Lounge, Breakroom, or Waiting Area | 0.09
Reception area | 0.18
Stairwell | 0
Electrical, Mechanical, Telephone Rooms | 0.18

## Interior Lights
Interior Lighting - Outpatient
Space | New Construction |  |  | Existing
| LPD (W/ft²) | Additional LPD for PorTable Lighting (W/ft²) | Source | LPD (W/ft²) | Additional LPD for PorTable Lighting (W/ft²) | Source
Healthcare Facility and Hospitals (Exam/Treatment Room) | 1.15 |  | T24, 2025, Table 140.6 C (Area category method) | 1.15 |  | T24, 2019, Table 140.6 C Room (Area category method)
Healthcare Facility and Hospitals (Medical Supply Room) | 0.55 |  |  | 0.55
Healthcare Facility and Hospitals (Imaging Room) | 0.6 |  |  | 1
Healthcare Facility and Hospitals (Nurse's Station) | 0.85 |  |  | 0.75
Healthcare Facility and Hospitals (Operating Room) | 1.9 |  |  | 1.9
Healthcare Facility and Hospitals (Recovery Room) | 0.9 |  |  | 0.9
Healthcare Facility and Hospitals (Physical Therapy Room) | 0.75 |  |  | 0.85
Healthcare Facility and Hospitals (Patient Room) | 0.7 |  |  | 0.55
Dining Area (Cafeteria/Fast Food) | 0.45 |  |  | 0.4
Office Area (<250 square feet) | 0.65 |  |  | 0.7
Office Area (>250 square feet) | 0.6 |  |  | 0.65
Convention, Conference, Multipurpose and Meeting Area | 0.75 |  |  | 0.85
Lobby, Main Entry | 0.7 |  |  | 0.85
Corridor Area | 0.4 |  |  | 0.6
Restrooms | 0.65 |  |  | 0.65
Locker Room | 0.45 |  |  | 0.45
Kitchen/Food Preparation Area | 0.95 |  |  | 0.95
Storage (General) | 0.4 |  |  | 0.4
Lounge, Breakroom, or Waiting Area | 0.55 |  |  | 0.65
Stairwell | 0.6 |  |  | 0.5
Electrical, Mechanical, Telephone Rooms | 0.4 |  |  | 0.4
Reception area | 0.7 |  |  | 0.85
Elevator | 0 |  |  | 0
*Healthcare Buildings are expected to update their lighting systems more frequently than offices. Therefore code edition of 2019 was considered as the reference for LPD of the existing prototypes.

## Ext Lighting
Exterior Lighting - Outpatient
Motion Controlled Luminaires (W) | Non-motion Controlled Luminaires (W) | Total (W) | Source
1841.885 | 1030.665 | 2872.55 | T24, 2022 & 2025 2019 Outdoor Lighting CASE report PNNL 90.1-2010 TSD
Exterior Lighting
Items (Assume LZ2) | Assumptions [2019 Outdoor Lighting CASE Report & PNNL 90.1-2010 TSD] |  | Unit | Lighting Power Allowance [Title 24, 2025, Table 140.7-A & 140.7-B] | Unit | Exterior Lighting Power (W)
IWA (Initial Wattage Allowance) |  |  |  | 200 | (W) | 200
Parking area | 400 ft² for every parking space 1 parking space per 830 ft² of gross building area | 65520 | (ft²) | 0.019 | (W/ft²) | 1244.88
Building Entrance | 14 building entrance per PNNL Model | 14 | (count) | 15 | (W/ea) | 210
Hardscape Ornamental Light | 0.1 ft² per 1 ft² of gross building area for hardscape ornamental light | 4095 | (ft²) | 0.007 | (W/ft²) | 28.665
Building façade | 0.1 W per 1 ft² of facade area Façade Area = Perimeter × 0.5 × 28 ft (30 ft is the max height that is lit) * The 0.5 factor assumes that only half of the perimeter walls are lit. -Formula ia developed based on the 2019 Outdoor Lighting CASE report | 10020 | (ft²) | 0.1 | (W/ft²) | 1002
Non-sales canopy |  | 1365 | (ft²) | 0.137 | (W/ft²) | 187.005
Motion Controlled Luminaires (W) | [5 empty] | 1841.885
Non-motion-controlled Luminaires | [5 empty] | 1030.665
Total | [5 empty] | 2872.55
Total floor area | 40950
Perimeter | 668
Floors | 3
Background Data [To be deleted prior to publication]

## Equipment
Equipment - Outpatient
Spaces | Plug load Power Density (W/ft²) | Gas Power Density (Btu/hr-ft²) | Refrigeration Power Density (W/ft²) | Source | Note
Healthcare Facility and Hospitals (Exam/Treatment Room) | 1.5 | 1.1259 |  | T24 2022 - Appendix 5.4A | Appendix 5.4A: Gas equipment=1.1259 Btu/h-ft²--CEC model has the Gas equipment for 3.59 Btu/h-ft²
Healthcare Facility and Hospitals (Medical Supply Room) | 1.5
Healthcare Facility and Hospitals (Imaging Room) | 10 |  |  |  | PNNL has EPD=10 for Imaging room
Healthcare Facility and Hospitals (Nurse's Station) | 2 |  |  |  | PNNL has EPD=2 for Nurse station
Healthcare Facility and Hospitals (Operating Room) | 11 | 3.62 |  |  | PNNL has EPD=11 for Operating room--CEC: Gas equipment=3.62 Btu/h-ft²
Healthcare Facility and Hospitals (Recovery Room) | 1.5
Healthcare Facility and Hospitals (Physical Therapy Room) | 1.5
Healthcare Facility and Hospitals (Patient Room) | 1.5
Dining Area (Cafeteria/Fast Food) | 0.5 |  | 0.25 |  | CEC: Refrig Load = 0.25 w/ft²
Office Area (<250 square feet) | 0.7 |  |  |  | Plug load and schedules project with CEC, 2025
Office Area (>250 square feet) | 0.7 |  |  |  | Plug load and schedules project with CEC, 2025
Convention, Conference, Multipurpose and Meeting Area | 1
Lobby, Main Entry | 0.5
Corridor Area | 0
Restrooms | 0
Locker Room | 0.5
Kitchen/Food Preparation Area | 1.5 | 17.5377 | 1.12 |  | Appendix 5.4A: Gas equipment=17.53768 -- CEC: Refrig Load = 1.12 w/ft²
Storage (General) | 0.2
Lounge, Breakroom, or Waiting Area | 1
Stairwell | 0
Electrical, Mechanical, Telephone Rooms | 3
Reception area | 0.5
Elevator | 0
Elevator
Vintage | No. of Elevators | Cab Lighting Power Limit (W/ft²) | Lighting Shutoff | Cab Fan Control | Fan Power Limit | Regenerative Drive Threshold | Design load (W) | Note
Existing | 3 | 1.65 | n/a | n/a | n/a | n/a | 13860.78 | Design Load based on PNNL ASHRAE 90.1 2013 Outpatient prototype
New Construction | 3 | ≤ 0.6 W/ft² of cab floor area- Exempt (covered process) | Automatic shut‑off after ≤ 5 min no‑occupancy | When the elevator cab is stopped and unoccupied with doors closed for over 15 minutes, the cab interior lighting and ventilation fans shall be switched off until elevator cab operation resumes. | ≤ 0.33 W per cfm of fan airflow | n/a | 7611.31 | Design Load based on PNNL ASHRAE 90.1 2022 Outpatient prototype --- per T24 2025 §120.6 (f)
Assumptions for elevators:
One elevator for approximately 50,000 square feet in use.
For every two floors or two and a half floors, one more elevator was added.
An in-use rate of 70% for the floor area was assumed, based on engineering judgment.
Calculated number of Elevators: |  | 3 | Same as PNNL assumptions
Calculate Elevator load (kw)based on ACM 2022: |  | 30 | 30 kw is PNNL ASHRE 90.1 2019 elevator load (Lift,light and Fan)--CEC Model has 80K for the elevator load.
ACM 2022 suggestion for elevator load (kw): |  | 10
Elevator load will be defined as exterior load not equipment load
Elevator Load= Elevator Lift+ Elevator Light+Fan | 2022 | 2019 | 2013
Elevator Lift (W) | 7453.34 | 13672.78 | 13672.78
Elevator Fan | 157.97 | 188 | 188
Elevator Light | 0.7 W/ft² | 1.5 w/ft² | 1.65 w/ft²
based on PNNL ASHRAE 90.1 Outpatient prototype | 7611.31 | 13860.78 | 13860.78

## Schedules
Schedules - Outpatient
Zone | Schedule Category | Schedule | Source | Type | Hour
[5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
All Zones at level 2 and 3 | Health | Occupancy | T24 2022 - Appendix 5.4B, [Health] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
All Zones at level 2 and 3 | Health | Lights | T24 2022 - Appendix 5.4B, [Health] | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.45 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1
|  |  |  | Saturday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
All Zones at level 2 and 3 | Health | ElecEquipment | T24 2022 - Appendix 5.4B, [Health] | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1
|  |  |  | Saturday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
All Zones at level 2 and 3 | Health | ServiceHotWater | T24 2022 - Appendix 5.4B, [Health] | Weekday | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.17 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.18 | 0.18 | 0.18 | 0.1 | 0.01 | 0.01
|  |  |  | Saturday | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.2 | 0.28 | 0.3 | 0.3 | 0.24 | 0.24 | 0.23 | 0.23 | 0.23 | 0.1 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
|  |  |  | Sunday | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
All Zones at level 2 and 3 | Health | GasEquipment | T24 2022 - Appendix 5.4B, [Health] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.75 | 0.2 | 0.1 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
All Zones at level 2 and 3 | Health | Refrigeration | T24 2022 - Appendix 5.4B, [Health] | Weekday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Saturday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Sunday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
All Zones at level 2 and 4 | Health | Infiltration | T24 2022 - Appendix 5.4B, [Health] | Weekday | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1
|  |  |  | Saturday | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1
|  |  |  | Sunday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
All Zones at level 2 and 3 | Health | HVACAvail | T24 2022 - Appendix 5.4B, [Health] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
All the zones | Health | HtgSetpt |  | Weekday | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
|  |  |  | Saturday | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
|  |  |  | Sunday | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
All the zones | Health | ClgSetpt |  | Weekday | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
|  |  |  | Saturday | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
|  |  |  | Sunday | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
Office |  | Other
Office | Office | Occupancy | T24 2022 - Appendix 5.4B, [Office] Updated base on Plug load and schedules project with CEC, 2025 | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
Office | Office | Lights | T24 2022 - Appendix 5.4B, [Office] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.35 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Office | Office | ElecEquipment | Plug load and schedules project with CEC, 2025 | Weekday | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.74 | 0.87 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.5 | 0.45 | 0.45 | 0.45
|  |  |  | Saturday | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43
|  |  |  | Sunday | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43
Office | Office | HVACAvail | T24 2022 - Appendix 5.4B, [Office] Updated base on Plug load and schedules project with CEC, 202 | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Office | Office | ServiceHotWater | T24 2022 - Appendix 5.4B, [Office] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.12 | 0.14 | 0.07 | 0.07 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05
|  |  |  | Sunday | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04
Office | Office | Infiltration | T24 2022 - Appendix 5.4B, [Office] Updated base on Plug load and schedules project with CEC, 202 | Weekday | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
Office | Office | HtgSetpt | Honeywell-INNCOM e7 Thermostat User Guide & Engineering Judgement | Weekday | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
|  |  |  | Saturday | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
|  |  |  | Sunday | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
Office | Office | ClgSetpt | Honeywell-INNCOM e7 Thermostat User Guide & Engineering Judgement | Weekday | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
|  |  |  | Saturday | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
|  |  |  | Sunday | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
Other |  | Other
| Building | Elevator | T24 2022 - Appendix 5.4B, [Health] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02 | 0.75 | 1 | 1 | 1 | 0.75 | 1 | 1 | 1 | 1 | 1 | 0.52 | 0.52 | 0.52 | 0.28 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02 | 0.46 | 0.7 | 0.7 | 0.7 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.25 | 0.02 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Building | ExtLightingNonMotionCtrl | PNNL Hospital Prototype (2022) | Weekday | bar: Hour 1 to Hour 24
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
| Building | ExtLightingMotionCtrl | PNNL Hospital Prototype (2022) Modified to 0 for 11 pm to 5 am during weekday and 12 am to 5 am during weekend | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Office, Exam Room,Nurse Station, Recovery Room,Operating Room. Patient Room,Physical Therapy, Imaging Room, Medical Supply Room | Building | FunctionalAreaPeopleActivityLevel | CEC Hospital Prototype | Weekday | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
|  |  |  | Saturday | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
|  |  |  | Sunday | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
Corridor, Lobby, Restroom, Mechanical Room, Elevator, Stairwell, Reception rea, Lounge and Breakroom | Building | CommonAreaPeopleActivityLevel | CEC Hospital Prototype | Weekday | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5
|  |  |  | Saturday | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5
|  |  |  | Sunday | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5
Dining | Building | DiningAreaPeopleActivityLevel | CEC Hospital Prototype | Weekday | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2
|  |  |  | Saturday | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2
|  |  |  | Sunday | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2
Kitchen | Building | KitchenPeopleActivityLevel | CEC Hospital Prototype | Weekday | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8
|  |  |  | Saturday | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8
|  |  |  | Sunday | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8
Locker room | Building | LockerRoomPeopleActivityLevel | CEC Hospital Prototype | Weekday | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9
|  |  |  | Saturday | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9
|  |  |  | Sunday | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9 | 213.9
Background Data [To be deleted prior to publication] | bar: Hour 1 to Hour 2
Restaurant
Dining and Café | Restaurant | Occupancy | PNNL,ASHRAE 90.1, 2022 Fast Food Restaurant prototype (It has higher occupancy rate during morning compared to T24 2022 - Appendix 5.4B) | Weekday | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.4 | 0.4 | 0.4 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.8 | 0.8 | 0.8 | 0.5 | 0.35 | 0.2
|  |  |  | Saturday | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.4 | 0.2 | 0.45 | 0.5 | 0.5 | 0.35 | 0.3 | 0.3 | 0.3 | 0.7 | 0.9 | 0.7 | 0.65 | 0.55 | 0.35
|  |  |  | Sunday | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.3 | 0.2 | 0.25 | 0.35 | 0.55 | 0.65 | 0.7 | 0.35 | 0.2 | 0.2
Dining and Café | Restaurant | Lights | T24 2022 - Appendix 5.4B Updated based on the equipment schedule from the plug load and schedule project with CEC | Weekday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.3 | 0.67 | 0.73 | 0.75 | 0.85 | 0.85 | 0.85 | 0.83 | 0.72 | 0.65 | 0.67 | 0.75 | 0.85 | 0.85 | 0.85 | 0.75 | 0.57 | 0.3
|  |  |  | Saturday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.3 | 0.67 | 0.73 | 0.75 | 0.85 | 0.85 | 0.85 | 0.83 | 0.72 | 0.65 | 0.67 | 0.75 | 0.85 | 0.85 | 0.85 | 0.75 | 0.57 | 0.3
|  |  |  | Sunday | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.67 | 0.73 | 0.75 | 0.85 | 0.85 | 0.85 | 0.83 | 0.72 | 0.65 | 0.67 | 0.75 | 0.85 | 0.85 | 0.85 | 0.75 | 0.57 | 0.3
Dining and Café | Restaurant | ElecEuipment | Plug load and schedules project with CEC, 2025 | Weekday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.3 | 0.72 | 0.78 | 0.8 | 0.9 | 0.9 | 0.9 | 0.88 | 0.77 | 0.7 | 0.72 | 0.8 | 0.9 | 0.9 | 0.9 | 0.8 | 0.62 | 0.3
|  |  |  | Saturday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.3 | 0.72 | 0.78 | 0.8 | 0.9 | 0.9 | 0.9 | 0.88 | 0.77 | 0.7 | 0.72 | 0.8 | 0.9 | 0.9 | 0.9 | 0.8 | 0.62 | 0.3
|  |  |  | Sunday | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.72 | 0.78 | 0.8 | 0.9 | 0.9 | 0.9 | 0.88 | 0.77 | 0.7 | 0.72 | 0.8 | 0.9 | 0.9 | 0.9 | 0.8 | 0.62 | 0.3
Dining and Café | Restaurant | HVACAvail | T24 2022 - Appendix 5.4B Updated based on the adopted PNNL occupancy | Weekday | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Saturday | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Sunday | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Dining and Café | Restaurant | ServiceHotWater | T24 2022 - Appendix 5.4B Updated based on the adopted PNNL occupancy | Weekday | 0.2 | 0 | 0 | 0 | 0 | 0.6 | 0.6 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25
|  |  |  | Saturday | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3
|  |  |  | Sunday | 0.25 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2
Dining and Café | Restaurant | Infiltration | T24 2022 - Appendix 5.4B Updated based on the adopted PNNL occupancy | Weekday | 0.25 | 0 | 0 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  |  | Saturday | 0.25 | 0 | 0 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  |  | Sunday | 0.25 | 0 | 0 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Dining and Café | Restaurant | HtgSetpt | T24 2022 - Appendix 5.4B, [Restaurant] | Weekday | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
|  |  |  | Saturday | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
|  |  |  | Sunday | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
Dining and Café | Restaurant | ClgSetpt | T24 2022 - Appendix 5.4B, [Restaurant] | Weekday | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
|  |  |  | Saturday | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
|  |  |  | Sunday | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
Kitchen
Kitchen | Kitchen | occupancy | PNNL,ASHRAE 90.1, 2022 Fast Food Restaurant prototype (It has higher occupancy rate during morning compared to T24 2022 - Appendix 5.4B) | Weekday | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.4 | 0.4 | 0.4 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.8 | 0.8 | 0.8 | 0.5 | 0.35 | 0.2
|  |  |  | Saturday | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.4 | 0.2 | 0.45 | 0.5 | 0.5 | 0.35 | 0.3 | 0.3 | 0.3 | 0.7 | 0.9 | 0.7 | 0.65 | 0.55 | 0.35
|  |  |  | Sunday | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.3 | 0.2 | 0.25 | 0.35 | 0.55 | 0.65 | 0.7 | 0.35 | 0.2 | 0.2
Kitchen | Kitchen | Lights | T24 2022 - Appendix 5.4B, [Restaurant] Updated based on the equipment schedule from the plug load and schedule project with CEC | Weekday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.3 | 0.67 | 0.73 | 0.75 | 0.85 | 0.85 | 0.85 | 0.83 | 0.72 | 0.65 | 0.67 | 0.75 | 0.85 | 0.85 | 0.85 | 0.75 | 0.57 | 0.3
|  |  |  | Saturday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.3 | 0.67 | 0.73 | 0.75 | 0.85 | 0.85 | 0.85 | 0.83 | 0.72 | 0.65 | 0.67 | 0.75 | 0.85 | 0.85 | 0.85 | 0.75 | 0.57 | 0.3
|  |  |  | Sunday | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.67 | 0.73 | 0.75 | 0.85 | 0.85 | 0.85 | 0.83 | 0.72 | 0.65 | 0.67 | 0.75 | 0.85 | 0.85 | 0.85 | 0.75 | 0.57 | 0.3
Kitchen | Kitchen | ElecEquipment | Plug load and schedules project with CEC, 2025 | Weekday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.3 | 0.72 | 0.78 | 0.8 | 0.9 | 0.9 | 0.9 | 0.88 | 0.77 | 0.7 | 0.72 | 0.8 | 0.9 | 0.9 | 0.9 | 0.8 | 0.62 | 0.3
|  |  |  | Saturday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.3 | 0.72 | 0.78 | 0.8 | 0.9 | 0.9 | 0.9 | 0.88 | 0.77 | 0.7 | 0.72 | 0.8 | 0.9 | 0.9 | 0.9 | 0.8 | 0.62 | 0.3
|  |  |  | Sunday | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.72 | 0.78 | 0.8 | 0.9 | 0.9 | 0.9 | 0.88 | 0.77 | 0.7 | 0.72 | 0.8 | 0.9 | 0.9 | 0.9 | 0.8 | 0.62 | 0.3
Kitchen | Kitchen | HVACAvail | T24 2022 - Appendix 5.4B , [Restaurant] Updated based on the adopted PNNL occupancy | Weekday | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Saturday | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Sunday | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Kitchen | Kitchen | ServiceHotWater | T24 2022 - Appendix 5.4B Updated based on the adopted PNNL occupancy | Weekday | 0.2 | 0 | 0 | 0 | 0 | 0.6 | 0.6 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25
|  |  |  | Saturday | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3
|  |  |  | Sunday | 0.25 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2
Kitchen | Kitchen | Infiltration | T24 2022 - Appendix 5.4B, [Restaurant] Updated based on the adopted PNNL occupancy | Weekday | 0.25 | 0 | 0 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  |  | Saturday | 0.25 | 0 | 0 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  |  | Sunday | 0.25 | 0 | 0 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Kitchen | Kitchen | ExhaustHoodEqualOrLessThan5000cfm | T24 2022 - Appendix 5.4B, [Restaurant] Updated based on the adopted PNNL occupancy | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
Kitchen | Kitchen | ExhaustHoodGreaterThan 5000cfm | T24 2022 - Appendix 5.4B, [Restaurant] Updated based on the adopted PNNL occupancy | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 0.5 | 1 | 0.5 | 1 | 0.5 | 1 | 0.5 | 1 | 0.5 | 1 | 0.5 | 1 | 0.5 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 0.5 | 1 | 0.5 | 1 | 0.5 | 1 | 0.5 | 1 | 0.5 | 1 | 0.5 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 0.5 | 1 | 0.5 | 1 | 0.5 | 1 | 0.5 | 1 | 0.5 | 1 | 0.5 | 0 | 0 | 0 | 0 | 0
Kitchen | Kitchen | Refrigeration | T24 2022 - Appendix 5.4B, [Restaurant] | Weekday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Saturday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Sunday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
Kitchen | Kitchen | GasEquipment | T24 2022 - Appendix 5.4B, [Restaurant] Updated based on the equipment schedule from the plug load and schedule project with CEC | Weekday | 0.5 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.75 | 0.75 | 0.75 | 0.9 | 0.9 | 0.9 | 0.9 | 0.75 | 0.5 | 0.5
|  |  |  | Saturday | 0.5 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.75 | 0.75 | 0.75 | 0.9 | 0.9 | 0.9 | 0.9 | 0.75 | 0.75 | 0.5
|  |  |  | Sunday | 0.5 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.75 | 0.75 | 0.75 | 0.9 | 0.9 | 0.9 | 0.9 | 0.75 | 0.5 | 0.5
Kitchen | Kitchen | HtgSetpt | Thermostat Setpoints of PNNL 09.1, 2022 Restaurant prototype and HVAC availability schedule of CEC Restaurant prototype | Weekday | 60 | 60 | 60 | 60 | 60 | 66 | 60 | 66 | 60 | 66 | 60 | 66 | 60 | 66 | 60 | 66 | 60 | 66 | 60 | 60 | 60 | 60 | 60 | 60
|  |  |  | Saturday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 66 | 60 | 66 | 60 | 66 | 60 | 66 | 60 | 66 | 60 | 66 | 60 | 60 | 60 | 60 | 60 | 60
|  |  |  | Sunday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 66 | 60 | 66 | 60 | 66 | 60 | 66 | 60 | 66 | 60 | 66 | 60 | 60 | 60 | 60 | 60 | 60
Kitchen | Kitchen | ClgSetpt | Thermostat Setpoints of PNNL 09.1, 2022 Restaurant prototype and HVAC availability schedule of CEC Restaurant prototype | Weekday | 86 | 86 | 86 | 86 | 86 | 79 | 86 | 79 | 86 | 79 | 86 | 79 | 86 | 79 | 86 | 79 | 86 | 79 | 86 | 86 | 86 | 86 | 86 | 86
|  |  |  | Saturday | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 79 | 86 | 79 | 86 | 79 | 86 | 79 | 86 | 79 | 86 | 79 | 86 | 86 | 86 | 86 | 86 | 86
|  |  |  | Sunday | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 79 | 86 | 79 | 86 | 79 | 86 | 79 | 86 | 79 | 86 | 79 | 86 | 86 | 86 | 86 | 86 | 86

## Energy Usage
CalBEM Energy Consumption - Outpatient | [11 empty] | Energy Consumption - Outpatient
Prototype | CZ | CalBEM Electricity EUI (KBTU/ft²) | CalBEM Gas EUI (KBTU/ft²) | CalBEM Total EUI (KBTU/ft²) | New Construction Electricity EUI (KBTU/ft²) | New Construction Gas EUI (KBTU/ft²) | New Construction Total EUI (KBTU/ft²) | National Average | Acceptable Range (25% Higher) | Acceptable Range (25% Lower) | National Average Acceptable EUI Range | Prototype | CZ | Total Floorspace (Thousand of ft²) | CEUS 2023 Electricity EUI (kBtu/ft²) | CEUS 2023 Gas EUI (kBtu/ft²) | CEUS 2023 Total EUI (kBtu/ft²) | Acceptable Range (25% Higher) | Acceptable Range (25% Lower) | CEUS 2022 Acceptable EUI Range
Outpatient | 1 | 49.4 | 39 | 88.4 | 29.1 | 28.5 | 57.7 | 108 | 135 | 81 | 54 | Outpatient | 1 | 7059 | 70.9802 | 51.1577 | 122.1379 | 152.6724 | 91.6034 | 61.069
| 2 | 57.6 | 32.5 | 90.2 | 32.1 | 23 | 55.2 | 106.4 | 133 | 79.8 | 53.2 |  | 2 | 14514 | 45.6312 | 53.4755 | 99.1067 | 123.8834 | 74.33 | 49.5533
| 3 | 55.2 | 28.2 | 83.4 | 30.8 | 20.9 | 51.7 | 104.6 | 130.75 | 78.45 | 52.3 |  | 3 | 56689 | 53.4877 | 48.1605 | 101.6482 | 127.0603 | 76.2362 | 50.8241
| 4 | 62.2 | 30.9 | 93.1 | 33.8 | 21.2 | 55 | 111.8 | 139.75 | 83.85 | 55.9 |  | 4 | 29372 | 54.7559 | 50.1593 | 104.9152 | 131.1441 | 78.6864 | 52.4576
| 5 | 56.2 | 28.3 | 84.5 | 31.4 | 20.3 | 51.7 | 103.8 | 129.75 | 77.85 | 51.9 |  | 5 | 5067 | 39.8282 | 24.8165 | 64.6447 | 80.8058 | 48.4835 | 32.3223
| 6 | 59.7 | 17 | 76.6 | 32.8 | 12.1 | 44.9 | 107.3 | 134.125 | 80.475 | 53.65 |  | 6 | 32891 | 54.9321 | 75.4764 | 130.4085 | 163.0106 | 97.8064 | 65.2042
| 7 | 58.9 | 14.7 | 73.7 | 33 | 10.8 | 43.7 | 108.5 | 135.625 | 81.375 | 54.25 |  | 7 | 31754 | 74.8437 | 45.4861 | 120.3298 | 150.4123 | 90.2474 | 60.1649
| 8 | 65.2 | 17.6 | 82.8 | 34.5 | 11.7 | 46.2 | 113.6 | 142 | 85.2 | 56.8 |  | 8 | 50355 | 56.5439 | 86.9115 | 143.4554 | 179.3193 | 107.5916 | 71.7277
| 9 | 65.8 | 19.5 | 85.4 | 34.8 | 12.8 | 47.5 | 113.1 | 141.375 | 84.825 | 56.55 |  | 9 | 72118 | 45.2257 | 63.3727 | 108.5983 | 135.7479 | 81.4488 | 54.2992
| 10 | 65.3 | 19.2 | 84.5 | 35.9 | 13.1 | 49 | 110.1 | 137.625 | 82.575 | 55.05 |  | 10 | 55175 | 66.7723 | 63.834 | 130.6063 | 163.2578 | 97.9547 | 65.3031
| 11 | 64.1 | 28.7 | 92.8 | 35.8 | 20.4 | 56.2 | 119.3 | 149.125 | 89.475 | 59.65 |  | 11 | 20961 | 67.7136 | 42.2205 | 109.9341 | 137.4176 | 82.4506 | 54.967
| 12 | 59.5 | 28.2 | 87.7 | 33.5 | 20.2 | 53.6 | 115.6 | 144.5 | 86.7 | 57.8 |  | 12 | 93863 | 69.3375 | 42.635 | 111.9726 | 139.9657 | 83.9794 | 55.9863
| 13 | 62.2 | 23 | 85.2 | 35.3 | 16.8 | 52.1 | 121.5 | 151.875 | 91.125 | 60.75 |  | 13 | 30306 | 75.5934 | 48.3022 | 123.8956 | 154.8695 | 92.9217 | 61.9478
| 14 | 68.6 | 29.9 | 98.5 | 37.7 | 20 | 57.7 | 119.9 | 149.875 | 89.925 | 59.95 |  | 14 | 13400 | 63.1769 | 77.509 | 140.6859 | 175.8574 | 105.5144 | 70.3429
| 15 | 76.4 | 13.8 | 90.2 | 41.9 | 9.4 | 51.2 | 137.9 | 172.375 | 103.425 | 68.95 |  | 15 | 24206 | 61.2178 | 63.6567 | 124.8745 | 156.0932 | 93.6559 | 62.4373
| 16 | 57.9 | 39 | 96.9 | 34.3 | 27.1 | 61.4 | 113.1 | 141.375 | 84.825 | 56.55 |  | 16 | 57915 | 72.2681 | 64.3832 | 136.6513 | 170.8142 | 102.4885 | 68.3257
Ref: CEUS 2022 Report
And converted FZ level data to CZ level
CEUS has only one category for healthcare.
Background Data [To be deleted prior to publication]

## Weights
% of Floor Area per CZ and Vintage Bin - Outpatient | [7 empty] | % of Floor Area per CZ and Vintage Bin - Outpatient
Prototype | CZ | Vintage Bin | [5 empty] | Prototype | Vintage Bin | CZ
|  | Pre-1978 | 1978-1997 | 1998-2007 | 2008-2018 | Not available |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
Outpatient | 1 | 36% | 16% | 17% | 26% | 5% | 100% | Outpatient | Pre-1978 | 1% | 3% | 7% | 4% | 0% | 8% | 5% | 12% | 19% | 8% | 3% | 13% | 4% | 2% | 3% | 8% | 100%
| 2 | 46% | 19% | 15% | 18% | 3% | 101% |  | 1978-1997 | 1% | 2% | 13% | 7% | 2% | 5% | 8% | 6% | 8% | 12% | 3% | 15% | 3% | 2% | 5% | 9% | 101%
| 3 | 27% | 37% | 20% | 10% | 6% | 100% |  | 1998-2007 | 1% | 3% | 14% | 7% | 2% | 6% | 5% | 9% | 7% | 5% | 4% | 21% | 6% | 2% | 0% | 8% | 100%
| 4 | 28% | 37% | 19% | 10% | 6% | 100% |  | 2008-2018 | 2% | 3% | 7% | 4% | 0% | 1% | 3% | 1% | 5% | 11% | 6% | 23% | 10% | 2% | 6% | 16% | 100%
| 5 | 10% | 51% | 33% | 6% | 0% | 100% |  | Not available | 1% | 1% | 7% | 4% | 0% | 4% | 1% | 9% | 15% | 12% | 2% | 10% | 9% | 3% | 10% | 11% | 99%
| 6 | 53% | 24% | 15% | 3% | 6% | 101% |  | Total | 1% | 2% | 10% | 5% | 1% | 6% | 5% | 8% | 12% | 9% | 4% | 16% | 5% | 2% | 4% | 10%
| 7 | 35% | 43% | 14% | 8% | 1% | 101%
| 8 | 55% | 21% | 15% | 2% | 8% | 101%
| 9 | 59% | 18% | 8% | 6% | 9% | 100%
| 10 | 32% | 35% | 7% | 16% | 10% | 100%
| 11 | 33% | 23% | 18% | 22% | 5% | 101%
| 12 | 32% | 26% | 19% | 19% | 5% | 101%
| 13 | 30% | 14% | 18% | 26% | 13% | 101%
| 14 | 40% | 26% | 12% | 12% | 10% | 100%
| 15 | 27% | 36% | 1% | 19% | 18% | 101%
| 16 | 33% | 24% | 12% | 23% | 8% | 100%
| Statewide | 40% | 29% | 15% | 10% | 7%
Ref: CEUS 2022 dataset
And converted FZ level data to CZ level
CEUS has only one category for healthcare.
Background Data [To be deleted prior to publication]

## PV (hidden)
PV - Outpatient
TBD

## EV Charger (hidden)
EV Charger - Outpatient
TBD
Background Data [To be deleted prior to publication]

## Data (hidden)
Space Function | Electric Equipment Load Intensity | Electric Equipment Load Intensity | LPD
Aging Eye/Low-vision (Corridor Area) |  |  | 2013 | 2016 | 2019 | 2025
Aging Eye/Low-vision (Dining)
Aging Eye/Low-vision (Lobby, Main Entry)
Aging Eye/Low-vision (Lounge/Waiting Area)
Aging Eye/Low-vision (Multipurpose Room)
Aging Eye/Low-vision (Religious Worship Area)
Aging Eye/Low-vision (Restroom)
Aging Eye/Low-vision (Stairwell)
Audience Seating Area
Auditorium Area
Auto Repair / Maintenance Area
Barber, Beauty Salon, Spa Area
Civic Meeting Place Area
Classroom, Lecture, Training, Vocational Areas
Concourse and Atria Area
Convention, Conference, Multipurpose and Meeting Area
Copy Room
Corridor Area
Dining Area (Bar/Lounge and Fine Dining)
Dining Area (Cafeteria/Fast Food)
Dining Area (Family and Leisure)
Electrical, Mechanical, Telephone Rooms
Exercise/Fitness Center and Gymnasium Areas
Financial Transaction Area
Healthcare Facility and Hospitals (Exam/Treatment Room)
Healthcare Facility and Hospitals (Imaging Room)
Healthcare Facility and Hospitals (Medical Supply Room)
Healthcare Facility and Hospitals (Nursery)
Healthcare Facility and Hospitals (Nurse's Station)
Healthcare Facility and Hospitals (Operating Room)
Healthcare Facility and Hospitals (Patient Room)
Healthcare Facility and Hospitals (Physical Therapy Room)
Healthcare Facility and Hospitals (Recovery Room)
Hotel Function Area
Kitchen/Food Preparation Area
Kitchenette or Residential Kitchen
Laboratory, Scientific
Laundry Area
Library (Reading Area)
Library (Stacks Area)
Lobby, Main Entry
Locker Room
Lounge, Breakroom, or Waiting Area
Manufacturing, Commercial & Industrial Work Area (Low Bay)
Manufacturing, Commercial & Industrial Work Area (High Bay)
Manufacturing, Commercial & Industrial Work Area (Precision)
Museum Area (Exhibition/Display)
Museum Area (Restoration Room)
Office Area (>250 square feet)
Office Area (<250 square feet)
Parking Garage Area (Parking Zone and Ramps)
Parking Garage Area (Daylight Adaptation Zones)
Pharmacy Area
Retail Sales Area (Grocery Sales)
Retail Sales Area (Retail Merchandise Sales)
Retail Sales Area (Fitting Room)
Religious Worship Area
Restrooms
Stairwell
Storage, Commercial/Industrial (Warehouse)
Storage, Commercial/Industrial (Refrigerated)
Storage, Commercial/Industrial (Shipping & Handling)
Storage (General)
Sports Arena - Playing Area (> 5,000 Spectators)
Sports Arena - Playing Area (2,000 - 5,000 Spectators)
Sports Arena - Playing Area (< 2,000 Spectators)
Sports Arena - Playing Area (Recreational)
Theater Area (Motion Picture)
Theater Area (Performance)
Transportation Function (Baggage Area)
Transportation Function (Ticketing Area)
Videoconferencing Studio
High-Rise Residential Living Spaces
Hotel/Motel Guest Room
All other
Attic
Reception area
Elevator
Plenum
IT Room (EPD 12)
Computer Room (EPD 20)
Server Room (EPD 45)