## Notes
Data Sources
Dataset | Dodge 2023
CEUS 2022
ComStock 2023
Prototype | CEC School prototype (CBECC 2022.3.1) | https://bees.noresco.com/software2022.html
Codes | Title 24, part 6, referred to as T24 (1984, 2001, 2007, 2013, 2016, 2022, 2025)
ASHRAE 90.1 (2022)
CFR Title 10 (2008, 2010, 2025)
ACM 2022
| T24 2022 - Appendix 5.4A and Appendix 5.4B | https://www.energy.ca.gov/publications/2022/2022-nonresidential-and-multifamily-alternative-calculation-method-reference
Other | 2022 Reduced infiltration CASE report | https://title24stakeholders.com/wp-content/uploads/2020/10/2022-T24-Final-CASE-Report_Reduce-Infiltration.pdf
| 2019 Outdoor Lighting CASE Report | https://title24stakeholders.com/wp-content/uploads/2016/10/T24-2019-CASE-Study-Results-Report-Outdoor-Sources_Final_with-Attachments.pdf
| 2019 High Efficiency Fume Hoods in Laboratory Spaces CASE Report | https://title24stakeholders.com/wp-content/uploads/2017/09/2019-T24-CASE-Report_Fume-Hoods_Final_September-2017.pdf?
| PNNL 20405, 2010 | file:///N:/Prj_SUS/2023/S23668%20SCE%20CA%20Prototypes%20Development/Technical/NR/0_Input%20data/Lighting/PNNL-20405.pdf
| Air leakage Memo, NORESCO, 2025 | Infiltration_rate_report_14May2025-Short-Version.docx
Construction Rate
Notes
2025 T24 | School Building includes four individual buildings, including north classroom, westclassroom, kindergarten, and MPR/Admin.

## Prototype
NORESCO, Updated September 2025
SchoolK-8
Characteristic | Value | Data Sources
Building Type | K-8 School
Building Category | Nonresidential
Vintages | 4 Vintages: Pre-1978, 1978-1997,1998-2007, 2008-2018 New Construction (2019+) | Based on the vintage bin analysis | NonRes-Vintage bins-Draft Report-30Nov2023-Final.docx
Shape |  | The analysis uses prototype geometry originally developed by CEC.
Total Floor Area (ft²) | 49979.36 | Same as CEC
Aspect Ratio | It varies for different buildings. | Same as CEC
Number of Floors | It varies for different buildings. | Same as CEC
Roof type | Flat | Same as CEC
WWR | 7.08% | Same as CEC
Shading Geometry | No Shades | Same as CEC
Floor to floor height (feet) | It varies for different buildings: MPR/Admin: 14-25 Other buildings: 14 ft | Same as CEC
Floor to ceiling height (feet) | It varies for different buildings: MPR/Admin: 14-25 Other buildings: 14 ft | Same as CEC
Glazing sill height (feet) | It varies for different buildings. | Same as CEC
Above grade wall area (ft²) | 42450.09
Gross wall area (ft²) | 42450.09
Roof area (ft²) | 37687.78
Underground Gross Wall Area (ft²) | 0

## Zones
Proposed Layout - K-8 School
Space Type | Space/Thermal Zone | HVAC System Name/AHU Name | Schedule Category | Conditioned (Y/N) | Area Fraction | Area (ft²) | Volume (ft³) | Multipliers | Number of People | People (Persons/1,000 ft²) [T24, 2025,Table 120.1-A]
Lounge, Breakroom, or Waiting Area | Admin/MPR_Breakroom_Zn | AHU-1 | MPR | Y | 1.151% | 575.2 | 353.2 | 1 | 37.9632 | 66
Convention, Conference, Multipurpose and Meeting Area | Admin/MPR_Conference Room Zns 3_Zn | AHU-2 | MPR | Y | 3.351% | 1674.74 | 353.2 | 1 | 110.5328 | 66
Corridor Area | Admin/MPR_Corridor_Zn | AHU-3 | MPR | Y | 2.324% | 1161.52 | 353.2 | 1 | 11.6152 | 10
Electrical, Mechanical, Telephone Rooms | Admin/MPR_EMT_Zn | AHU-4 | MPR | Y | 0.5566% | 278.21 | 353.2 | 1 | 2.7821 | 10
Electrical, Mechanical, Telephone Rooms | Admin/MPR_IDF Room_Zn | AHU-5 | MPR | Y | 0.6807% | 340.23 | 353.2 | 1 | 3.4023 | 10
Kitchen/Food Preparation Area | Admin/MPR_Kitchen_Zn | AHU-6 | Kitchen | Y | 2.916% | 1457.25 | 353.2 | 1 | 8.7435 | 6
Lobby, Main Entry | Admin/MPR_Lobby_Zn | AHU-7 | MPR | Y | 2.484% | 1241.47 | 353.2 | 1 | 81.937 | 66
Convention, Conference, Multipurpose and Meeting Area | Admin/MPR_Multipurpose Room Zns 3_Zn | AHU-8 | MPR | Y | 11.03% | 5512.19 | 137811.47 | 1 | 363.8045 | 66
Office Area (<250 square feet) | Admin/MPR_Office - LT 250 sf Zns 6_Zn | AHU-9 | MPR | Y | 2.098% | 1048.35 | 353.2 | 1 | 10.4835 | 10
Restrooms | Admin/MPR_Restroom Zns 3_Zn | AHU-10 | MPR | Y | 1.803% | 901.17 | 12617.05 | 1 | 9.0117 | 10
Storage (General) | Admin/MPR_Storage - General_Zn | AHU-11 | MPR | Y | 2.496% | 1247.73 | 353.2 | 1 | 12.4773 | 10
Storage, Commercial/Industrial (Refrigerated) | Admin/MPR_Storage - Refrigerated_Zn | AHU-12 | MPR | Y | 0.5036% | 251.72 | 353.2 | 1 | 0 | 0
Theater Area (Performance) | Admin/MPR_Theater - Performance_Zn | AHU-13 | MPR | Y | 2.132% | 1065.56 | 353.2 | 1 | 70.327 | 66
Classroom, Lecture, Training, Vocational Areas | Classrm N_Flr 1_Classroom-01_Zn | AHU-14 | Classroom | Y | 2.004% | 1001.75 | 353.2 | 1 | 50.0875 | 50
Classroom, Lecture, Training, Vocational Areas | Classrm N_Flr 1_Classroom-02 Zns 6_Zn | AHU-15 | Classroom | Y | 12.11% | 6054.03 | 353.2 | 1 | 302.7015 | 50
Office Area (<250 square feet) | Classrm N_Flr 1_Office - LT 250 sf_Zn | AHU-16 | Classroom | Y | 0.5765% | 288.13 | 353.2 | 1 | 2.8813 | 10
Restrooms | Classrm N_Flr 1_Restroom_Zn | AHU-17 | Classroom | Y | 1.066% | 532.7 | 353.2 | 1 | 5.327 | 10
Classroom, Lecture, Training, Vocational Areas | Classrm N_Flr 2_Classroom-01 Zns 6_Zn | AHU-18 | Classroom | Y | 12.11% | 6054.03 | 353.2 | 1 | 302.7015 | 50
Classroom, Lecture, Training, Vocational Areas | Classrm N_Flr 2_Classroom-02_Zn | AHU-19 | Classroom | Y | 2.004% | 1001.75 | 353.2 | 1 | 50.0875 | 50
Office Area (<250 square feet) | Classrm N_Flr 2_Office - LT 250 sf_Zn | AHU-20 | Classroom | Y | 0.5765% | 288.13 | 353.2 | 1 | 2.8813 | 10
Restrooms | Classrm N_Flr 2_Restroom_Zn | AHU-21 | Classroom | Y | 1.066% | 532.7 | 353.2 | 1 | 5.327 | 10
Classroom, Lecture, Training, Vocational Areas | Classrm W_Flr 1_Classroom Zns 2_Zn | AHU-22 | Classroom | Y | 4.112% | 2054.94 | 28770.52 | 1 | 102.747 | 50
Electrical, Mechanical, Telephone Rooms | Classrm W_Flr 1_EMT-01_Zn | AHU-23 | Classroom | Y | 0.2421% | 121.01 | 353.2 | 1 | 1.2101 | 10
Electrical, Mechanical, Telephone Rooms | Classrm W_Flr 1_EMT-02_Zn | AHU-24 | Classroom | Y | 0.1961% | 98.01 | 353.2 | 1 | 0.9801 | 10
Library (Reading Area) | Classrm W_Flr 1_Library - Reading Area_Zn | AHU-25 | Classroom | Y | 2.395% | 1197.13 | 353.2 | 1 | 23.9426 | 20
Restrooms | Classrm W_Flr 1_Restroom_Zn | AHU-26 | Classroom | Y | 1.127% | 563.05 | 353.2 | 1 | 5.6305 | 10
Storage (General) | Classrm W_Flr 1_Storage - General_Zn | AHU-27 | Classroom | Y | 0.762% | 380.84 | 353.2 | 1 | 3.8084 | 10
Classroom, Lecture, Training, Vocational Areas | Classrm W_Flr 2_Classroom-01 Zns 3_Zn | AHU-28 | Classroom | Y | 6.507% | 3252.06 | 353.2 | 1 | 162.603 | 50
Classroom, Lecture, Training, Vocational Areas | Classrm W_Flr 2_Classroom-02_Zn | AHU-29 | Classroom | Y | 0.762% | 380.84 | 353.2 | 1 | 19.042 | 50
Electrical, Mechanical, Telephone Rooms | Classrm W_Flr 2_IDF Room_Zn | AHU-30 | Classroom | Y | 0.2421% | 121.01 | 353.2 | 1 | 1.2101 | 10
Restrooms | Classrm W_Flr 2_Restroom_Zn | AHU-31 | Classroom | Y | 1.127% | 563.05 | 353.2 | 1 | 5.6305 | 10
Storage (General) | Classrm W_Flr 2_Storage - General_Zn | AHU-32 | Classroom | Y | 0.1961% | 98.01 | 353.2 | 1 | 0.9801 | 10
Classroom, Lecture, Training, Vocational Areas | Kindergarten_Classroom-01_Zn | AHU-33 | Classroom | Y | 10.99% | 5494.54 | 353.2 | 1 | 274.727 | 50
Classroom, Lecture, Training, Vocational Areas | Kindergarten_Classroom-02_Zn | AHU-34 | Classroom | Y | 2.881% | 1440.14 | 353.2 | 1 | 72.007 | 50
Electrical, Mechanical, Telephone Rooms | Kindergarten_EMT_Zn | AHU-35 | Classroom | Y | 0.3419% | 170.87 | 353.2 | 1 | 1.7087 | 10
Electrical, Mechanical, Telephone Rooms | Kindergarten_IDF Room_Zn | AHU-36 | Classroom | Y | 0.171% | 85.48 | 353.2 | 1 | 0.8548 | 10
Restrooms | Kindergarten_Restroom_Zn | AHU-37 | Classroom | Y | 0.5323% | 266.03 | 353.2 | 1 | 2.6603 | 10
Storage (General) | Kindergarten_Storage - General_Zn | AHU-38 | Classroom | Y | 2.369% | 1183.8 | 353.2 | 1 | 11.838 | 10
Total (15 Space types) | Total (38 spaces) | Total ( 5 HVAC zones) | Total (4 Schedule categories)) | Total (38 Conditioned zones) | 100% | 49979.37 | 191561.04 |  | 2136.655
Background Data [To be deleted prior to publication]
[11 empty] | Fraction Convected | Sensible Fraction Calculation | Activity level | ASHRAE 55 Warnings | Carbon Dioxide Generation Rate | Nominal Minimum Number of People | Nominal Maximum Number of People
[11 empty] | 0.7 | 0.5 | ADMIN/MPR_BREAKROOM PEOPLE ACTIVITY LEVEL | No | 3.82e-08 | 0 | 19
[11 empty] | 0.7 | 0.613 | ADMIN/MPR_CONFERENCE ROOM ZNS 3 PEOPLE ACTIVITY LEVEL | No | 3.82e-08 | 0 | 55
[11 empty] | 0.7 | 0.5 | ADMIN/MPR_CORRIDOR PEOPLE ACTIVITY LEVEL | No | 3.82e-08 | 0 | 6
[11 empty] | 0.7 | 0.5 | ADMIN/MPR_EMT PEOPLE ACTIVITY LEVEL | No | 3.82e-08 | 0 | 1
[11 empty] | 0.7 | 0.5 | ADMIN/MPR_IDF ROOM PEOPLE ACTIVITY LEVEL | No | 3.82e-08 | 0 | 2
[11 empty] | 0.7 | 0.367 | ADMIN/MPR_KITCHEN PEOPLE ACTIVITY LEVEL | No | 3.82e-08 | 0 | 4
[11 empty] | 0.7 | 0.5 | ADMIN/MPR_LOBBY PEOPLE ACTIVITY LEVEL | No | 3.82e-08 | 0 | 41
[11 empty] | 0.7 | 0.613 | ADMIN/MPR_MULTIPURPOSE ROOM ZNS 3 PEOPLE ACTIVITY LEVEL | No | 3.82e-08 | 0 | 182
[11 empty] | 0.7 | 0.556 | ADMIN/MPR_OFFICE - LT 250 SF ZNS 6 PEOPLE ACTIVITY LEVEL | No | 3.82e-08 | 0 | 5
[11 empty] | 0.7 | 0.5 | ADMIN/MPR_RESTROOM ZNS 3 PEOPLE ACTIVITY LEVEL | No | 3.82e-08 | 0 | 5
[11 empty] | 0.7 | 0.556 | ADMIN/MPR_STORAGE - GENERAL PEOPLE ACTIVITY LEVEL | No | 3.82e-08 | 0 | 6
[11 empty] | 0.7 | 0.7 | ADMIN/MPR_THEATER - PERFORMANCE PEOPLE ACTIVITY LEVEL | No | 3.82e-08 | 0 | 35
[11 empty] | 0.7 | 0.613 | CLASSRM N_FLR 1_CLASSROOM-01 PEOPLE ACTIVITY LEVEL | No | 3.82e-08 | 0 | 25
[11 empty] | 0.7 | 0.613 | CLASSRM N_FLR 1_CLASSROOM-02 ZNS 6 PEOPLE ACTIVITY LEVEL | No | 3.82e-08 | 0 | 151
[11 empty] | 0.7 | 0.556 | CLASSRM N_FLR 1_OFFICE - LT 250 SF PEOPLE ACTIVITY LEVEL | No | 3.82e-08 | 0 | 1
[11 empty] | 0.7 | 0.5 | CLASSRM N_FLR 1_RESTROOM PEOPLE ACTIVITY LEVEL | No | 3.82e-08 | 0 | 3
[11 empty] | 0.7 | 0.613 | CLASSRM N_FLR 2_CLASSROOM-01 ZNS 6 PEOPLE ACTIVITY LEVEL | No | 3.82e-08 | 0 | 151
[11 empty] | 0.7 | 0.613 | CLASSRM N_FLR 2_CLASSROOM-02 PEOPLE ACTIVITY LEVEL | No | 3.82e-08 | 0 | 25
[11 empty] | 0.7 | 0.556 | CLASSRM N_FLR 2_OFFICE - LT 250 SF PEOPLE ACTIVITY LEVEL | No | 3.82e-08 | 0 | 1
[11 empty] | 0.7 | 0.5 | CLASSRM N_FLR 2_RESTROOM PEOPLE ACTIVITY LEVEL | No | 3.82e-08 | 0 | 3
[11 empty] | 0.7 | 0.613 | CLASSRM W_FLR 1_CLASSROOM ZNS 2 PEOPLE ACTIVITY LEVEL | No | 3.82e-08 | 0 | 51
[11 empty] | 0.7 | 0.5 | CLASSRM W_FLR 1_EMT-01 PEOPLE ACTIVITY LEVEL | No | 3.82e-08 | 0 | 1
[11 empty] | 0.7 | 0.5 | CLASSRM W_FLR 1_EMT-02 PEOPLE ACTIVITY LEVEL | No | 3.82e-08 | 0 | 0
[11 empty] | 0.7 | 0.556 | CLASSRM W_FLR 1_LIBRARY - READING AREA PEOPLE ACTIVITY LEVEL | No | 3.82e-08 | 0 | 12
[11 empty] | 0.7 | 0.5 | CLASSRM W_FLR 1_RESTROOM PEOPLE ACTIVITY LEVEL | No | 3.82e-08 | 0 | 3
[11 empty] | 0.7 | 0.556 | CLASSRM W_FLR 1_STORAGE - GENERAL PEOPLE ACTIVITY LEVEL | No | 3.82e-08 | 0 | 2
[11 empty] | 0.7 | 0.613 | CLASSRM W_FLR 2_CLASSROOM-01 ZNS 3 PEOPLE ACTIVITY LEVEL | No | 3.82e-08 | 0 | 81
[11 empty] | 0.7 | 0.613 | CLASSRM W_FLR 2_CLASSROOM-02 PEOPLE ACTIVITY LEVEL | No | 3.82e-08 | 0 | 10
[11 empty] | 0.7 | 0.5 | CLASSRM W_FLR 2_IDF ROOM PEOPLE ACTIVITY LEVEL | No | 3.82e-08 | 0 | 1
[11 empty] | 0.7 | 0.5 | CLASSRM W_FLR 2_RESTROOM PEOPLE ACTIVITY LEVEL | No | 3.82e-08 | 0 | 3
[11 empty] | 0.7 | 0.556 | CLASSRM W_FLR 2_STORAGE - GENERAL PEOPLE ACTIVITY LEVEL | No | 3.82e-08 | 0 | 0
[11 empty] | 0.7 | 0.613 | KINDERGARTEN_CLASSROOM-01 PEOPLE ACTIVITY LEVEL | No | 3.82e-08 | 0 | 137
[11 empty] | 0.7 | 0.613 | KINDERGARTEN_CLASSROOM-02 PEOPLE ACTIVITY LEVEL | No | 3.82e-08 | 0 | 36
[11 empty] | 0.7 | 0.5 | KINDERGARTEN_EMT PEOPLE ACTIVITY LEVEL | No | 3.82e-08 | 0 | 1
[11 empty] | 0.7 | 0.5 | KINDERGARTEN_IDF ROOM PEOPLE ACTIVITY LEVEL | No | 3.82e-08 | 0 | 0
[11 empty] | 0.7 | 0.5 | KINDERGARTEN_RESTROOM PEOPLE ACTIVITY LEVEL | No | 3.82e-08 | 0 | 1
[11 empty] | 0.7 | 0.556 | KINDERGARTEN_STORAGE - GENERAL PEOPLE ACTIVITY LEVEL | No | 3.82e-08 | 0 | 6
N
North Classroom
West Classroom
Kindergarten
MPR/Admin

## Envelope
Envelope - SchoolK-8
Element | Prototype | Assembly Type | Construction | Thermal properties | Vintage | Selected T24 | Note | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
External Wall | SchoolK-8 | ExtWall_MetalFramed_NonRes | Metal frame + insulation + Gypsum board | U-value IP | Pre 1978 | N/A | ASHRAE 90.1, 2022, Table A3.4.3.1, 3.5", R-0 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292
[5 empty] | 1978-1997 | 1986 | Table 2-53V-16: Package A/ Heat Capacity was considered 10.0-14.99 (BTU/F/ft²) | 0.15083 | 0.15748 | 0.15748 | 0.14368 | 0.14368 | 0.21645 | 0.21645 | 0.21645 | 0.21645 | 0.21645 | 0.18622 | 0.18622 | 0.18622 | 0.15873 | 0.15873 | 0.15083
[5 empty] | 1998-2007 | 2001 | Table 1-H | 0.084 | 0.084 | 0.092 | 0.092 | 0.092 | 0.092 | 0.092 | 0.092 | 0.092 | 0.084 | 0.084 | 0.084 | 0.084 | 0.084 | 0.084 | 0.084
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.102 | 0.059 | 0.11 | 0.059 | 0.102 | 0.11 | 0.11 | 0.102 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.042 | 0.059
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.078 | 0.053 | 0.102 | 0.053 | 0.095 | 0.102 | 0.102 | 0.095 | 0.053 | 0.053 | 0.042 | 0.053 | 0.053 | 0.053 | 0.038 | 0.053
Roof | SchoolK-8 | FlatRoof_WoodFramedAndOther_NonRes | Built-up Roof roof membrane+roof insulation+metal decking | U-value IP | Pre 1978 | N/A | Table 2-53V-16: Considering 30 years for roof/ insulation replacement. | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 1978-1997 | 1992 |  | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 1998-2007 | 2001 | Table 1-H | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.049 | 0.039 | 0.039 | 0.039 | 0.049 | 0.075 | 0.067 | 0.067 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.047 | 0.047 | 0.047 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028
Windows | SchoolK-8 | FixedWindow_NonRes | Single pane | U-value IP | Pre 1978 | N/A | ASHRAE Handbook of Fundamentals (Table 4-Ch15) for single pane & T24, 2013 for double pane (33%-67%)* | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108
[5 empty] | 1978-1997 | N/A |  | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108
|  |  | Double pane |  | 1998-2007 | 2001 | Table 1-H | 0.49 | 0.49 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.34 | 0.36 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.36
| SchoolK-8 | FixedWindow_NonRes | Single pane | SHGC | Pre 1978 | N/A | ASHRAE Handbook of Fundamentals (Table 10-Ch15) for single pane & T24, 2013 for double pane (33%-67%)* | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282
[5 empty] | 1978-1997 | N/A |  | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282
|  |  | Double pane |  | 1998-2007 | 2001 | Table 1-H - WWR:31-40% / SHGC non-north | 0.43 | 0.36 | 0.41 | 0.41 | 0.41 | 0.34 | 0.34 | 0.34 | 0.34 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.43
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.22 | 0.25 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.25
Infiltration
[5 empty] | Vintage | I_75 6-Sided Inifltration rate @ 75 pa | Note | I-design (cfm/ft²) (4-sided Infiltration rate at normal presure) (Design flow rate approach and Flow/Exterior Wall Area calulation method)
|  |  |  | Infiltration | Pre 1978 | 1.1 | 2022 CASE report (Table 38) | 0.342
[5 empty] | 1978-1997 | 1.1 | 2022 CASE report (Table 38) | 0.342
[5 empty] | 1998-2007 | 1.1 | 2022 CASE report (Table 38) | 0.342
[5 empty] | 2008-2018 | 1 | 2022 CASE report (Table 38) & T24, 2008-2016 (Table 140.3-B)--Air barrier is required in CZ 10-16 | 0.3129
[5 empty] | 2019+ | 0.6 | 2022 CASE report (Table 38) & T24, 2025 (Table 140.3-B)--Air barrier is required in all CZs | 0.1865
Source: T24 air barrier requirements (all editions) and the standardized infiltration rate reported in the 2022 CASE report and Dodge 2023 data
|  |  |  | Air Lekage Memo: |  | Infiltration_rate_report_14May2025-Short-Version.docx

## HVAC System
HVAC system - SchoolK-8
Vintage | Zones | Heating | Cooling | Air Distribution | Source | Note
Exisiting | All Space Types | Gas Furnace | PSZAC (DX cooling) | CAV | Engineering Judgement | System 3a
New Construction | All Space Types | SZHP | SZHP | CAV | ACM 2025 | System 3b
Efficiency of HVAC system
Vintage | Upgrade/Installed year | Gas Furnace | Heating DX | Cooling DX | Sources | Note
Pre 1978 | 2008 | Thermal Efficiency of 80% | n/a | EER 11.2 for <65 kBtu/h EER 10.3 for 65-135 kBtu/h | 2005 Title 20 Appliance Efficiency Regulations, 2005 T24 Standards, Tables 112-A, 112-B
1978-1997
1998-2007
2008-2018 | 2013 | Thermal Efficiency of 80% | n/a | EER 11.2 for <65 kBtu/h EER 10.3 for 65-135 kBtu/h | 2013 Title 20 Appliance Efficiency Regulations, 2013 T24 Tables 112-A, 112-B
New Construction | 2025 | n/a | Heating @ 47 °F : COP = Federal Minimum COP : 3.3 Heating @ 17 °F : COP = Title 24 Table 110.2-B: COP : 2.25 | EER 11.2 for <65 kBtu/h EER 11, COP fed min for 65-135 kBtu/h | Title 20 Appliance Efficiency Regulations, T24, 2025, Tables 110.2-A, 110.2-B
|  | * Et = Combustion efficiency | * Et = Thermal efficiency
Fan power
Vintage | Approach | System | Total Static Pressure (TSP) in w.c. [PNNL 20405, 2010, Table 5.11] | Fan Efficiency [ACM, 2025] | Fan Motor and Drive Efficiency [ACM 2025, Table 14] | W/cfm [ACM 2025, Table 15] | Data Source | Note
Existing | PNNL TSP | CAV | 2.5 for CAV <7,437 cfm 4.09 for CAV >=7,437 cfm | 0.65 | 0.9 |  | PNNL 2010 TSD
Brake horse power (bhp)=(Supply cfm*TSP in w.c.)/(6356*Fan efficiency)
Fan power (w/cfm) = bhp/motor and drive efficiency *746
New Construction | ACM 2025 | SZHP>10,000 | 3.3694 | 0.65 | 0.9 | 0.676 | 2025 ACM
* 0.9 is an average fan efficiency according to ACM 2025, Table 14
Fan total eff (E+ input) = 0.65 x Motor_eff
TSP (E+ input) in w.c. = Motor_eff/746 x (6356 x Fan_eff) x W/cfm
Fan_eff=0.65
Background Data [To be deleted prior to publication]

## Thermostat
Thermostat Setpoints - SchoolK-8
Setpoint | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16 | Source
School Heating Setpoint (F) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | T24 2022 - Appendix 5.4B
School Heating Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
School Cooling Setpoint (F) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | T24 2022 - Appendix 5.4B
School Cooling Setback (F) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85

## Ventilation
Outdoor Airflow Rate - SchoolK-8
Space Type | Space/Thermal Zone | Number of People | Floor Area (ft²) | cfm/person [T24, 2025, Equation 120.1-F and Table 120.1-A] | cfm/ft² [T24, 2025, Equation 120.1-F and Table 120.1-A] | Required exhaust rate-CFM/ft²- [T24, 2025, Table 120.1-B – minimum exhaust rates] | Total cfm driven by people | Total cfm driven by area | Total cfm driven by exhaust | Total cfm | Notes
Lounge, Breakroom, or Waiting Area | Admin/MPR_Breakroom_Zn | 37.9632 | 575.2 | 15 | 0.15 |  | 569.448 | 86.28 | 0 | 569.448
Convention, Conference, Multipurpose and Meeting Area | Admin/MPR_Conference Room Zns 3_Zn | 110.5328 | 1674.74 | 15 | 0.15 |  | 1657.9926 | 251.211 | 0 | 1657.9926
Corridor Area | Admin/MPR_Corridor_Zn | 11.6152 | 1161.52 | 30 | 0.15 |  | 348.456 | 174.228 | 0 | 348.456
Electrical, Mechanical, Telephone Rooms | Admin/MPR_EMT_Zn | 2.7821 | 278.21 | 30 | 0.15 |  | 83.463 | 41.7315 | 0 | 83.463
Electrical, Mechanical, Telephone Rooms | Admin/MPR_IDF Room_Zn | 3.4023 | 340.23 | 30 | 0.15 |  | 102.069 | 51.0345 | 0 | 102.069
Kitchen/Food Preparation Area | Admin/MPR_Kitchen_Zn | 8.7435 | 1457.25 | 50 | 0.15 |  | 437.175 | 218.5875 | 0 | 437.175
Lobby, Main Entry | Admin/MPR_Lobby_Zn | 81.937 | 1241.47 | 15 | 0.15 |  | 1229.0553 | 186.2205 | 0 | 1229.0553
Convention, Conference, Multipurpose and Meeting Area | Admin/MPR_Multipurpose Room Zns 3_Zn | 363.8045 | 5512.19 | 15 | 0.15 |  | 5457.0681 | 826.8285 | 0 | 5457.0681
Office Area (<250 square feet) | Admin/MPR_Office - LT 250 sf Zns 6_Zn | 10.4835 | 1048.35 | 30 | 0.15 |  | 314.505 | 157.2525 | 0 | 314.505
Restrooms | Admin/MPR_Restroom Zns 3_Zn | 9.0117 | 901.17 | 15 | 0.15 |  | 135.1755 | 135.1755 | 0 | 135.1755
Storage (General) | Admin/MPR_Storage - General_Zn | 12.4773 | 1247.73 | 30 | 0.15 |  | 374.319 | 187.1595 | 0 | 374.319
Storage, Commercial/Industrial (Refrigerated) | Admin/MPR_Storage - Refrigerated_Zn | 0 | 251.72 | 0 | 0.15 |  | 0 | 37.758 | 0 | 37.758
Theater Area (Performance) | Admin/MPR_Theater - Performance_Zn | 70.327 | 1065.56 | 15 | 0.15 |  | 1054.9044 | 159.834 | 0 | 1054.9044
Classroom, Lecture, Training, Vocational Areas | Classrm N_Flr 1_Classroom-01_Zn | 50.0875 | 1001.75 | 15 | 0.15 |  | 751.3125 | 150.2625 | 0 | 751.3125
Classroom, Lecture, Training, Vocational Areas | Classrm N_Flr 1_Classroom-02 Zns 6_Zn | 302.7015 | 6054.03 | 15 | 0.15 |  | 4540.5225 | 908.1045 | 0 | 4540.5225
Office Area (<250 square feet) | Classrm N_Flr 1_Office - LT 250 sf_Zn | 2.8813 | 288.13 | 30 | 0.15 |  | 86.439 | 43.2195 | 0 | 86.439
Restrooms | Classrm N_Flr 1_Restroom_Zn | 5.327 | 532.7 | 15 | 0.15 |  | 79.905 | 79.905 | 0 | 79.905
Classroom, Lecture, Training, Vocational Areas | Classrm N_Flr 2_Classroom-01 Zns 6_Zn | 302.7015 | 6054.03 | 15 | 0.15 |  | 4540.5225 | 908.1045 | 0 | 4540.5225
Classroom, Lecture, Training, Vocational Areas | Classrm N_Flr 2_Classroom-02_Zn | 50.0875 | 1001.75 | 15 | 0.15 |  | 751.3125 | 150.2625 | 0 | 751.3125
Office Area (<250 square feet) | Classrm N_Flr 2_Office - LT 250 sf_Zn | 2.8813 | 288.13 | 30 | 0.15 |  | 86.439 | 43.2195 | 0 | 86.439
Restrooms | Classrm N_Flr 2_Restroom_Zn | 5.327 | 532.7 | 15 | 0.15 |  | 79.905 | 79.905 | 0 | 79.905
Classroom, Lecture, Training, Vocational Areas | Classrm W_Flr 1_Classroom Zns 2_Zn | 102.747 | 2054.94 | 15 | 0.15 |  | 1541.205 | 308.241 | 0 | 1541.205
Electrical, Mechanical, Telephone Rooms | Classrm W_Flr 1_EMT-01_Zn | 1.2101 | 121.01 | 30 | 0.15 |  | 36.303 | 18.1515 | 0 | 36.303
Electrical, Mechanical, Telephone Rooms | Classrm W_Flr 1_EMT-02_Zn | 0.9801 | 98.01 | 30 | 0.15 |  | 29.403 | 14.7015 | 0 | 29.403
Library (Reading Area) | Classrm W_Flr 1_Library - Reading Area_Zn | 23.9426 | 1197.13 | 15 | 0.15 |  | 359.139 | 179.5695 | 0 | 359.139
Restrooms | Classrm W_Flr 1_Restroom_Zn | 5.6305 | 563.05 | 15 | 0.15 |  | 84.4575 | 84.4575 | 0 | 84.4575
Storage (General) | Classrm W_Flr 1_Storage - General_Zn | 3.8084 | 380.84 | 30 | 0.15 |  | 114.252 | 57.126 | 0 | 114.252
Classroom, Lecture, Training, Vocational Areas | Classrm W_Flr 2_Classroom-01 Zns 3_Zn | 162.603 | 3252.06 | 15 | 0.15 |  | 2439.045 | 487.809 | 0 | 2439.045
Classroom, Lecture, Training, Vocational Areas | Classrm W_Flr 2_Classroom-02_Zn | 19.042 | 380.84 | 15 | 0.15 |  | 285.63 | 57.126 | 0 | 285.63
Electrical, Mechanical, Telephone Rooms | Classrm W_Flr 2_IDF Room_Zn | 1.2101 | 121.01 | 30 | 0.15 |  | 36.303 | 18.1515 | 0 | 36.303
Restrooms | Classrm W_Flr 2_Restroom_Zn | 5.6305 | 563.05 | 15 | 0.15 |  | 84.4575 | 84.4575 | 0 | 84.4575
Storage (General) | Classrm W_Flr 2_Storage - General_Zn | 0.9801 | 98.01 | 30 | 0.15 |  | 29.403 | 14.7015 | 0 | 29.403
Classroom, Lecture, Training, Vocational Areas | Kindergarten_Classroom-01_Zn | 274.727 | 5494.54 | 15 | 0.15 |  | 4120.905 | 824.181 | 0 | 4120.905
Classroom, Lecture, Training, Vocational Areas | Kindergarten_Classroom-02_Zn | 72.007 | 1440.14 | 15 | 0.15 |  | 1080.105 | 216.021 | 0 | 1080.105
Electrical, Mechanical, Telephone Rooms | Kindergarten_EMT_Zn | 1.7087 | 170.87 | 30 | 0.15 |  | 51.261 | 25.6305 | 0 | 51.261
Electrical, Mechanical, Telephone Rooms | Kindergarten_IDF Room_Zn | 0.8548 | 85.48 | 30 | 0.15 |  | 25.644 | 12.822 | 0 | 25.644
Restrooms | Kindergarten_Restroom_Zn | 2.6603 | 266.03 | 15 | 0.15 |  | 39.9045 | 39.9045 | 0 | 39.9045
Storage (General) | Kindergarten_Storage - General_Zn | 11.838 | 1183.8 | 30 | 0.15 |  | 355.14 | 177.57 | 0 | 355.14
Total (15 Space types) | Total (38 spaces) | 2136.655 | 49979.37 |  |  |  | 33392.5464 | 7496.9055 | 0 | 33430.3044

## Water Heater
Water Heater -SchoolK-8
Vintage | WH Type | Efficiency | Tank Volume (gal) | Tank Loss |  | Note
Existing | Electric | 0.98 | 141.2165 | 0.4912 | %hr
New Construction | HPWH | 1.7563 | 141.2165 | 0.4912 | %hr | - Section 1605.1. Federal and State Standards for Federally-Regulated Appliances. - HPWH is required in climate zones 2-15, with UEF of 2.25.
Peak Hot Water Consumption
Space Name | Baseline WH Type [T24, 2022, Appendix 5.4A , sheet: "2022 SpaceFuncData-Input"] | Total Area (ft²) | Number of People | Hot Water Usage Specification (gal/hr per person) [T24, 2022, Appendix 5.4A , sheet: "2022 SpaceFuncData-Input"] | Peak Hot Water Usage (gal/hr) | Peak Hot Water Usage (gal/min)
Admin/MPR_Breakroom_Zn | HPWH | 575.2 | 37.9632 | 0.09 | 3.4167 | 0.056945
Admin/MPR_Conference Room Zns 3_Zn | HPWH | 1674.74 | 110.5328 | 0.09 | 9.948 | 0.1658
Admin/MPR_Corridor_Zn | HPWH | 1161.52 | 11.6152 | 0 | 0 | 0
Admin/MPR_EMT_Zn | HPWH | 278.21 | 2.7821 | 0.18 | 0.50078 | 0.0083463
Admin/MPR_IDF Room_Zn | HPWH | 340.23 | 3.4023 | 0.18 | 0.61241 | 0.010207
Admin/MPR_Kitchen_Zn | HPWH | 1457.25 | 8.7435 | 0.578 | 5.0537 | 0.084229
Admin/MPR_Lobby_Zn | HPWH | 1241.47 | 81.937 | 0.09 | 7.3743 | 0.12291
Admin/MPR_Multipurpose Room Zns 3_Zn | HPWH | 5512.19 | 363.8045 | 0.09 | 32.7424 | 0.54571
Admin/MPR_Office - LT 250 sf Zns 6_Zn | HPWH | 1048.35 | 10.4835 | 0.18 | 1.887 | 0.03145
Admin/MPR_Restroom Zns 3_Zn | HPWH | 901.17 | 9.0117 | 0 | 0 | 0
Admin/MPR_Storage - General_Zn | HPWH | 1247.73 | 12.4773 | 0 | 0 | 0
Admin/MPR_Storage - Refrigerated_Zn | HPWH | 251.72 | 0 | 0.18 | 0 | 0
Admin/MPR_Theater - Performance_Zn | HPWH | 1065.56 | 70.327 | 0.09 | 6.3294 | 0.10549
Classrm N_Flr 1_Classroom-01_Zn | HPWH | 1001.75 | 50.0875 | 0.18 | 9.0157 | 0.15026
Classrm N_Flr 1_Classroom-02 Zns 6_Zn | HPWH | 6054.03 | 302.7015 | 0.18 | 54.4863 | 0.9081
Classrm N_Flr 1_Office - LT 250 sf_Zn | HPWH | 288.13 | 2.8813 | 0.18 | 0.51863 | 0.0086439
Classrm N_Flr 1_Restroom_Zn | HPWH | 532.7 | 5.327 | 0 | 0 | 0
Classrm N_Flr 2_Classroom-01 Zns 6_Zn | HPWH | 6054.03 | 302.7015 | 0.18 | 54.4863 | 0.9081
Classrm N_Flr 2_Classroom-02_Zn | HPWH | 1001.75 | 50.0875 | 0.18 | 9.0157 | 0.15026
Classrm N_Flr 2_Office - LT 250 sf_Zn | HPWH | 288.13 | 2.8813 | 0.18 | 0.51863 | 0.0086439
Classrm N_Flr 2_Restroom_Zn | HPWH | 532.7 | 5.327 | 0 | 0 | 0
Classrm W_Flr 1_Classroom Zns 2_Zn | HPWH | 2054.94 | 102.747 | 0.18 | 18.4945 | 0.30824
Classrm W_Flr 1_EMT-01_Zn | HPWH | 121.01 | 1.2101 | 0.18 | 0.21782 | 0.0036303
Classrm W_Flr 1_EMT-02_Zn | HPWH | 98.01 | 0.9801 | 0.18 | 0.17642 | 0.0029403
Classrm W_Flr 1_Library - Reading Area_Zn | HPWH | 1197.13 | 23.9426 | 0.18 | 4.3097 | 0.071828
Classrm W_Flr 1_Restroom_Zn | HPWH | 563.05 | 5.6305 | 0 | 0 | 0
Classrm W_Flr 1_Storage - General_Zn | HPWH | 380.84 | 3.8084 | 0 | 0 | 0
Classrm W_Flr 2_Classroom-01 Zns 3_Zn | HPWH | 3252.06 | 162.603 | 0.18 | 29.2685 | 0.48781
Classrm W_Flr 2_Classroom-02_Zn | HPWH | 380.84 | 19.042 | 0.18 | 3.4276 | 0.057126
Classrm W_Flr 2_IDF Room_Zn | HPWH | 121.01 | 1.2101 | 0.18 | 0.21782 | 0.0036303
Classrm W_Flr 2_Restroom_Zn | HPWH | 563.05 | 5.6305 | 0 | 0 | 0
Classrm W_Flr 2_Storage - General_Zn | HPWH | 98.01 | 0.9801 | 0 | 0 | 0
Kindergarten_Classroom-01_Zn | HPWH | 5494.54 | 274.727 | 0.18 | 49.4509 | 0.82418
Kindergarten_Classroom-02_Zn | HPWH | 1440.14 | 72.007 | 0.18 | 12.9613 | 0.21602
Kindergarten_EMT_Zn | HPWH | 170.87 | 1.7087 | 0.18 | 0.30757 | 0.0051261
Kindergarten_IDF Room_Zn | HPWH | 85.48 | 0.8548 | 0.18 | 0.15386 | 0.0025644
Kindergarten_Restroom_Zn | HPWH | 266.03 | 2.6603 | 0 | 0 | 0
Kindergarten_Storage - General_Zn | HPWH | 1183.8 | 11.838 | 0 | 0 | 0
Total |  | 49979.37 | 2136.655 |  | 314.8919 | 5.2482
Water Heater Capacity, Tank Capacity, and Tank Loss
WH Type | Peak Hot Water Usage (gal/hr) | Heat Output (Btu/hr) [ACM, 2025, 5.9.2: Rated capacity section] | WH Capacity (Btu/hr) [ACM, 2025, 5.9.2: Rated capacity section] | Required Energy Input (Btu/hr) | Storage Volume (gal) | Standby Loss | Unit | Off/On Cycle Loss Coefficient to Ambient Temp (Btu/h-F) | Source
Electric | 353.0413 | 235690.3772 | 141414.2263 | 144300.231 | 141.2165 | 0.4912 | %hr | 5.7226 | - Tank size equation: 2022/2025 Nonres & MF ACM, §5.9.2 ‘Storage Volume - Heat output equation: Nonres/MF ACM 2019/2022/2025, §5.9.2 ‘Rated Capacity - Input capacity / efficiency source: ACM §5.9.2 ‘Rated Capacity’ + Title 20 CCR §1605.1(f), Tables F-2/F-4 (Appliance Efficiency Regulations) - Standby loss equation (STBY in Btu/h): ACM §5.9.2 ‘Tank Standby Loss’; test method parameters from Title 20 Appliance Efficiency Regs, Section 1604(f). - Standby-loss limit Sₘₐₓ (%/h): 42 U.S.C. §6313(a)(5)(A); DOE 10 CFR Part 431 Subpart G; adopted in California Title 20 CCR §1605.1(f), Table F-4.
HPWH - Admin | 75 | 50070 | 30042 | 17105.5395 | 30 | 1.2 | %hr | 2.97
HPWH - North Classroom | 128.0413 | 85480.3772 | 51288.2263 | 29202.8754 | 51.2165 | 0.82717 | %hr | 3.4951
HPWH - West Classroom | 75 | 50070 | 30042 | 17105.5395 | 30 | 1.2 | %hr | 2.97
HPWH - Kindergarten | 75 | 50070 | 30042 | 17105.5395 | 30 | 1.2 | %hr | 2.97
HPWH - Total | 353.0413 | 235690.3772 | 141414.2263 | 80519.4939 | 141.2165 | 0.4912 | %hr | 5.7226
-
Design supply temperature (F) | 135 | Ref: T24 2022 - Appendix 5.4B
Cold Water supply temperature (F) | 55 | Ref: ACM, 2025, 5.9.2: Rated capacity section
WH system factor | 0.6 | Ref: ACM, 2025, 5.9.2: Rated capacity section
Reheat multiplier | 0.4
* The 0.40 multiplier is a storage sizing factor used to account for the fact that the water heater doesn't need to store the full peak hour demand—it can reheat water during that time. This factor assumes that the heater will recover part of the hot water used during the peak hour, so only 40% of the peak hour demand needs to be stored at any given moment.
**For Gas Water Heater: UA(Btu/h-°F)​=Q˙​SL​ (Btu/h)/ΔT (∘F)​
Ambient temp | 68
Delta T | 67
** For Electric Water Heater: UA(Btu/h-°F)​= 0.0834 *SL​ (%/hr)*V gal
DV (daily hot water Volume in gallons, DOE UEF tests) | 38 | Note: 10 (very small draw), 38 (low draw), 55 (Medium draw), or 84 (high draw)
UEF = 0.1513 + 0.8407 * EF + 0.0043 * DV | 2.15 | Source: https://energy.gov/sites/prod/files/2016/12/f34/WH_Conversion_Final%20Rule.pdf
EF = (UEF - 0.1513 - (0.0043 * DV)) / 0.8407 | 2.1831
COP = EF * (2.6 - 0.0133 * Ttank) | 1.7563 | Source: https://www.nrel.gov/docs/fy16osti/64904.pdf
Background Data [To be deleted prior to publication]

## Interior Lights
Interior Lighting - SchoolK-8
Space Type | New Construction |  |  | Existing
| Lighting density (W/ft²) | Additional lighting power for porTable lighting (W/ft²) | Source | LPD (W/ft²) | Additional LPD for PorTable Lighting (W/ft²) | Source
Lounge, Breakroom, or Waiting Area | 0.55 |  | T24, 2025, Table 140.6 C (Area category method) | 0.9 |  | T24, 2016, Table 140.6 C (Area category method)
Convention, Conference, Multipurpose and Meeting Area | 0.75 |  |  | 1.2
Corridor Area | 0.4 |  |  | 0.6
Electrical, Mechanical, Telephone Rooms | 0.4 |  |  | 0.55
Kitchen/Food Preparation Area | 0.95 |  |  | 1.2
Lobby, Main Entry | 0.7 |  |  | 0.95
Restrooms | 0.65 |  |  | 0.6
Storage (General) | 0.4 |  |  | 0.6
Storage, Commercial/Industrial (Refrigerated) | 0.4 |  |  | 0.7
Theater Area (Performance) | 0.8 |  |  | 1.4
Classroom, Lecture, Training, Vocational Areas | 0.6 |  |  | 1.2
Office Area (<250 square feet) | 0.65 |  |  | 1
Library (Reading Area) | 0.8 |  |  | 1.1

## Equipment
Equipment - SchoolK-8
Space Type | Plug load Power Density (W/ft²) | Gas Power Density (Btu/hr-ft²) | Refrigeration Power Density (W/ft²) | Source
Lounge, Breakroom, or Waiting Area | 1 | 0 | 0 | T24 2022 - Appendix 5.4A
Convention, Conference, Multipurpose and Meeting Area | 1 | 0 | 0
Corridor Area | 0 | 0 | 0
Electrical, Mechanical, Telephone Rooms | 3 | 0 | 0
Kitchen/Food Preparation Area | 1.5 | 17.5377 | 1.12 | Plug load and schedules project with CEC, 2025
Lobby, Main Entry | 0.5 | 0 | 0 | T24 2022 - Appendix 5.4A
Office Area (<250 square feet) | 0.7 | 0 | 0 | Plug load and schedules project with CEC, 2025
Restrooms | 0 | 0 | 0 | T24 2022 - Appendix 5.4A
Storage (General) | 0.2 | 0 | 0
Storage, Commercial/Industrial (Refrigerated) | 0.2 | 0 | 10
Theater Area (Performance) | 0.5 | 0 | 0
Classroom, Lecture, Training, Vocational Areas | 0.8 | 0 | 0 | Plug load and schedules project with CEC, 2025
Library (Reading Area) | 1.5 | 0 | 0
Elevator
Vintages | No of Elevator | Design Load (W) | Source
New Construction and Existing | 1 | 60000 | ACM with assumptions listed below |  | https://buildingandinteriors.com/find-the-magic-number-elevators-per-building/
For every two floors or two and a half floors, one more elevator was added.
An in-use rate of 70% for the floor area was assumed, based on engineering judgment.
Calculated number of Elevators: |  | 1
Calculate Elevator load (kw)based on ACM 2022: |  | 60
ACM 2022 suggestion for elevator load (kw): |  | 10
Elevator load will be defined as exterior load not equipment load

## Ext Lighting
Exterior Lighting - SchoolK-8
Motion Controlled Luminaires (W) | Non-motion Controlled Luminaires (W) | Total (W) | Source
717.6423 | 9012.8416 | 9730.4839 | T24, 2022 & 2025 2019 Outdoor Lighting CASE report PNNL 90.1-2010 TSD
Exterior Lighting
Items (Assume LZ2) | Assumptions [2019 Outdoor Lighting CASE Report & PNNL 90.1-2010 TS] |  | Unit | Lighting Power Allowance [T24, 2025, Table 140.7-A & 140.7-B] | Unit | Exterior Lighting Power (W)
IWA (Initial Wattage Allowance) |  |  |  | 200 | (W) | 200
Parking area | 400 ft² for every parking space 1 parking space per 830 ft² of gross building area | 24086.4386 | (ft²) | 0.019 | (W/ft²) | 457.6423
Building Entrance | 5 building entrance per PNNL Model (1 per 10,000 ft² footprint) | 4 | (count) | 15 | (W/ea) | 60
Hardscape Ornamental Light | 0.1 ft² per 1 ft² of gross building area for hardscape ornamental light | 4997.936 | (ft²) | 0.007 | (W/ft²) | 34.9856
Building façade | 0.1 W per 1 ft² of facade area Façade Area = Perimeter × 0.5 × max ( height and 30) (30 ft is the max height that is lit) * The 0.5 factor assumes that only half of the perimeter walls are lit. -Formula ia developed based on the 2019 Outdoor Lighting CASE report | 89778.56 | (ft²) | 0.1 | (W/ft²) | 8977.856
Motion Controlled Luminaires (W) | [5 empty] | 717.6423
Non-motion-controlled Luminaires | [5 empty] | 9012.8416
Total | [5 empty] | 9730.4839
| North Classroom | West Classroom | Kindergarten | MPR/Admin
Perimeter of each buildings (ft) | 537.2 | 326.56 | 474 | 562.72
Max Height that is lit for each buildings (ft) | 28 | 28 | 14 | 25
Each building footprint | 7876 | 4415 | 8640 | 16754
Floors | 2 | 2 | 1 | 1
Total Perimeter (ft) | 1900.48
Total floor area (ft²) | 49979.36
Background Data [To be deleted prior to publication]

## Schedules
Schedules - SchoolLarge
Zone | Schedule Category | Schedule | Source | Type | Hour
[5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
School Zones | Classroom | Occupancy | T24 2022 - Appendix 5.4B [School] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.75 | 0.9 | 0.9 | 0.8 | 0.8 | 0.8 | 0.8 | 0.45 | 0.15 | 0.05 | 0.15 | 0.2 | 0.2 | 0.1 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School Zones | Classroom | Lights | T24 2022 - Appendix 5.4B [School] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.6 | 0.65 | 0.65 | 0.65 | 0.55 | 0.55 | 0.55 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.3 | 0.05 | 0.05
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
School Zones | Classroom | ElecEquipment | T24 2022 - Appendix 5.4B [School] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.85 | 0.95 | 0.95 | 0.95 | 0.8 | 0.8 | 0.8 | 0.7 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.3 | 0.05 | 0.05
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
School Zones | Classroom | ServiceHotWater | T24 2022 - Appendix 5.4B [School] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09
|  |  |  | Saturday | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
|  |  |  | Sunday | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
School Zones | Classroom | GasEquipment | T24 2022 - Appendix 5.4B [School] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.75 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School Zones | Classroom | Refrigeration | T24 2022 - Appendix 5.4B [School] | Weekday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Saturday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Sunday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
School Zones | Classroom | HVACAvail | T24 2022 - Appendix 5.4B [School] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School Zones | Classroom | HtgSetpt | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 60 | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 60 | 60
|  |  |  | Saturday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  |  | Sunday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
School Zones | Classroom | ClgSetpt | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 85 | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 85 | 85
|  |  |  | Saturday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
|  |  |  | Sunday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
School Zones | Classroom | Infiltration | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
Kitchen |  | Other
Kitchen Zone | Kitchen | Occupancy | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitchen Zone | Kitchen | HVACAvail | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitchen Zone | Kitchen | Lights | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitchen Zone | Kitchen | ElecEquipment | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.3 | 0.9 | 0.9 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.7 | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitchen Zone | Kitchen | HtgSetpt | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  |  | Saturday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  |  | Sunday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Kitchen Zone | Kitchen | ClgSetpt | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
|  |  |  | Saturday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
|  |  |  | Sunday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
Kitchen Zone | Kitchen | OAControl | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitchen Zone | Kitchen | Infiltration | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
Kitchen Zone | Kitchen | Refrigeration | T24 2022 - Appendix 5.4B [School] | Weekday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Saturday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Sunday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
Kitchen Zone | Kitchen | GasEquipment | T24 2022 - Appendix 5.4B [School] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.75 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitchen Zone | Kitchen | ServiceHotWater | T24 2022 - Appendix 5.4B [School] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09
|  |  |  | Saturday | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
|  |  |  | Sunday | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
MPR |  | Other
MPR Zone | MPR | Occupancy | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.5 | 0.25 | 0.25 | 0.05 | 0.25 | 0.95 | 0.95 | 0.25 | 0.2 | 0.2 | 0.2 | 0.15 | 0.15 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MPR Zone | MPR | HVACAvail | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MPR Zone | MPR | Lights | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MPR Zone | MPR | ElecEquipment | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.3 | 0.9 | 0.9 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.7 | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MPR Zone | MPR | HtgSetpt | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 60 | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 60 | 60 | 60 | 60
|  |  |  | Saturday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  |  | Sunday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
MPR Zone | MPR | ClgSetpt | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 85 | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 85 | 85 | 85 | 85
|  |  |  | Saturday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
|  |  |  | Sunday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
MPR Zone | MPR | OAControl | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MPR Zone | MPR | Infiltration | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
MPR Zone | MPR | Refrigeration | T24 2022 - Appendix 5.4B [School] | Weekday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Saturday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Sunday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
MPR Zone | MPR | ServiceHotWater | T24 2022 - Appendix 5.4B [School] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09
|  |  |  | Saturday | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
|  |  |  | Sunday | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
Other |  | Other
| Building | Elevator | T24 2022 - Appendix 5.4B, [School] | Weekday | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.12
|  |  |  | Saturday | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
|  |  |  | Sunday | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
| Building | ExtLightingNonMotionCtrl |  | Weekday | bar: Hour 1 to Hour 24
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
| Building | ExtLightingMotionCtrl |  | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Auditorium | Building | PerformanceSpcPeopleActivityLevel | Based on Activilty level schedules in CEC Prototypes | Weekday | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6
|  |  |  | Saturday | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6
|  |  |  | Sunday | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6
Gym | Building | GymPeopleActivityLevel | Based on Activilty level schedules in CEC Prototypes | Weekday | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2
|  |  |  | Saturday | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2
|  |  |  | Sunday | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2
Restroom, Coridor, Lobby, Mechanical RM, Lounge, Storage, Theater | Building | CommonAreaPeopleActivityLevel | Based on Activilty level schedules in CEC Prototypes | Weekday | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5
|  |  |  | Saturday | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5
|  |  |  | Sunday | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5
Classroom | Building | MeetingPeopleActivityLevel | Based on Activilty level schedules in CEC Prototypes | Weekday | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2
|  |  |  | Saturday | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2
|  |  |  | Sunday | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2
DiningArea | Building | DiningAreaPeopleActivityLevel | Based on Activilty level schedules in CEC Prototypes | Weekday | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2
|  |  |  | Saturday | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2
|  |  |  | Sunday | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2
Library, office, MultiMeetingRm | Building | FunctionalAreaPeopleActivityLevel | Based on Activilty level schedules in CEC Prototypes and assumed spaces for Basement | Weekday | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
|  |  |  | Saturday | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
|  |  |  | Sunday | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
RefStorage | Building | RefStoragePeopleActivityLevel | Based on Activilty level schedules in CEC Prototypes | Weekday | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8
|  |  |  | Saturday | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8
|  |  |  | Sunday | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8
Background Data [To be deleted prior to publication]

## Energy Usage
CalBEM Energy Consumption - K-8 School | [11 empty] | Energy Consumption - SchoolK-8
Prototype | CZ | CalBEM Electricity EUI (KBTU/ft²) | CalBEM Gas EUI (KBTU/ft²) | CalBEM Total EUI (KBTU/ft²) | New Construction Electricity EUI (KBTU/ft²) | New Construction Gas EUI (KBTU/ft²) | New Construction Total EUI (KBTU/ft²) | National Average | Acceptable Range (25% Higher) | Acceptable Range (25% Lower) | National Average Acceptable EUI Range | Prototype | CZ | Total Floorspace (Thousand of ft²) | CEUS 2023 Electricity EUI (kBtu/ft²) | CEUS 2023 Gas EUI (kBtu/ft²) | CEUS 2023 Total EUI (kBtu/ft²) | Acceptable Range (25% Higher) | Acceptable Range (25% Lower) | CEUS 2022 Acceptable EUI Range
K-8 School | 1 | 61.0994 | 56.5864 | 117.6857 | 56.85 | 0.57 | 57.42 | 38.7 | 48.375 | 29.025 | 19.35 | K-8 School | 1 | 7618.5337 | 32.3492 | 12.8481 | 55.3648 | 69.206 | 41.5236 | 27.6824
| 2 | 63.1953 | 38.9539 | 102.1492 | 56.44 | 0.57 | 57.01 | 34.3 | 42.875 | 25.725 | 17.15 |  | 2 | 11477.6706 | 15.4216 | 12.914 | 47.8933 | 59.8666 | 35.92 | 23.9466
| 3 | 55.8737 | 31.3404 | 87.2142 | 49.61 | 0.57 | 50.18 | 30.8 | 38.5 | 23.1 | 15.4 |  | 3 | 46411.8605 | 20.4796 | 12.7992 | 100.095 | 125.1187 | 75.0712 | 50.0475
| 4 | 68.7233 | 30.7759 | 99.4992 | 58.5 | 0.57 | 59.07 | 39.5 | 49.375 | 29.625 | 19.75 |  | 4 | 23032.968 | 21.4937 | 13.0198 | 106.6213 | 133.2767 | 79.966 | 53.3107
| 5 | 57.5529 | 22.8172 | 80.3701 | 49.6 | 0.57 | 50.17 | 29.7 | 37.125 | 22.275 | 14.85 |  | 5 | 5978.4428 | 11.9981 | 11.5852 | 59.1493 | 73.9366 | 44.362 | 29.5746
| 6 | 51.984 | 9.7623 | 61.7463 | 44.94 | 0.57 | 45.51 | 31.8 | 39.75 | 23.85 | 15.9 |  | 6 | 57755.9589 | 22.6073 | 9.9467 | 82.3475 | 102.9344 | 61.7606 | 41.1737
| 7 | 51.2448 | 7.0379 | 58.2827 | 45.09 | 0.57 | 45.66 | 32.8 | 41 | 24.6 | 16.4 |  | 7 | 35149.9926 | 24.8484 | 6.97 | 88.5535 | 110.6918 | 66.4151 | 44.2767
| 8 | 60.195 | 10.1112 | 70.3062 | 51.71 | 0.57 | 52.28 | 38.6 | 48.25 | 28.95 | 19.3 |  | 8 | 92353.4113 | 22.9353 | 8.8422 | 103.4418 | 129.3023 | 77.5814 | 51.7209
| 9 | 61.0067 | 13.2149 | 74.2216 | 51.66 | 0.57 | 52.23 | 38.5 | 48.125 | 28.875 | 19.25 |  | 9 | 141795.4506 | 26.7973 | 10.0891 | 119.1513 | 148.9391 | 89.3635 | 59.5757
| 10 | 63.3643 | 12.2651 | 75.6294 | 54.75 | 0.57 | 55.32 | 42.2 | 52.75 | 31.65 | 21.1 |  | 10 | 92589.8669 | 22.4904 | 10.109 | 67.4191 | 84.2739 | 50.5643 | 33.7096
| 11 | 72.9296 | 43.3529 | 116.2826 | 64.9 | 0.57 | 65.47 | 47.7 | 59.625 | 35.775 | 23.85 |  | 11 | 33810.4884 | 26.9287 | 8.7604 | 68.8393 | 86.0491 | 51.6294 | 34.4196
| 12 | 65.3159 | 35.1866 | 100.5025 | 58.31 | 0.57 | 58.88 | 41.6 | 52 | 31.2 | 20.8 |  | 12 | 108342.4341 | 31.7996 | 12.2303 | 85.5874 | 106.9842 | 64.1905 | 42.7937
| 13 | 71.486 | 27.0641 | 98.5502 | 62.85 | 0.57 | 63.42 | 49.6 | 62 | 37.2 | 24.8 |  | 13 | 46676.8078 | 32.656 | 15.4735 | 57.7357 | 72.1696 | 43.3018 | 28.8678
| 14 | 78.1971 | 35.3139 | 113.511 | 68.15 | 0.57 | 68.72 | 48.8 | 61 | 36.6 | 24.4 |  | 14 | 22787.7389 | 21.8072 | 11.4332 | 68.5025 | 85.6282 | 51.3769 | 34.2513
| 15 | 85.8399 | 8.0392 | 93.879 | 71.19 | 0.57 | 71.76 | 65.8 | 82.25 | 49.35 | 32.9 |  | 15 | 54746.0029 | 21.9543 | 10.4391 | 47.7153 | 59.6441 | 35.7864 | 23.8576
| 16 | 69.3819 | 80.0289 | 149.4108 | 71.33 | 0.57 | 71.9 | 44 | 55 | 33 | 22 |  | 16 | 85267.8904 | 27.0269 | 11.6529 | 67.5765 | 84.4706 | 50.6824 | 33.7882
Ref: CEUS 2022 Report
And by applying FZ-CZ multipliers for converting FZ data to CZ data

## Weights
% of Floor Area per CZ and Vintage Bin - Schools
Prototype | CZ | Vintage Bin
|  | Pre-1978 | 1978-1997 | 1998-2007 | 2008-2018 | Not available
K-8 School | 1 | 48.5% | 27.4% | 7.6% | 2.9% | 13.6% | 100%
| 2 | 85.8% | 7% | 3.8% | 1.4% | 2% | 100%
| 3 | 66.1% | 20.9% | 1.5% | 0.6% | 10.9% | 100%
| 4 | 68.2% | 17.9% | 0.9% | 0.6% | 12.4% | 100%
| 5 | 53.6% | 42.1% | 2.4% | 0.8% | 1.2% | 100.1%
| 6 | 65.7% | 13.9% | 10.3% | 4.4% | 5.8% | 100.1%
| 7 | 28.8% | 24.7% | 18.8% | 23.5% | 4.2% | 100%
| 8 | 66.6% | 12.5% | 10.3% | 3.6% | 7% | 100%
| 9 | 60.2% | 15.2% | 7.4% | 2% | 15.2% | 100%
| 10 | 32.7% | 20.1% | 31.7% | 11.1% | 4.4% | 100%
| 11 | 47.5% | 30.5% | 7.3% | 1.7% | 13.1% | 100.1%
| 12 | 44.7% | 31% | 9.6% | 2.8% | 11.8% | 99.9%
| 13 | 32.3% | 34.7% | 13.7% | 6.1% | 13.2% | 100%
| 14 | 52.3% | 17.9% | 14.3% | 9.8% | 5.7% | 100%
| 15 | 20.5% | 20.4% | 51% | 4.7% | 3.3% | 99.9%
| 16 | 44.7% | 23.5% | 12.7% | 9.4% | 9.8% | 100.1%
Statewide
Ref: CEUS 2022 dataset
Background Data [To be deleted prior to publication]

## PV (hidden)
PV - SchoolK-8
TBD

## EV Charger (hidden)
EV Charger - SchoolK-8
TBD
Background Data [To be deleted prior to publication]

## Data (hidden)
Space Function | Electric Equipment Load Intensity | Electric Equipment Load Intensity | LPD
Aging Eye/Low-vision (Corridor Area) |  |  | 2013 | 2016 | 2019 | 2025
Aging Eye/Low-vision (Dining)
Aging Eye/Low-vision (Lobby, Main Entry)
Aging Eye/Low-vision (Lounge/Waiting Area)
Aging Eye/Low-vision (Multipurpose Room)
Aging Eye/Low-vision (Religious Worship Area)
Aging Eye/Low-vision (Restroom)
Aging Eye/Low-vision (Stairwell)
Audience Seating Area
Auditorium Area
Auto Repair / Maintenance Area
Barber, Beauty Salon, Spa Area
Civic Meeting Place Area
Classroom, Lecture, Training, Vocational Areas
Concourse and Atria Area
Convention, Conference, Multipurpose and Meeting Area
Copy Room
Corridor Area
Dining Area (Bar/Lounge and Fine Dining)
Dining Area (Cafeteria/Fast Food)
Dining Area (Family and Leisure)
Electrical, Mechanical, Telephone Rooms
Exercise/Fitness Center and Gymnasium Areas
Financial Transaction Area
Healthcare Facility and Hospitals (Exam/Treatment Room)
Healthcare Facility and Hospitals (Imaging Room)
Healthcare Facility and Hospitals (Medical Supply Room)
Healthcare Facility and Hospitals (Nursery)
Healthcare Facility and Hospitals (Nurse's Station)
Healthcare Facility and Hospitals (Operating Room)
Healthcare Facility and Hospitals (Patient Room)
Healthcare Facility and Hospitals (Physical Therapy Room)
Healthcare Facility and Hospitals (Recovery Room)
Hotel Function Area
Kitchen/Food Preparation Area
Kitchenette or Residential Kitchen
Laboratory, Scientific
Laundry Area
Library (Reading Area)
Library (Stacks Area)
Lobby, Main Entry
Locker Room
Lounge, Breakroom, or Waiting Area
Manufacturing, Commercial & Industrial Work Area (Low Bay)
Manufacturing, Commercial & Industrial Work Area (High Bay)
Manufacturing, Commercial & Industrial Work Area (Precision)
Museum Area (Exhibition/Display)
Museum Area (Restoration Room)
Office Area (>250 square feet)
Office Area (<250 square feet)
Parking Garage Area (Parking Zone and Ramps)
Parking Garage Area (Daylight Adaptation Zones)
Pharmacy Area
Retail Sales Area (Grocery Sales)
Retail Sales Area (Retail Merchandise Sales)
Retail Sales Area (Fitting Room)
Religious Worship Area
Restrooms
Stairwell
Storage, Commercial/Industrial (Warehouse)
Storage, Commercial/Industrial (Refrigerated)
Storage, Commercial/Industrial (Shipping & Handling)
Storage (General)
Sports Arena - Playing Area (> 5,000 Spectators)
Sports Arena - Playing Area (2,000 - 5,000 Spectators)
Sports Arena - Playing Area (< 2,000 Spectators)
Sports Arena - Playing Area (Recreational)
Theater Area (Motion Picture)
Theater Area (Performance)
Transportation Function (Baggage Area)
Transportation Function (Ticketing Area)
Videoconferencing Studio
High-Rise Residential Living Spaces
Hotel/Motel Guest Room
All other
Attic
Reception Area
Elevator
Plenum
Computer Room
Server Room