## Notes
Data Sources
Dataset | Dodge 2023
CEUS 2022
ComStock 2023
Prototype | CEC School prototype (CBECC 2022.3.1) | https://bees.noresco.com/software2022.html
Codes | Title 24, part 6, referred to as T24 (1984, 2001, 2007, 2013, 2016, 2022, 2025)
ASHRAE 90.1 (2022)
CFR Title 10 (2008, 2010, 2025)
ACM 2022
| T24 2022 - Appendix 5.4A and Appendix 5.4B | https://www.energy.ca.gov/publications/2022/2022-nonresidential-and-multifamily-alternative-calculation-method-reference
Other | 2022 Reduced infiltration CASE report | https://title24stakeholders.com/wp-content/uploads/2020/10/2022-T24-Final-CASE-Report_Reduce-Infiltration.pdf
| 2019 Outdoor Lighting CASE Report | https://title24stakeholders.com/wp-content/uploads/2016/10/T24-2019-CASE-Study-Results-Report-Outdoor-Sources_Final_with-Attachments.pdf
| 2019 High Efficiency Fume Hoods in Laboratory Spaces CASE Report | https://title24stakeholders.com/wp-content/uploads/2017/09/2019-T24-CASE-Report_Fume-Hoods_Final_September-2017.pdf?
| PNNL 20405, 2010 | file:///N:/Prj_SUS/2023/S23668%20SCE%20CA%20Prototypes%20Development/Technical/NR/0_Input%20data/Lighting/PNNL-20405.pdf
| Air leakage Memo, NORESCO, 2025 | Infiltration_rate_report_14May2025-Short-Version.docx
Construction Rate
Notes

## Prototype
NORESCO, Updated September 2025
SchoolLarge
Characteristic | Value | Data Sources
Building Type | Large School
Building Category | Nonresidential
Vintages | 4 Vintages: Pre-1978, 1978-1997,1998-2007, 2008-2018 New Construction (2019+) | Based on the vintage bin analysis | NonRes-Vintage bins-Draft Report-30Nov2023-Final.docx
Shape |  | The analysis uses prototype geometry originally developed by CEC.
Total Floor Area (ft²) | 210906.62 | Same as CEC
Aspect Ratio | 1.3558 | Same as CEC
Number of Floors | 2 | Same as CEC
Roof type | Flat | Same as CEC
WWR | 34.5% | Same as CEC
Shading Geometry | No Shades | Same as CEC
Floor to floor height (feet) | 13.2 ft | Same as CEC
Floor to ceiling height (feet) | 13.2 ft | Same as CEC
Glazing sill height (feet) | 3.6 ft | Same as CEC
Above grade wall area (ft²) | 64245.23
Gross wall area (ft²) | 64245.23
Roof area (ft²) | 128124.28
Underground Gross Wall Area (ft²) | 0

## Zones
Proposed Layout - SchoolLarge
Space Type | Space/Thermal Zone | HVAC System Name/AHU Name | Schedule Category | Conditioned (Y/N) | Area Fraction | Area (ft²) | Volume (ft³) | Multipliers | Number of People | People (Persons/1,000 ft²) [T24, 2025,Table 120.1-A]
Auditorium Area | Auditorium_FF_Zn | BaseAirSys5 | Classroom | Y | 5.043% | 10635.81 | 279168.51 | 1 | 1510.285 | 142
Exercise/Fitness Center and Gymnasium Areas | Aux_Gym_FF_Zn | BaseAirSys5 | Classroom | Y | 6.37% | 13434.61 | 352631.31 | 1 | 268.6922 | 20
Restrooms | Bathrooms_FF_Zn | BaseAirSys5 | Classroom | Y | 1.072% | 2260.58 | 29667.9 | 1 | 22.6058 | 10
Restrooms | Bathrooms_SF_Zn | BaseAirSys5-2 | Classroom | Y | 1.072% | 2260.58 | 29667.68 | 1 | 22.6058 | 10
Dining Area (Cafeteria/Fast Food) | Cafeteria_FF_Zn | BaseAirSys5 | Classroom | Y | 3.185% | 6717.34 | 88158.58 | 1 | 447.8227 | 66.6667
Classroom, Lecture, Training, Vocational Areas | Corner_Class_1_Pod_1_FF_Zn | BaseAirSys5 | Classroom | Y | 0.5053% | 1065.73 | 13986.7 | 1 | 53.2865 | 50
Classroom, Lecture, Training, Vocational Areas | Corner_Class_1_Pod_1_SF_Zn | BaseAirSys5-2 | Classroom | Y | 0.5053% | 1065.73 | 13986.6 | 1 | 53.2865 | 50
Classroom, Lecture, Training, Vocational Areas | Corner_Class_1_Pod_2_FF_Zn | BaseAirSys5 | Classroom | Y | 0.5053% | 1065.71 | 13986.42 | 1 | 53.2855 | 50
Classroom, Lecture, Training, Vocational Areas | Corner_Class_1_Pod_2_SF_Zn | BaseAirSys5-2 | Classroom | Y | 0.5053% | 1065.71 | 13986.31 | 1 | 53.2855 | 50
Classroom, Lecture, Training, Vocational Areas | Corner_Class_1_Pod_3_FF_Zn | BaseAirSys5 | Classroom | Y | 0.5053% | 1065.75 | 13986.89 | 1 | 53.2875 | 50
Classroom, Lecture, Training, Vocational Areas | Corner_Class_1_Pod_3_SF_Zn | BaseAirSys5-2 | Classroom | Y | 0.5053% | 1065.75 | 13986.79 | 1 | 53.2875 | 50
Classroom, Lecture, Training, Vocational Areas | Corner_Class_2_Pod_1_FF_Zn | BaseAirSys5 | Classroom | Y | 0.5053% | 1065.73 | 13986.66 | 1 | 53.2865 | 50
Classroom, Lecture, Training, Vocational Areas | Corner_Class_2_Pod_1_SF_Zn | BaseAirSys5-2 | Classroom | Y | 0.5053% | 1065.73 | 13986.55 | 1 | 53.2865 | 50
Classroom, Lecture, Training, Vocational Areas | Corner_Class_2_Pod_2_FF_Zn | BaseAirSys5 | Classroom | Y | 0.5053% | 1065.75 | 13986.89 | 1 | 53.2875 | 50
Classroom, Lecture, Training, Vocational Areas | Corner_Class_2_Pod_2_SF_Zn | BaseAirSys5-2 | Classroom | Y | 0.5053% | 1065.75 | 13986.79 | 1 | 53.2875 | 50
Classroom, Lecture, Training, Vocational Areas | Corner_Class_2_Pod_3_FF_Zn | BaseAirSys5 | Classroom | Y | 0.5053% | 1065.71 | 13986.42 | 1 | 53.2855 | 50
Classroom, Lecture, Training, Vocational Areas | Corner_Class_2_Pod_3_SF_Zn | BaseAirSys5-2 | Classroom | Y | 0.5053% | 1065.71 | 13986.31 | 1 | 53.2855 | 50
Corridor Area | Corridor_Pod_1_FF_Zn | BaseAirSys5 | Classroom | Y | 1.633% | 3444.79 | 45209.59 | 1 | 34.4479 | 10
Corridor Area | Corridor_Pod_1_SF_Zn | BaseAirSys5-2 | Classroom | Y | 1.633% | 3444.79 | 45209.24 | 1 | 34.4479 | 10
Corridor Area | Corridor_Pod_2_FF_Zn | BaseAirSys5 | Classroom | Y | 1.633% | 3444.75 | 45209.03 | 1 | 34.4475 | 10
Corridor Area | Corridor_Pod_2_SF_Zn | BaseAirSys5-2 | Classroom | Y | 1.633% | 3444.75 | 45208.69 | 1 | 34.4475 | 10
Corridor Area | Corridor_Pod_3_FF_Zn | BaseAirSys5 | Classroom | Y | 1.633% | 3444.75 | 45209.03 | 1 | 34.4475 | 10
Corridor Area | Corridor_Pod_3_SF_Zn | BaseAirSys5-2 | Classroom | Y | 1.633% | 3444.75 | 45208.69 | 1 | 34.4475 | 10
Exercise/Fitness Center and Gymnasium Areas | Gym_FF_Zn | BaseAirSys5 | Gym | Y | 10.09% | 21271.52 | 558334.4 | 1 | 425.4304 | 20
Kitchen/Food Preparation Area | Kitchen_FF_Zn | BaseAirSys5 | Kitchen | Y | 1.103% | 2325.26 | 30516.83 | 1 | 11.6263 | 5
Library (Reading Area) | Library_Media_Center_SF_Zn | BaseAirSys5-2 | Classroom | Y | 4.287% | 9042.6 | 118674.5 | 1 | 180.852 | 20
Lobby, Main Entry | Lobby_FF_Zn | BaseAirSys5 | Classroom | Y | 1.072% | 2260.62 | 29668.42 | 1 | 150.708 | 66.6667
Lobby, Main Entry | Lobby_SF_Zn | BaseAirSys5-2 | Classroom | Y | 1.072% | 2260.62 | 29668.19 | 1 | 150.708 | 66.6667
Corridor Area | Main_Corridor_FF_Zn | BaseAirSys5 | Classroom | Y | 5.819% | 12271.92 | 161057.23 | 1 | 122.7192 | 10
Corridor Area | Main_Corridor_SF_Zn | BaseAirSys5-2 | Classroom | Y | 5.819% | 12271.92 | 161056 | 1 | 122.7192 | 10
Electrical, Mechanical, Telephone Rooms | Mech_FF_Zn | BaseAirSys5 | Classroom | Y | 1.746% | 3681.67 | 48318.44 | 1 | 11.045 | 3
Electrical, Mechanical, Telephone Rooms | Mech_SF_Zn | BaseAirSys5-2 | Classroom | Y | 1.746% | 3681.67 | 48318.07 | 1 | 11.045 | 3
Classroom, Lecture, Training, Vocational Areas | Mult_Class_1_Pod_1_FF_Zn | BaseAirSys5 | Classroom | Y | 2.435% | 5134.9 | 67390.66 | 1 | 256.745 | 50
Classroom, Lecture, Training, Vocational Areas | Mult_Class_1_Pod_1_SF_Zn | BaseAirSys5-2 | Classroom | Y | 2.435% | 5134.9 | 67390.15 | 1 | 256.745 | 50
Classroom, Lecture, Training, Vocational Areas | Mult_Class_1_Pod_2_FF_Zn | BaseAirSys5 | Classroom | Y | 2.435% | 5134.8 | 67389.29 | 1 | 256.74 | 50
Classroom, Lecture, Training, Vocational Areas | Mult_Class_1_Pod_2_SF_Zn | BaseAirSys5-2 | Classroom | Y | 2.435% | 5134.8 | 67388.78 | 1 | 256.74 | 50
Classroom, Lecture, Training, Vocational Areas | Mult_Class_1_Pod_3_FF_Zn | BaseAirSys5 | Classroom | Y | 2.435% | 5134.97 | 67391.57 | 1 | 256.7485 | 50
Classroom, Lecture, Training, Vocational Areas | Mult_Class_1_Pod_3_SF_Zn | BaseAirSys5-2 | Classroom | Y | 2.435% | 5134.97 | 67391.06 | 1 | 256.7485 | 50
Classroom, Lecture, Training, Vocational Areas | Mult_Class_2_Pod_1_FF_Zn | BaseAirSys5 | Classroom | Y | 2.435% | 5134.88 | 67390.43 | 1 | 256.744 | 50
Classroom, Lecture, Training, Vocational Areas | Mult_Class_2_Pod_1_SF_Zn | BaseAirSys5-2 | Classroom | Y | 2.435% | 5134.88 | 67389.92 | 1 | 256.744 | 50
Classroom, Lecture, Training, Vocational Areas | Mult_Class_2_Pod_2_FF_Zn | BaseAirSys5 | Classroom | Y | 2.435% | 5134.97 | 67391.57 | 1 | 256.7485 | 50
Classroom, Lecture, Training, Vocational Areas | Mult_Class_2_Pod_2_SF_Zn | BaseAirSys5-2 | Classroom | Y | 2.435% | 5134.97 | 67391.06 | 1 | 256.7485 | 50
Classroom, Lecture, Training, Vocational Areas | Mult_Class_2_Pod_3_FF_Zn | BaseAirSys5 | Classroom | Y | 2.435% | 5134.8 | 67389.29 | 1 | 256.74 | 50
Classroom, Lecture, Training, Vocational Areas | Mult_Class_2_Pod_3_SF_Zn | BaseAirSys5-2 | Classroom | Y | 2.435% | 5134.8 | 67388.78 | 1 | 256.74 | 50
Office Area (>250 square feet) | Offices_FF_Zn | BaseAirSys5 | Classroom | Y | 2.715% | 5726.97 | 75160.96 | 1 | 57.2697 | 10
Office Area (>250 square feet) | Offices_SF_Zn | BaseAirSys5-2 | Classroom | Y | 2.715% | 5726.97 | 75160.39 | 1 | 57.2697 | 10
Total (11 Space types) | Total (46 spaces) | Total ( 5 HVAC zones) | Total (3 Schedule categories) | Total (46 Conditioned zones) | 100% | 210906.64 | 3363003.57 |  | 7500.4598
Background Data [To be deleted prior to publication]
N

## Envelope
Envelope - SchoolLarge
Element | Prototype | Assembly Type | Construction | Thermal properties | Vintage | Selected T24 | Note | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
External Wall | SchoolLarge | ExtWall_MetalFramed_NonRes | Metal frame + insulation + Gypsum board | U-value IP | Pre 1978 | N/A | ASHRAE 90.1, 2022, Table A3.4.3.1, 3.5", R-0 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292
[5 empty] | 1978-1997 | 1986 | Table 2-53V-16: Package A/ Heat Capacity was considered 10.0-14.99 (BTU/F/ft²) | 0.15083 | 0.15748 | 0.15748 | 0.14368 | 0.14368 | 0.21645 | 0.21645 | 0.21645 | 0.21645 | 0.21645 | 0.18622 | 0.18622 | 0.18622 | 0.15873 | 0.15873 | 0.15083
[5 empty] | 1998-2007 | 2001 | Table 1-H | 0.084 | 0.084 | 0.092 | 0.092 | 0.092 | 0.092 | 0.092 | 0.092 | 0.092 | 0.084 | 0.084 | 0.084 | 0.084 | 0.084 | 0.084 | 0.084
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.102 | 0.059 | 0.11 | 0.059 | 0.102 | 0.11 | 0.11 | 0.102 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.042 | 0.059
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.078 | 0.053 | 0.102 | 0.053 | 0.095 | 0.102 | 0.102 | 0.095 | 0.053 | 0.053 | 0.042 | 0.053 | 0.053 | 0.053 | 0.038 | 0.053
Roof | SchoolLarge | FlatRoof_WoodFramedAndOther_NonRes | Built-up Roof roof membrane+roof insulation+metal decking | U-value IP | Pre 1978 | N/A | Table 2-53V-16: Considering 30 years for roof/ insulation replacement. | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 1978-1997 | 1992 |  | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 1998-2007 | 2001 | Table 1-H | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.049 | 0.039 | 0.039 | 0.039 | 0.049 | 0.075 | 0.067 | 0.067 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.047 | 0.047 | 0.047 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028
Windows | SchoolLarge | FixedWindow_NonRes | Single pane | U-value IP | Pre 1978 | N/A | ASHRAE Handbook of Fundamentals (Table 4-Ch15) for single pane & T24, 2013 for double pane (33%-67%)* | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108
[5 empty] | 1978-1997 | N/A |  | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108 | 0.6108
|  |  | Double pane |  | 1998-2007 | 2001 | Table 1-H | 0.49 | 0.49 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.34 | 0.36 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.36
| SchoolLarge | FixedWindow_NonRes | Single pane | SHGC | Pre 1978 | N/A | ASHRAE Handbook of Fundamentals (Table 10-Ch15) for single pane & T24, 2013 for double pane (33%-67%)* | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282
[5 empty] | 1978-1997 | N/A |  | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282 | 0.4282
|  |  | Double pane |  | 1998-2007 | 2001 | Table 1-H - WWR:31-40% / SHGC non-north | 0.43 | 0.36 | 0.41 | 0.41 | 0.41 | 0.34 | 0.34 | 0.34 | 0.34 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.43
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.22 | 0.25 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.25
Infiltration
[5 empty] | Vintage | I_75 6-Sided Inifltration rate @ 75 pa | Note | I-design (cfm/ft²) (4-sided Infiltration rate at normal presure) (Design flow rate approach and Flow/Exterior Wall Area calulation method)
|  |  |  | Infiltration | Pre 1978 | 1.1 | 2022 CASE report (Table 38) | 0.6146
[5 empty] | 1978-1997 | 1.1 | 2022 CASE report (Table 38) | 0.6146
[5 empty] | 1998-2007 | 1.1 | 2022 CASE report (Table 38) | 0.6146
[5 empty] | 2008-2018 | 1 | 2022 CASE report (Table 38) & T24, 2008-2016 (Table 140.3-B)--Air barrier is required in CZ 10-16 | 0.5624
[5 empty] | 2019+ | 0.6 | 2022 CASE report (Table 38) & T24, 2025 (Table 140.3-B)--Air barrier is required in all CZs | 0.3352
Source: T24 air barrier requirements (all editions) and the standardized infiltration rate reported in the 2022 CASE report and Dodge 2023 data
|  |  |  | Air Lekage Memo: |  | Infiltration_rate_report_14May2025-Short-Version.docx

## HVAC System
HVAC system - SchoolLarge
Vintage | Zones | Heating | Cooling | Air Distribution | Source | Note
Exisiting | All Space Types | Gas Boiler | Air-cooled Chiller | VAV + Hydronic reheat | Engineering Judgement | System 6
New Construction | All Space Types | Gas Boiler | Air-cooled Chiller | VAV + Hydronic reheat | Engineering Judgement | System 6
Efficiency of HVAC system
Vintage | Upgrade/Installed year | Gas-Fired Boiler | Heating DX | Water Cooled Chiller | Heat Rejection (Cooling Tower) | Source | Note
Pre 1978 | 2008 | If 300,000 Btu/h ≤ input < 2.5 MMBtu/h: Et ≥ 75% | n/a | Centrifugal ≥ 300: COP_FL ≥ 6.10 IPLV COP ≥ 6.40 (ARI 550/590) | Axial fan Open-circuit cooling tower--95°F entering water 85°F leaving water 75°F entering air wb--≥ 38.2 gpm/hp | T24, 2008, Table 112-D (for chiller COP) – Table 112-G (for boiler thermal efficiency)
1978-1997
1998-2007
2008-2018 | 2013 | 300k–2.5 MMBtu/h: Et ≥ 80% > 2.5 MMBtu/h: Ec ≥ 82% | n/a | Positive-displacement (Screw) ≥ 300 and < 600 tons: Path B ≤ 0.639 kW/ton ≤ 0.490 kW/ton IPLV (AHRI 550/590) | Axial fan Open-circuit cooling tower--95°F entering water 85°F leaving water 75°F entering air wb--≥ 42.1 gpm/hp | T24, 2013 Table 110.2-D ( for air cooled chiller) T24, 2013 Table 110.2-K (for boiler efficiency with capacity between 300,000-2,500,000 Btu/hr)
New Construction | 2025 | Boiler (hot-water, gas, > 2.5 MMBtu/h): Ec ≥ 85% | n/a | Positive-displacement (Screw) ≥ 300 and < 600 tons: Path B ≤ 0.625 kW/ton ≤ 0.410 kW/ton IPLV | Axial fan Open-circuit cooling tower--95°F entering water 85°F leaving water 75°F entering air wb--≥ 42.1 gpm/hp | T24, 2025 , Table 110.2-D (for chiller COP) Table 110.2-J (for Boiler thermal efficiency)
|  | * Et = Combustion efficiency | * Et = Thermal efficiency
Fan power
Vintage | Approach | System | Total Static Pressure (TSP) in w.c. [PNNL 20405, 2010, Table 5.11] | Fan Efficiency [ACM, 2025] | Fan Motor and Drive Efficiency [ACM 2025, Table 14] | W/cfm [ACM 2025, Table 15] | Data Source | Note
Existing | PNNL TSP | VAV | 5.58 for VAV >=20,000 cfm | 0.65 | 0.9 |  | PNNL 2010 TSD
Brake horse power (bhp)=(Supply cfm*TSP in w.c.)/(6356*Fan efficiency)
Fan power (w/cfm) = bhp/motor and drive efficiency *746
New Construction | ACM 2025 | VAV | 4.7201 | 0.65 | 0.9 | 0.947 | 2025 ACM
* 0.9 is an average fan efficiency according to ACM 2025, Table 14
Fan total eff (E+ input) = 0.65 x Motor_eff
TSP (E+ input) in w.c. = Motor_eff/746 x (6356 x Fan_eff) x W/cfm
Fan_eff=0.65
Background Data [To be deleted prior to publication]

## Thermostat
Thermostat Setpoints - SchoolLarge
Setpoint | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16 | Source
School Heating Setpoint (F) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | T24 2022 - Appendix 5.4B
School Heating Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
School Cooling Setpoint (F) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | T24 2022 - Appendix 5.4B
School Cooling Setback (F) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85

## Ventilation
Outdoor Airflow Rate - SchoolLarge
Space Type | Space/Thermal Zone | Number of People | Floor Area (ft²) | cfm/person [T24, 2025, Equation 120.1-F and Table 120.1-A] | cfm/ft² [T24, 2025, Equation 120.1-F and Table 120.1-A] | Required exhaust rate-CFM/ft²- [T24, 2025, Table 120.1-B – minimum exhaust rates] | Total cfm driven by people | Total cfm driven by area | Total cfm driven by exhaust | Total cfm | Notes
Auditorium Area | Auditorium_FF_Zn | 1510.285 | 10635.81 | 15 | 1.065 |  | 22654.2753 | 11327.1376 | 0 | 22654.2753
Exercise/Fitness Center and Gymnasium Areas | Aux_Gym_FF_Zn | 268.6922 | 13434.61 | 15 | 0.15 |  | 4030.383 | 2015.1915 | 0 | 4030.383
Restrooms | Bathrooms_FF_Zn | 22.6058 | 2260.58 | 15 | 0.075 |  | 339.087 | 169.5435 | 0 | 339.087
Restrooms | Bathrooms_SF_Zn | 22.6058 | 2260.58 | 15 | 0.075 |  | 339.087 | 169.5435 | 0 | 339.087
Dining Area (Cafeteria/Fast Food) | Cafeteria_FF_Zn | 447.8227 | 6717.34 | 15 | 0.495 |  | 6717.34 | 3325.0833 | 0 | 6717.34
Classroom, Lecture, Training, Vocational Areas | Corner_Class_1_Pod_1_FF_Zn | 53.2865 | 1065.73 | 15 | 0.375 |  | 799.2975 | 399.6488 | 0 | 799.2975
Classroom, Lecture, Training, Vocational Areas | Corner_Class_1_Pod_1_SF_Zn | 53.2865 | 1065.73 | 15 | 0.375 |  | 799.2975 | 399.6488 | 0 | 799.2975
Classroom, Lecture, Training, Vocational Areas | Corner_Class_1_Pod_2_FF_Zn | 53.2855 | 1065.71 | 15 | 0.375 |  | 799.2825 | 399.6413 | 0 | 799.2825
Classroom, Lecture, Training, Vocational Areas | Corner_Class_1_Pod_2_SF_Zn | 53.2855 | 1065.71 | 15 | 0.375 |  | 799.2825 | 399.6413 | 0 | 799.2825
Classroom, Lecture, Training, Vocational Areas | Corner_Class_1_Pod_3_FF_Zn | 53.2875 | 1065.75 | 15 | 0.375 |  | 799.3125 | 399.6562 | 0 | 799.3125
Classroom, Lecture, Training, Vocational Areas | Corner_Class_1_Pod_3_SF_Zn | 53.2875 | 1065.75 | 15 | 0.375 |  | 799.3125 | 399.6562 | 0 | 799.3125
Classroom, Lecture, Training, Vocational Areas | Corner_Class_2_Pod_1_FF_Zn | 53.2865 | 1065.73 | 15 | 0.375 |  | 799.2975 | 399.6488 | 0 | 799.2975
Classroom, Lecture, Training, Vocational Areas | Corner_Class_2_Pod_1_SF_Zn | 53.2865 | 1065.73 | 15 | 0.375 |  | 799.2975 | 399.6488 | 0 | 799.2975
Classroom, Lecture, Training, Vocational Areas | Corner_Class_2_Pod_2_FF_Zn | 53.2875 | 1065.75 | 15 | 0.375 |  | 799.3125 | 399.6562 | 0 | 799.3125
Classroom, Lecture, Training, Vocational Areas | Corner_Class_2_Pod_2_SF_Zn | 53.2875 | 1065.75 | 15 | 0.375 |  | 799.3125 | 399.6562 | 0 | 799.3125
Classroom, Lecture, Training, Vocational Areas | Corner_Class_2_Pod_3_FF_Zn | 53.2855 | 1065.71 | 15 | 0.375 |  | 799.2825 | 399.6413 | 0 | 799.2825
Classroom, Lecture, Training, Vocational Areas | Corner_Class_2_Pod_3_SF_Zn | 53.2855 | 1065.71 | 15 | 0.375 |  | 799.2825 | 399.6413 | 0 | 799.2825
Corridor Area | Corridor_Pod_1_FF_Zn | 34.4479 | 3444.79 | 30 | 0.15 |  | 1033.437 | 516.7185 | 0 | 1033.437
Corridor Area | Corridor_Pod_1_SF_Zn | 34.4479 | 3444.79 | 30 | 0.15 |  | 1033.437 | 516.7185 | 0 | 1033.437
Corridor Area | Corridor_Pod_2_FF_Zn | 34.4475 | 3444.75 | 30 | 0.15 |  | 1033.425 | 516.7125 | 0 | 1033.425
Corridor Area | Corridor_Pod_2_SF_Zn | 34.4475 | 3444.75 | 30 | 0.15 |  | 1033.425 | 516.7125 | 0 | 1033.425
Corridor Area | Corridor_Pod_3_FF_Zn | 34.4475 | 3444.75 | 30 | 0.15 |  | 1033.425 | 516.7125 | 0 | 1033.425
Corridor Area | Corridor_Pod_3_SF_Zn | 34.4475 | 3444.75 | 30 | 0.15 |  | 1033.425 | 516.7125 | 0 | 1033.425
Exercise/Fitness Center and Gymnasium Areas | Gym_FF_Zn | 256.7485 | 5134.97 | 15 | 0.15 |  | 3851.2275 | 770.2455 | 0 | 3851.2275
Kitchen/Food Preparation Area | Kitchen_FF_Zn | 256.7485 | 5134.97 | 50 | 0.15 |  | 12837.425 | 770.2455 | 0 | 12837.425
Library (Reading Area) | Library_Media_Center_SF_Zn | 256.744 | 5134.88 | 15 | 0.15 |  | 3851.16 | 770.232 | 0 | 3851.16
Lobby, Main Entry | Lobby_FF_Zn | 256.744 | 5134.88 | 30 | 0.15 |  | 7702.32 | 770.232 | 0 | 7702.32
Lobby, Main Entry | Lobby_SF_Zn | 150.708 | 2260.62 | 30 | 0.15 |  | 4521.24 | 339.093 | 0 | 4521.24
Corridor Area | Main_Corridor_FF_Zn | 122.7192 | 12271.92 | 30 | 0.15 |  | 3681.576 | 1840.788 | 0 | 3681.576
Corridor Area | Main_Corridor_SF_Zn | 122.7192 | 12271.92 | 30 | 0.15 |  | 3681.576 | 1840.788 | 0 | 3681.576
Electrical, Mechanical, Telephone Rooms | Mech_FF_Zn | 11.045 | 3681.67 | 30 | 0.15 |  | 331.3503 | 552.2505 | 0 | 552.2505
Electrical, Mechanical, Telephone Rooms | Mech_SF_Zn | 11.045 | 3681.67 | 30 | 0.15 |  | 331.3503 | 552.2505 | 0 | 552.2505
Classroom, Lecture, Training, Vocational Areas | Mult_Class_1_Pod_1_FF_Zn | 256.745 | 5134.9 | 15 | 0.375 |  | 3851.175 | 1925.5875 | 0 | 3851.175
Classroom, Lecture, Training, Vocational Areas | Mult_Class_1_Pod_1_SF_Zn | 256.745 | 5134.9 | 15 | 0.375 |  | 3851.175 | 1925.5875 | 0 | 3851.175
Classroom, Lecture, Training, Vocational Areas | Mult_Class_1_Pod_2_FF_Zn | 256.74 | 5134.8 | 15 | 0.375 |  | 3851.1 | 1925.55 | 0 | 3851.1
Classroom, Lecture, Training, Vocational Areas | Mult_Class_1_Pod_2_SF_Zn | 0 | 0 | 15 | 0.375 |  | 0 | 0 | 0 | 0
Classroom, Lecture, Training, Vocational Areas | Mult_Class_1_Pod_3_FF_Zn | 0 | 0 | 15 | 0.375 |  | 0 | 0 | 0 | 0
Classroom, Lecture, Training, Vocational Areas | Mult_Class_1_Pod_3_SF_Zn | 0 | 0 | 15 | 0.375 |  | 0 | 0 | 0 | 0
Classroom, Lecture, Training, Vocational Areas | Mult_Class_2_Pod_1_FF_Zn | 0 | 0 | 15 | 0.375 |  | 0 | 0 | 0 | 0
Classroom, Lecture, Training, Vocational Areas | Mult_Class_2_Pod_1_SF_Zn | 150.708 | 2260.62 | 15 | 0.375 |  | 2260.62 | 847.7325 | 0 | 2260.62
Classroom, Lecture, Training, Vocational Areas | Mult_Class_2_Pod_2_FF_Zn | 122.7192 | 12271.92 | 15 | 0.375 |  | 1840.788 | 4601.97 | 0 | 4601.97
Classroom, Lecture, Training, Vocational Areas | Mult_Class_2_Pod_2_SF_Zn | 122.7192 | 12271.92 | 15 | 0.375 |  | 1840.788 | 4601.97 | 0 | 4601.97
Classroom, Lecture, Training, Vocational Areas | Mult_Class_2_Pod_3_FF_Zn | 11.045 | 3681.67 | 15 | 0.375 |  | 165.6752 | 1380.6263 | 0 | 1380.6263
Classroom, Lecture, Training, Vocational Areas | Mult_Class_2_Pod_3_SF_Zn | 11.045 | 3681.67 | 15 | 0.375 |  | 165.6752 | 1380.6263 | 0 | 1380.6263
Office Area (>250 square feet) | Offices_FF_Zn | 256.745 | 5134.9 | 30 | 0.15 |  | 7702.35 | 770.235 | 0 | 7702.35
Office Area (>250 square feet) | Offices_SF_Zn | 256.745 | 5134.9 | 30 | 0.15 |  | 7702.35 | 770.235 | 0 | 7702.35
Total (11 Space types) | Total (46 spaces) | 7500.4598 | 210906.64 |  |  |  | 123893.2377 | 53238.8165 | 0 | 132287.3043

## Water Heater
Water Heater -SchoolLarge
Vintage | WH Type | Efficiency | Tank Volume (gal) | Tank Loss |  | Note
Existing | Gas | 0.8 | 526.5104 | 3342.2073 | (Btu/hr)
New Construction | Gas | 0.8 | 526.5104 | 3342.2073 | (Btu/hr) | Section 1605.1. Federal and State Standards for Federally-Regulated Appliances.
Peak Hot Water Consumption
Space Name | Baseline WH Type [T24, 2022, Appendix 5.4A , sheet: "2022 SpaceFuncData-Input"] | New Construction: Baseline WH Type ACM 2025 | Total Area (ft²) | Number of People | Hot Water Usage Specification (gal/hr per person) [T24, 2022, Appendix 5.4A , sheet: "2022 SpaceFuncData-Input"] | Peak Hot Water Usage (gal/hr) | Peak Hot Water Usage (gal/min)
Auditorium_FF_Zn | Gas |  | 10635.81 | 1510.285 | 0.09 | 135.9257 | 2.2654
Aux_Gym_FF_Zn | Gas |  | 13434.61 | 268.6922 | 0.18 | 48.3646 | 0.80608
Bathrooms_FF_Zn | Gas |  | 2260.58 | 22.6058 | 0 | 0 | 0
Bathrooms_SF_Zn | Gas |  | 2260.58 | 22.6058 | 0 | 0 | 0
Cafeteria_FF_Zn | Gas |  | 6717.34 | 447.8227 | 0.578 | 258.8415 | 4.314
Corner_Class_1_Pod_1_FF_Zn | Gas |  | 1065.73 | 53.2865 | 0.18 | 9.5916 | 0.15986
Corner_Class_1_Pod_1_SF_Zn | Gas |  | 1065.73 | 53.2865 | 0.18 | 9.5916 | 0.15986
Corner_Class_1_Pod_2_FF_Zn | Gas |  | 1065.71 | 53.2855 | 0.18 | 9.5914 | 0.15986
Corner_Class_1_Pod_2_SF_Zn | Gas |  | 1065.71 | 53.2855 | 0.18 | 9.5914 | 0.15986
Corner_Class_1_Pod_3_FF_Zn | Gas |  | 1065.75 | 53.2875 | 0.18 | 9.5917 | 0.15986
Corner_Class_1_Pod_3_SF_Zn | Gas |  | 1065.75 | 53.2875 | 0.18 | 9.5917 | 0.15986
Corner_Class_2_Pod_1_FF_Zn | Gas |  | 1065.73 | 53.2865 | 0.18 | 9.5916 | 0.15986
Corner_Class_2_Pod_1_SF_Zn | Gas |  | 1065.73 | 53.2865 | 0.18 | 9.5916 | 0.15986
Corner_Class_2_Pod_2_FF_Zn | Gas |  | 1065.75 | 53.2875 | 0.18 | 9.5917 | 0.15986
Corner_Class_2_Pod_2_SF_Zn | Gas |  | 1065.75 | 53.2875 | 0.18 | 9.5917 | 0.15986
Corner_Class_2_Pod_3_FF_Zn | Gas |  | 1065.71 | 53.2855 | 0.18 | 9.5914 | 0.15986
Corner_Class_2_Pod_3_SF_Zn | Gas |  | 1065.71 | 53.2855 | 0.18 | 9.5914 | 0.15986
Corridor_Pod_1_FF_Zn | Gas |  | 3444.79 | 34.4479 | 0 | 0 | 0
Corridor_Pod_1_SF_Zn | Gas |  | 3444.79 | 34.4479 | 0 | 0 | 0
Corridor_Pod_2_FF_Zn | Gas |  | 3444.75 | 34.4475 | 0 | 0 | 0
Corridor_Pod_2_SF_Zn | Gas |  | 3444.75 | 34.4475 | 0 | 0 | 0
Corridor_Pod_3_FF_Zn | Gas |  | 3444.75 | 34.4475 | 0 | 0 | 0
Corridor_Pod_3_SF_Zn | Gas |  | 3444.75 | 34.4475 | 0 | 0 | 0
Gym_FF_Zn | Gas |  | 21271.52 | 425.4304 | 0.18 | 76.5775 | 1.2763
Kitchen_FF_Zn | Gas |  | 2325.26 | 11.6263 | 0.578 | 6.72 | 0.112
Library_Media_Center_SF_Zn | Gas |  | 9042.6 | 180.852 | 0.18 | 32.5534 | 0.54256
Lobby_FF_Zn | Gas |  | 2260.62 | 150.708 | 0.09 | 13.5637 | 0.22606
Lobby_SF_Zn | Gas |  | 2260.62 | 150.708 | 0.09 | 13.5637 | 0.22606
Main_Corridor_FF_Zn | Gas |  | 12271.92 | 122.7192 | 0 | 0 | 0
Main_Corridor_SF_Zn | Gas |  | 12271.92 | 122.7192 | 0 | 0 | 0
Mech_FF_Zn | Gas |  | 3681.67 | 11.045 | 0.18 | 1.9881 | 0.033135
Mech_SF_Zn | Gas |  | 3681.67 | 11.045 | 0.18 | 1.9881 | 0.033135
Mult_Class_1_Pod_1_FF_Zn | Gas |  | 5134.9 | 256.745 | 0.18 | 46.2141 | 0.77023
Mult_Class_1_Pod_1_SF_Zn | Gas |  | 5134.9 | 256.745 | 0.18 | 46.2141 | 0.77023
Mult_Class_1_Pod_2_FF_Zn | Gas |  | 5134.8 | 256.74 | 0.18 | 46.2132 | 0.77022
Mult_Class_1_Pod_2_SF_Zn | Gas |  | 5134.8 | 256.74 | 0.18 | 46.2132 | 0.77022
Mult_Class_1_Pod_3_FF_Zn | Gas |  | 5134.97 | 256.7485 | 0.18 | 46.2147 | 0.77025
Mult_Class_1_Pod_3_SF_Zn | Gas |  | 5134.97 | 256.7485 | 0.18 | 46.2147 | 0.77025
Mult_Class_2_Pod_1_FF_Zn | Gas |  | 5134.97 | 256.7485 | 0.18 | 46.2147 | 0.77025
Mult_Class_2_Pod_1_SF_Zn | Gas |  | 5134.88 | 256.744 | 0.18 | 46.2139 | 0.77023
Mult_Class_2_Pod_2_FF_Zn | Gas |  | 5134.88 | 256.744 | 0.18 | 46.2139 | 0.77023
Mult_Class_2_Pod_2_SF_Zn | Gas |  | 5134.97 | 256.7485 | 0.18 | 46.2147 | 0.77025
Mult_Class_2_Pod_3_FF_Zn | Gas |  | 5134.97 | 256.7485 | 0.18 | 46.2147 | 0.77025
Mult_Class_2_Pod_3_SF_Zn | Gas |  | 5134.8 | 256.74 | 0.18 | 46.2132 | 0.77022
Offices_FF_Zn | Gas |  | 5134.8 | 256.74 | 0.18 | 46.2132 | 0.77022
Offices_SF_Zn | Gas |  | 5726.97 | 57.2697 | 0.18 | 10.3085 | 0.17181
Total |  |  | 210314.64 | 7699.9386 |  | 1316.2761 | 21.9379
Water Heater Capacity, Tank Capacity, and Tank Loss
WH Type | Peak Hot Water Usage (gal/hr) | Heat Output (Btu/hr) [ACM, 2025, 5.9.2: Rated capacity section] | WH Capacity (Btu/hr) [ACM, 2025, 5.9.2: Rated capacity section] | Required Energy Input (Btu/hr) | Storage Volume (gal) | Standby Loss | Unit | Off/On Cycle Loss Coefficient to Ambient Temp (Btu/h-F) | Source
Gas Storage WH | 1316.2761 | 872712.1161 | 523627.2697 | 654534.0871 | 526.5104 | 3342.2073 | Btu/hr | 49.8837 | Standby loss equation: Title 20, §1605.1 Table F-4 WH capacity equation: ACM, 2025, 5.9.2: Rated capacity section)
Electric resistance WH | 0 | 0 | 0 | 0 | 0 | 0 | %hr | 0
Total | 1316.2761 | 872712.1161 | 523627.2697 | 654534.0871 | 526.5104
Design supply temperature (F) | 135 | Ref: T24 2022 - Appendix 5.4B |  |  | Standby Loss for Existing | 3342.2073 | Btu/hr | 49.8837
Cold Water supply temperature (F) | 55 | Ref: ACM, 2025, 5.9.2: Rated capacity section
WH system factor | 0.6 | Ref: ACM, 2025, 5.9.2: Rated capacity section
Reheat multiplier | 0.4
* The 0.40 multiplier is a storage sizing factor used to account for the fact that the water heater doesn't need to store the full peak hour demand—it can reheat water during that time. This factor assumes that the heater will recover part of the hot water used during the peak hour, so only 40% of the peak hour demand needs to be stored at any given moment.
**For Gas Water Heater: UA(Btu/h-°F)​=Q˙​SL​ (Btu/h)/ΔT (∘F)​
Ambient temp | 68
Delta T | 67
** For Electric Water Heater: UA(Btu/h-°F)​= 0.0834 *SL​ (%/hr)*V gal
Background Data [To be deleted prior to publication]

## Interior Lights
Interior Lighting - SchoolLarge
Space Type | New Construction |  |  | Existing
| Lighting density (W/ft²) | Additional lighting power for porTable lighting (W/ft²) | Source | LPD (W/ft²) | Additional LPD for PorTable Lighting (W/ft²) | Source
Auditorium Area | 0.7 |  | T24, 2025, Table 140.6 C (Area category method) | 1.4 |  | T24, 2016, Table 140.6 C (Area category method)
Exercise/Fitness Center and Gymnasium Areas | 0.5 |  |  | 1
Restrooms | 0.65 |  |  | 0.6
Dining Area (Cafeteria/Fast Food) | 0.6 |  |  | 1
Classroom, Lecture, Training, Vocational Areas | 0.6 |  |  | 1.2
Corridor Area | 0.4 |  |  | 0.6
Kitchen/Food Preparation Area | 0.6 |  |  | 1.2
Library (Reading Area) | 0.65 |  |  | 1.1
Lobby, Main Entry | 0.6 |  |  | 0.95
Electrical, Mechanical, Telephone Rooms | 0.6 |  |  | 0.55
Office Area (>250 square feet) | 0.6 |  |  | 0.75

## Ext Lighting
Exterior Lighting - SchoolLarge
Motion Controlled Luminaires (W) | Non-motion Controlled Luminaires (W) | Total (W) | Source
2296.1931 | 8911.3994 | 11207.5926 | T24, 2022 & 2025 2019 Outdoor Lighting CASE report PNNL 90.1-2010 TSD
Exterior Lighting
Items (Assume LZ2) | Assumptions [2019 Outdoor Lighting CASE Report & PNNL 90.1-2010 TS] |  | Unit | Lighting Power Allowance [T24, 2025, Table 140.7-A & 140.7-B] | Unit | Exterior Lighting Power (W)
IWA (Initial Wattage Allowance) |  |  |  | 200 | (W) | 200
Parking area | 400 ft² for every parking space 1 parking space per 830 ft² of gross building area | 101641.7446 | (ft²) | 0.019 | (W/ft²) | 1931.1931
Building Entrance | 5 building entrance per PNNL Model (1 per 10,000 ft² footprint) | 11 | (count) | 15 | (W/ea) | 165
Hardscape Ornamental Light | 0.1 ft² per 1 ft² of gross building area for hardscape ornamental light | 21090.662 | (ft²) | 0.007 | (W/ft²) | 147.6346
Building façade | 0.1 W per 1 ft² of facade area Façade Area = Perimeter × 0.5 × max ( height and 30) (30 ft is the max height that is lit) * The 0.5 factor assumes that only half of the perimeter walls are lit. -Formula ia developed based on the 2019 Outdoor Lighting CASE report | 87637.648 | (ft²) | 0.1 | (W/ft²) | 8763.7648
Motion Controlled Luminaires (W) | [5 empty] | 2296.1931
Non-motion-controlled Luminaires | [5 empty] | 8911.3994
Total | [5 empty] | 11207.5926
Max Height (ft) | 28
Building footprint | 105453.31
Floors | 2
Perimeter(ft) | 1564.958
Background Data [To be deleted prior to publication]
Total floor area (ft²) | 210906.62

## Equipment
Equipment - SchoolLarge
Space Type | Plug load Power Density (W/ft²) | Gas Power Density (Btu/hr-ft²) | Refrigeration Power Density (W/ft²) | Source
Auditorium Area | 1 | 0 | 0 | T24 2022 - Appendix 5.4A
Exercise/Fitness Center and Gymnasium Areas | 0.5 | 0 | 0
Restrooms | 0 | 0 | 0
Dining Area (Cafeteria/Fast Food) | 0.5 | 0 | 0.25
Corridor Area | 0 | 0 | 0 | T24 2022 - Appendix 5.4A
Kitchen/Food Preparation Area | 1.5 | 17.5377 | 1.12 | Plug load and schedules project with CEC, 2025
Library (Reading Area) | 1.5 | 0 | 0 | T24 2022 - Appendix 5.4A
Lobby, Main Entry | 0.5 | 0 | 0
Electrical, Mechanical, Telephone Rooms | 3 | 0 | 0
Classroom, Lecture, Training, Vocational Areas | 0.8 | 0 | 0
Office Area (>250 square feet) | 0.7 | 0 | 0
Elevator
Vintages | No of Elevator | Design Load (W) | Source
New Construction and Existing | 2 | 11793.11 | PNNL ASHRAE 90.1 2019 Large School prototype
Assumptions for elevators:
One elevator for approximately 50,000 ft² in use. |  |  |  |  | https://buildingandinteriors.com/find-the-magic-number-elevators-per-building/
For every two floors or two and a half floors, one more elevator was added.
An in-use rate of 70% for the floor area was assumed, based on engineering judgment.
Calculated number of Elevators: |  | 2
Calculate Elevator load (kw)based on ACM 2022: |  | 20 | 12 kW is PNNL ASHRE 90.1 2019 elevator load |  | 11.7931
ACM 2022 suggestion for elevator load (kw): |  | 10
Elevator load will be defined as exterior load not equipment load.

## Schedules
Schedules - SchoolLarge
Zone | Schedule Category | Schedule | Source | Type | Hour
[5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
School Zones | Classroom | Occupancy | T24 2022 - Appendix 5.4B [School] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.75 | 0.9 | 0.9 | 0.8 | 0.8 | 0.8 | 0.8 | 0.45 | 0.15 | 0.05 | 0.15 | 0.2 | 0.2 | 0.1 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School Zones | Classroom | Lights | T24 2022 - Appendix 5.4B [School] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.6 | 0.65 | 0.65 | 0.65 | 0.55 | 0.55 | 0.55 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.3 | 0.05 | 0.05
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
School Zones | Classroom | ElecEquipment | T24 2022 - Appendix 5.4B [School] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.85 | 0.95 | 0.95 | 0.95 | 0.8 | 0.8 | 0.8 | 0.7 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.3 | 0.05 | 0.05
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
School Zones | Classroom | ServiceHotWater | T24 2022 - Appendix 5.4B [School] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09
|  |  |  | Saturday | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
|  |  |  | Sunday | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
School Zones | Classroom | GasEquipment | T24 2022 - Appendix 5.4B [School] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.75 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School Zones | Classroom | Refrigeration | T24 2022 - Appendix 5.4B [School] | Weekday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Saturday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Sunday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
School Zones | Classroom | HVACAvail | T24 2022 - Appendix 5.4B [School] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School Zones | Classroom | Infiltration | T24 2022 - Appendix 5.4B [School] | Weekday | 0 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1
|  |  |  | Saturday | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Sunday | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
School Zones | Classroom | HtgSetpt | T24 2022 - Appendix 5.4B [School] | Weekday | 60 | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 60 | 60
|  |  |  | Saturday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  |  | Sunday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
School Zones | Classroom | ClgSetpt | T24 2022 - Appendix 5.4B [School] | Weekday | 85 | 85 | 85 | 85 | 85 | 85 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 85 | 85
|  |  |  | Saturday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 70 | 70 | 70 | 70 | 70 | 70 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
|  |  |  | Sunday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
School Zones | Classroom | Infiltration | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
Kitchen |  | Other
Kitchen Zone | Kitchen | Occupancy | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitchen Zone | Kitchen | HVACAvail | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitchen Zone | Kitchen | Lights | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitchen Zone | Kitchen | ElecEquipment | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.3 | 0.9 | 0.9 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.7 | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitchen Zone | Kitchen | HtgSetpt | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  |  | Saturday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  |  | Sunday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Kitchen Zone | Kitchen | ClgSetpt | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
|  |  |  | Saturday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
|  |  |  | Sunday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
Kitchen Zone | Kitchen | OAControl | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitchen Zone | Kitchen | Infiltration | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
Kitchen Zone | Kitchen | Refrigeration | T24 2022 - Appendix 5.4B [School] | Weekday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Saturday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Sunday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
Kitchen Zone | Kitchen | GasEquipment | T24 2022 - Appendix 5.4B [School] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.75 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitchen Zone | Kitchen | ServiceHotWater | T24 2022 - Appendix 5.4B [School] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09
|  |  |  | Saturday | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
|  |  |  | Sunday | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
Gym |  | Other
Gym Zone | Gym | Occupancy | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.5 | 0.25 | 0.25 | 0.05 | 0.25 | 0.95 | 0.95 | 0.25 | 0.2 | 0.2 | 0.2 | 0.15 | 0.15 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gym Zone | Gym | HVACAvail | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gym Zone | Gym | Lights | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gym Zone | Gym | ElecEquipment | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.3 | 0.9 | 0.9 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.7 | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gym Zone | Gym | HtgSetpt | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 60 | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 60 | 60 | 60 | 60
|  |  |  | Saturday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  |  | Sunday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Gym Zone | Gym | ClgSetpt | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 85 | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 85 | 85 | 85 | 85
|  |  |  | Saturday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
|  |  |  | Sunday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
Gym Zone | Gym | OAControl | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gym Zone | Gym | Infiltration | T24 2022 - Appendix 5.4B Updated based on the Plug Loads project | Weekday | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
Gym Zone | Gym | ServiceHotWater | T24 2022 - Appendix 5.4B [School] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09
|  |  |  | Saturday | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
|  |  |  | Sunday | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
Other |  | Other
| Building | Elevator | T24 2022 - Appendix 5.4B, [School] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Building | ExtLightingNonMotionCtrl |  | Weekday | bar: Hour 1 to Hour 24
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
| Building | ExtLightingMotionCtrl |  | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Auditorium | Building | PerformanceSpcPeopleActivityLevel | Based on Activity level schedules in CEC Prototypes | Weekday | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6
|  |  |  | Saturday | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6
|  |  |  | Sunday | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6
Gym | Building | GymPeopleActivityLevel | Based on Activity level schedules in CEC Prototypes | Weekday | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2
|  |  |  | Saturday | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2
|  |  |  | Sunday | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2 | 331.2
Classroom | Building | MeetingPeopleActivityLevel | Based on Activity level schedules in CEC Prototypes | Weekday | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2
|  |  |  | Saturday | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2
|  |  |  | Sunday | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2
DiningArea | Building | DiningAreaPeopleActivityLevel | Based on Activity level schedules in CEC Prototypes | Weekday | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2
|  |  |  | Saturday | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2
|  |  |  | Sunday | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2 | 161.2
Library, Office | Building | FunctionalAreaPeopleActivityLevel | Based on Activity level schedules in CEC Prototypes | Weekday | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
|  |  |  | Saturday | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
|  |  |  | Sunday | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
Lobby, Mech, Corridor, Restroom | Building | CommonAreaPeopleActivityLevel | Based on Activity level schedules in CEC Prototypes | Weekday | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5
|  |  |  | Saturday | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5
|  |  |  | Sunday | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5
Kitchen | Building | KitchenPeopleActivityLevel | Based on Activity level schedules in CEC Prototypes | Weekday | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033
|  |  |  | Saturday | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033
|  |  |  | Sunday | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033 | 219.8033
Background Data [To be deleted prior to publication]

## Energy Usage
CalBEM Energy Consumption - Large School | [11 empty] | Energy Consumption - SchoolLarge
Prototype | CZ | CalBEM Electricity EUI (KBTU/ft²) | CalBEM Gas EUI (KBTU/ft²) | CalBEM Total EUI (KBTU/ft²) | New Construction Electricity EUI (KBTU/ft²) | New Construction Gas EUI (KBTU/ft²) | New Construction Total EUI (KBTU/ft²) | National Average | Acceptable Range (25% Higher) | Acceptable Range (25% Lower) | National Average Acceptable EUI Range | Prototype | CZ | Total Floorspace (Thousand of ft²) | CEUS 2023 Electricity EUI (kBtu/ft²) | CEUS 2023 Gas EUI (kBtu/ft²) | CEUS 2023 Total EUI (kBtu/ft²) | Acceptable Range (25% Higher) | Acceptable Range (25% Lower) | CEUS 2022 Acceptable EUI Range
Large School | 1 | 17.464 | 51.3798 | 68.8438 | 14.68 | 42.85 | 57.53 | 84 | 105 | 63 | 42 | Large School | 1 | 7618.5337 | 32.3492 | 12.8481 | 55.3648 | 69.206 | 41.5236 | 27.6824
| 2 | 22.9853 | 40.3683 | 63.3536 | 19.5 | 33.43 | 52.93 | 84 | 105 | 63 | 42 |  | 2 | 11477.6706 | 15.4216 | 12.914 | 47.8933 | 59.8666 | 35.92 | 23.9466
| 3 | 19.6374 | 32.7779 | 52.4153 | 16.64 | 27.84 | 44.48 | 84 | 105 | 63 | 42 |  | 3 | 46411.8605 | 20.4796 | 12.7992 | 100.095 | 125.1187 | 75.0712 | 50.0475
| 4 | 25.4627 | 34.9818 | 60.4445 | 21.37 | 28.59 | 49.96 | 84 | 105 | 63 | 42 |  | 4 | 23032.968 | 21.4937 | 13.0198 | 106.6213 | 133.2767 | 79.966 | 53.3107
| 5 | 20.9255 | 27.155 | 48.0805 | 18.02 | 22.83 | 40.85 | 84 | 105 | 63 | 42 |  | 5 | 5978.4428 | 11.9981 | 11.5852 | 59.1493 | 73.9366 | 44.362 | 29.5746
| 6 | 25.2376 | 17.5004 | 42.7379 | 22.12 | 15.7 | 37.82 | 84 | 105 | 63 | 42 |  | 6 | 57755.9589 | 22.6073 | 9.9467 | 82.3475 | 102.9344 | 61.7606 | 41.1737
| 7 | 25.465 | 16.1341 | 41.5991 | 22.03 | 14.8 | 36.83 | 84 | 105 | 63 | 42 |  | 7 | 35149.9926 | 24.8484 | 6.97 | 88.5535 | 110.6918 | 66.4151 | 44.2767
| 8 | 30.1664 | 20.4537 | 50.6201 | 26.09 | 18.26 | 44.35 | 84 | 105 | 63 | 42 |  | 8 | 92353.4113 | 22.9353 | 8.8422 | 103.4418 | 129.3023 | 77.5814 | 51.7209
| 9 | 29.2412 | 23.194 | 52.4352 | 25.33 | 20.09 | 45.42 | 84 | 105 | 63 | 42 |  | 9 | 141795.4506 | 26.7973 | 10.0891 | 119.1513 | 148.9391 | 89.3635 | 59.5757
| 10 | 30.3513 | 22.2346 | 52.5859 | 26.84 | 19.77 | 46.61 | 84 | 105 | 63 | 42 |  | 10 | 92589.8669 | 22.4904 | 10.109 | 67.4191 | 84.2739 | 50.5643 | 33.7096
| 11 | 29.678 | 45.7066 | 75.3846 | 25.19 | 37.89 | 63.08 | 84 | 105 | 63 | 42 |  | 11 | 33810.4884 | 26.9287 | 8.7604 | 68.8393 | 86.0491 | 51.6294 | 34.4196
| 12 | 26.2972 | 37.9245 | 64.2217 | 22.48 | 32.29 | 54.77 | 84 | 105 | 63 | 42 |  | 12 | 108342.4341 | 31.7996 | 12.2303 | 85.5874 | 106.9842 | 64.1905 | 42.7937
| 13 | 31.2437 | 33.2806 | 64.5243 | 26.74 | 28.36 | 55.1 | 84 | 105 | 63 | 42 |  | 13 | 46676.8078 | 32.656 | 15.4735 | 57.7357 | 72.1696 | 43.3018 | 28.8678
| 14 | 30.2429 | 38.9003 | 69.1432 | 25.64 | 32.35 | 57.99 | 84 | 105 | 63 | 42 |  | 14 | 22787.7389 | 21.8072 | 11.4332 | 68.5025 | 85.6282 | 51.3769 | 34.2513
| 15 | 40.425 | 23.2542 | 63.6792 | 34.62 | 20.72 | 55.34 | 84 | 105 | 63 | 42 |  | 15 | 54746.0029 | 21.9543 | 10.4391 | 47.7153 | 59.6441 | 35.7864 | 23.8576
| 16 | 22.3793 | 68.0989 | 90.4782 | 18.98 | 57.3 | 76.28 | 84 | 105 | 63 | 42 |  | 16 | 85267.8904 | 27.0269 | 11.6529 | 67.5765 | 84.4706 | 50.6824 | 33.7882
Ref: CEUS 2022 Report
And by applying FZ-CZ multipliers for converting FZ data to CZ data

## Weights
% of Floor Area per CZ and Vintage Bin - Schools
Prototype | CZ | Vintage Bin
|  | Pre-1978 | 1978-1997 | 1998-2007 | 2008-2018 | Not available
Large School | 1 | 48.5% | 27.4% | 7.6% | 2.9% | 13.6% | 100%
| 2 | 85.8% | 7% | 3.8% | 1.4% | 2% | 100%
| 3 | 66.1% | 20.9% | 1.5% | 0.6% | 10.9% | 100%
| 4 | 68.2% | 17.9% | 0.9% | 0.6% | 12.4% | 100%
| 5 | 53.6% | 42.1% | 2.4% | 0.8% | 1.2% | 100.1%
| 6 | 65.7% | 13.9% | 10.3% | 4.4% | 5.8% | 100.1%
| 7 | 28.8% | 24.7% | 18.8% | 23.5% | 4.2% | 100%
| 8 | 66.6% | 12.5% | 10.3% | 3.6% | 7% | 100%
| 9 | 60.2% | 15.2% | 7.4% | 2% | 15.2% | 100%
| 10 | 32.7% | 20.1% | 31.7% | 11.1% | 4.4% | 100%
| 11 | 47.5% | 30.5% | 7.3% | 1.7% | 13.1% | 100.1%
| 12 | 44.7% | 31% | 9.6% | 2.8% | 11.8% | 99.9%
| 13 | 32.3% | 34.7% | 13.7% | 6.1% | 13.2% | 100%
| 14 | 52.3% | 17.9% | 14.3% | 9.8% | 5.7% | 100%
| 15 | 20.5% | 20.4% | 51% | 4.7% | 3.3% | 99.9%
| 16 | 44.7% | 23.5% | 12.7% | 9.4% | 9.8% | 100.1%
Statewide
Ref: CEUS 2022 dataset
Background Data [To be deleted prior to publication]

## PV (hidden)
PV - SchoolLarge
TBD

## EV Charger (hidden)
EV Charger - SchoolLarge
TBD
Background Data [To be deleted prior to publication]

## Data (hidden)
Space Function
Aging Eye/Low-vision (Corridor Area)
Aging Eye/Low-vision (Dining)
Aging Eye/Low-vision (Lobby, Main Entry)
Aging Eye/Low-vision (Lounge/Waiting Area)
Aging Eye/Low-vision (Multipurpose Room)
Aging Eye/Low-vision (Religious Worship Area)
Aging Eye/Low-vision (Restroom)
Aging Eye/Low-vision (Stairwell)
Audience Seating Area
Auditorium Area
Auto Repair / Maintenance Area
Barber, Beauty Salon, Spa Area
Civic Meeting Place Area
Classroom, Lecture, Training, Vocational Areas
Concourse and Atria Area
Convention, Conference, Multipurpose and Meeting Area
Copy Room
Corridor Area
Dining Area (Bar/Lounge and Fine Dining)
Dining Area (Cafeteria/Fast Food)
Dining Area (Family and Leisure)
Electrical, Mechanical, Telephone Rooms
Exercise/Fitness Center and Gymnasium Areas
Financial Transaction Area
Healthcare Facility and Hospitals (Exam/Treatment Room)
Healthcare Facility and Hospitals (Imaging Room)
Healthcare Facility and Hospitals (Medical Supply Room)
Healthcare Facility and Hospitals (Nursery)
Healthcare Facility and Hospitals (Nurse's Station)
Healthcare Facility and Hospitals (Operating Room)
Healthcare Facility and Hospitals (Patient Room)
Healthcare Facility and Hospitals (Physical Therapy Room)
Healthcare Facility and Hospitals (Recovery Room)
Hotel Function Area
Kitchen/Food Preparation Area
Kitchenette or Residential Kitchen
Laboratory, Scientific
Laundry Area
Library (Reading Area)
Library (Stacks Area)
Lobby, Main Entry
Locker Room
Lounge, Breakroom, or Waiting Area
Manufacturing, Commercial & Industrial Work Area (Low Bay)
Manufacturing, Commercial & Industrial Work Area (High Bay)
Manufacturing, Commercial & Industrial Work Area (Precision)
Museum Area (Exhibition/Display)
Museum Area (Restoration Room)
Office Area (>250 square feet)
Office Area (<250 square feet)
Parking Garage Area (Parking Zone and Ramps)
Parking Garage Area (Daylight Adaptation Zones) (Note 2)
Pharmacy Area
Retail Sales Area (Grocery Sales)
Retail Sales Area (Retail Merchandise Sales)
Retail Sales Area (Fitting Room)
Religious Worship Area
Restrooms
Stairwell
Storage, Commercial/Industrial (Warehouse)
Storage, Commercial/Industrial (Refrigerated)
Storage, Commercial/Industrial (Shipping & Handling)
Storage (General)
Sports Arena - Playing Area (> 5,000 Spectators)
Sports Arena - Playing Area (2,000 - 5,000 Spectators)
Sports Arena - Playing Area (< 2,000 Spectators)
Sports Arena - Playing Area (Recreational)
Theater Area (Motion Picture)
Theater Area (Performance)
Transportation Function (Baggage Area)
Transportation Function (Ticketing Area)
Videoconferencing Studio
High-Rise Residential Living Spaces
Hotel/Motel Guest Room
All other
Attic
Reception Area
Elevator