## Notes
Data Sources
Dataset |  | DSA Drawings for relocatable schools
| Berkeley Lab article | https://www2.lbl.gov/Science-Articles/Archive/EETD-portable-classrooms.html
| California Portable Classroom Study | https://ww2.arb.ca.gov/sites/default/files/classic/research/apr/reports/l3006.pdf
| California Legislature Environmental Health Condions in California's Portable Classrooms | https://ww2.arb.ca.gov/sites/default/files/2020-05/pcs_v3_es_03-23-04.pdf
Codes | Title 24, part 6, referred to as T24 (1984, 2001, 2007, 2013, 2016, 2022, 2025)
ASHRAE 90.1 (2022)
CFR Title 10 (2008, 2010, 2025)
ACM 2022
| T24 2022 - Appendix 5.4A and Appendix 5.4B | https://www.energy.ca.gov/publications/2022/2022-nonresidential-and-multifamily-alternative-calculation-method-reference
| 2022 Reduced infiltration CASE report | https://title24stakeholders.com/wp-content/uploads/2020/10/2022-T24-Final-CASE-Report_Reduce-Infiltration.pdf
| 2019 Outdoor Lighting CASE Report | https://title24stakeholders.com/wp-content/uploads/2016/10/T24-2019-CASE-Study-Results-Report-Outdoor-Sources_Final_with-Attachments.pdf
| 2019 High Efficiency Fume Hoods in Laboratory Spaces CASE Report | https://title24stakeholders.com/wp-content/uploads/2017/09/2019-T24-CASE-Report_Fume-Hoods_Final_September-2017.pdf?
| PNNL 20405, 2010 | file:///N:/Prj_SUS/2023/S23668%20SCE%20CA%20Prototypes%20Development/Technical/NR/0_Input%20data/Lighting/PNNL-20405.pdf
Other | Air leakage Memo, NORESCO, 2025 | Infiltration_rate_report_14May2025-Short-Version.docx
| BARD Engineering Specification Guide for SPVHP | BARD Engineering Specification Guide for SPVHP
Construction Rate
Notes

## Prototype
NORESCO, Updated November 2025
SchoolRelocatable
Characteristic | Value | Data Sources
Building Type | Relocatable School
Building Category | Nonresidential
Vintages | 4 Vintages: Pre-1978, 1978-1997,1998-2007, 2008-2018 New Construction (2019+) | Based on the vintage bin analysis | NonRes-Vintage bins-Draft Report-30Nov2023-Final.docx
Shape |  | The analysis uses prototype geometry originally developed by CEC.
Total Floor Area (ft²) | 1920.19 | Same as CEC
Aspect Ratio | 1.6667 | Same as CEC
Number of Floors | 1 | Same as CEC
Roof type | Flat | Same as CEC
WWR | 5.15% | Same as CEC
Shading Geometry | No Shades | Same as CEC
Floor to floor height (feet) | 12 ft | Same as CEC
Floor to ceiling height (feet) | 12 ft | Same as CEC
Glazing sill height (feet) | 2.9 ft | Same as CEC
Above grade wall area (ft²) | 1536.15
Gross wall area (ft²) | 1920.15
Roof area (ft²) | 960.09
Underground Gross Wall Area (ft²) | 384

## Zones
Proposed Layout - SchoolRelocatable
Space Type | Space/Thermal Zone | HVAC System Name/AHU Name | Schedule Category | Conditioned (Y/N) | Area Fraction | Area (ft²) | Volume (ft³) | Multipliers | Number of People | People (Persons/1,000 ft²) [T24, 2025,Table 120.1-A]
Classroom, Lecture, Training, Vocational Areas | Classroom | BaseAirSys5 | Classroom | Y | 50% | 960 | 11521.69 | 1 | 48 | 50
Unoccupied-Exclude from Gross Floor Area | Crawlspace |  |  | N | 50% | 960 | 2884 | 1
Total (2 Space types) | Total (2 spaces) | Total ( 1 HVAC zone) | Total (1 Schedule categories) | Total (1 Conditioned zones) | 100% | 1920 | 14405.69 |  | 48 | 50
N

## HVAC System
HVAC system - SchoolRelocatable
Vintage | Zones | Heating | Cooling | Air Distribution | Other System | Source | Note
Existing | Classroom, Lecture, Training, Vocational Areas | SPVHP | DX Coil | CAV | Economizer* Fix Dry bulb; integrated; High DB Temperature Lockout: 75 °F | ACM 2025 | System 3b
New Construction | Classroom, Lecture, Training, Vocational Areas | SPVHP | DX Coil | CAV | Economizer* Fix Dry bulb; integrated; High DB Temperature Lockout: 75 °F | ACM 2025 | System 3b
Efficiency of HVAC system
Vintage | Upgrade/Installed year | Heating DX | Supplumentary Heating Coil | Cooling DX | Source |  | Note
Pre 1978 | 2008 | COP = 3 | Efficiency: 100% (Electric) | EER = 9.0 | 10 CFR 431.97, Table 10 to paragraph (e)(2): SPVHP <65,000 Btu/h → EER 9.0, COP 3.0 (federal standard effective Jan 1, 2010; used here for legacy/vintage modeling consistency) |  | System 3b
1978-1997
1998-2007
2008-2018 | 2013 | COP = 3 | Efficiency: 100% (Electric) | EER = 9.0 | 10 CFR 431.97, Table 10 to paragraph (e)(2): SPVHP <65,000 Btu/h → EER 9.0, COP 3.0 (still governing in 2013; later update came in 2019)
New Construction | 2025 | COP = 3.3 | Efficiency: 100% (Electric) | EER = 11.0 | CEC 2025 Space-Conditioning Efficiency Tables, Table 5 (row: SPVHP <65,000 Btu/h → EER 11.0, COP 3.3, test AHRI 390). The table cites 10 CFR 431 Subpart F as the federal basis |  | System 3b
Fan power
Vintage | Approach | System | Total Static Pressure (TSP) | Fan Efficiency | Fan Motor and Drive Efficiency | W/cfm | Note
Existing | ACM 2025 | CAV | 1.7445 | 0.65 | 0.9 | 0.35 | Engineering Judgment
Brake horse power (bhp)=(Supply cfm*TSP in w.c.)/(6356*Fan efficiency)
Fan power (w/cfm) = bhp/motor and drive efficiency *746
New Construction | ACM 2025 | CAV | 1.7445 | 0.65 | 0.9 | 0.35 | Engineering Judgment
* 0.9 is an average fan efficiency according to ACM 2025, Table 14
Fan total eff (E+ input) = 0.65 x Motor_eff
TSP (E+ input) in w.c. = Motor_eff/746 x (6356 x Fan_eff) x W/cfm
Fan_eff=0.65
Background Data [To be deleted prior to publication]
BARD Engineering Specification Guide for SPVHP

## Envelope
Envelope - SchoolRelocatable
Element | Prototype | Assembly Type | Construction | Thermal Properties | Vintage | Selected T24 | Note | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
External Wall | SchoolRelocatable | ExtWall_MetalFramed_NonRes | Metal-framed walls + insulation + Gypsum board | U-factor IP | Pre 1978 | N/A | ASHRAE 90.1, 2022, Table A3.3.3.1, 3.5", R-0 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292
[5 empty] | 1978-1997 | 1986 | Heat Capacity was considered 10.0-14.99 (Btu/F-ft²) | 0.15083 | 0.15748 | 0.15748 | 0.14368 | 0.14368 | 0.21645 | 0.21645 | 0.21645 | 0.21645 | 0.21645 | 0.18622 | 0.18622 | 0.18622 | 0.15873 | 0.15873 | 0.15083
[5 empty] | 1998-2007 | 2001 | TABLE 1-H-NonRes Bldgs | 0.182 | 0.182 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182
[5 empty] | 2008-2018 | 2013 | TABLE 140.3-B-NonRes Bldgs | 0.098 | 0.062 | 0.082 | 0.062 | 0.062 | 0.098 | 0.098 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062
[5 empty] | 2019+ | 2025 | TABLE 140.3-B-NonRes Bldgs | 0.06 | 0.055 | 0.071 | 0.055 | 0.055 | 0.06 | 0.06 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055
Roof | SchoolRelocatable | FlatRoof_WoodFramedAndOther_NonRes | Built-up Roof steel truss + cavity insulation + plywood deck + above deck insulation + membrane + coverboard | U-value IP | Pre 1978 | N/A | Considering 30 years for roof/ insulation replacement. | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 1978-1997 | 1986 |  | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 1998-2007 | 2001 | Table 1-H | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.049 | 0.039 | 0.039 | 0.039 | 0.049 | 0.075 | 0.067 | 0.067 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.047 | 0.047 | 0.047 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028
Windows_Nonrs | SchoolRelocatable | OperableWindow_NonRes | CBECS 2018 shows that ~58% of Large Hotels that were built before 2000 are single pane | U-factor IP | Pre 1978 | N/A | ASHRAE Handbook of Fundamentals for single pane & T24, 2013 for double pane (58%-42%) | 0.6582 | 0.6582 | 0.7926 | 0.7926 | 0.7926 | 0.7926 | 0.7926 | 0.7926 | 0.7926 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582
[5 empty] | 1978-1997 | N/A |  | 0.6582 | 0.6582 | 0.7926 | 0.7926 | 0.7926 | 0.7926 | 0.7926 | 0.7926 | 0.7926 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582
|  |  | Double pane |  | 1998-2007 | 2001 | Table1-H | 0.49 | 0.49 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46
| SchoolRelocatable |  | CBECS 2018 shows that ~58% of Large Hotels that were built before 2000 are single pane | SHGC | Pre 1978 | N/A | ASHRAE Handbook of Fundamentals for single pane & T24, 2013 for double pane (58%-42%) | 0.9192 | 0.9192 | 1.0536 | 1.0536 | 1.0536 | 1.0536 | 1.0536 | 1.0536 | 1.0536 | 0.9192 | 0.9192 | 0.9192 | 0.9192 | 0.9192 | 0.9192 | 0.9192
[5 empty] | 1978-1997 | N/A |  | 0.9192 | 0.9192 | 1.0536 | 1.0536 | 1.0536 | 1.0536 | 1.0536 | 1.0536 | 1.0536 | 0.9192 | 0.9192 | 0.9192 | 0.9192 | 0.9192 | 0.9192 | 0.9192
|  |  | Double pane |  | 1998-2007 | 2001 | Table 1-H (based on non north with WWR 30-40% ) | 0.45 | 0.39 | 0.51 | 0.51 | 0.51 | 0.475 | 0.475 | 0.475 | 0.475 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.45
[5 empty] | 2008-2018 | 2013 | Table 140.3-B (100% fixed, 0% operable) | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22
[5 empty] | 2019+ | 2025 | Table 140.3-B (100% fixed, 0% operable) | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22
* California Legislature Environmental Health Condions in California's Portable Classrooms
Infiltration
[5 empty] | Vintage | I_75 6-Sided Inifltration rate @ 75 pa | Note | I-design (cfm/ft²) (4-sided Infiltration rate at normal presure) (Design flow rate approach and Flow/Exterior Wall Area calulation method) | [15 empty] | 0.028 | 0.028
|  |  |  | Infiltration | Pre 1978 | 1.1 | 2022 CASE report (Table 38) | 0.308
[5 empty] | 1978-1997 | 1.1 | 2022 CASE report (Table 38) | 0.308
[5 empty] | 1998-2007 | 1.1 | 2022 CASE report (Table 38) | 0.308
[5 empty] | 2008-2018 | 1 | 2022 CASE report (Table 38) & T24, 2008-2016 (Table 140.3-B)--Air barrier is required in CZ 10-16 | 0.2818
[5 empty] | 2019+ | 0.6 | 2022 CASE report (Table 38) & T24, 2025 (Table 140.3-B)--Air barrier is required in all CZs | 0.168
Source: T24 air barrier requirements (all editions) and the standardized infiltration rate reported in the 2022 CASE report and Dodge 2023 data
|  |  |  | Air Lekage Memo: |  | Infiltration_rate_report_14May2025-Short-Version.docx

## Thermostat
Thermostat Setpoints - SchoolRelocatable
Setpoint | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16 | Source
School Heating Setpoint (F) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | T24 2022 - Appendix 5.4B
School Heating Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
School Cooling Setpoint (F) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | T24 2022 - Appendix 5.4B
School Cooling Setback (F) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85

## Ventilation
Outdoor Airflow Rate - SchoolRelocatable
Space Type | Space/Thermal Zone | Number of People | Floor Area (ft²) | cfm/person [T24, 2025, Equation 120.1-F and Table 120.1-A] | cfm/ft² [T24, 2025, Equation 120.1-F and Table 120.1-A] | Required exhaust rate-CFM/ft²- [T24, 2025, Table 120.1-B – minimum exhaust rates] | Total cfm driven by people | Total cfm driven by area | Total cfm driven by exhaust | Total cfm | Notes
Classroom, Lecture, Training, Vocational Areas | Classroom | 48 | 960 | 15 | 0.15 |  | 720 | 144 | 0 | 720
Unoccupied-Exclude from Gross Floor Area | Crawlspace | 0 | 960 |  |  |  | 0 | 0 | 0 | 0
Total (2 Space types) | Total (2 spaces) | 48 | 1920 |  |  |  | 720 | 144 | 0 | 720

## Water Heater
Water Heater -SchoolRelocatable
Vintage | WH Type | Efficiency | Tank Volume (gal) | Tank Loss |  | Note
Existing | Electric | 1 | 2 | 0 | (Btu/hr)
New Construction | Electric | 1 | 2 | 0 | (%/hr) | Section 1605.1. Federal and State Standards for Federally-Regulated Appliances.
Peak Hot Water Consumption
Space Name | Baseline WH Type [T24, 2022, Appendix 5.4A , sheet: "2022 SpaceFuncData-Input"] | New Construction: Baseline WH Type ACM 2025 | Total Area (ft²) | Number of People | Hot Water Usage Specification (gal/hr per person) [T24, 2022, Appendix 5.4A , sheet: "2022 SpaceFuncData-Input"] | Peak Hot Water Usage (gal/hr) | Peak Hot Water Usage (gal/min)
Classroom | Electric |  | 960 | 48 | 0.18 | 8.64 | 0.144
Total |  |  | 960 | 48 | 0.18 | 8.64 | 0.144
Water Heater Capacity, Tank Capacity, and Tank Loss
WH Type | Peak Hot Water Usage (gal/hr) | Heat Output (Btu/hr) [ACM, 2025, 5.9.2: Rated capacity section] | WH Capacity (Btu/hr) [ACM, 2025, 5.9.2: Rated capacity section] | Required Energy Input (Btu/hr) | Storage Volume (gal) | Standby Loss | Unit | Off/On Cycle Loss Coefficient to Ambient Temp (Btu/h-F) | Source
Electric WH | 30 | 19890.48 | 19890.48 | 20296.4082 | 2 | 0 | %hr | 0 | Standby loss equation: Title 20, §1605.1 Table F-4 WH capacity equation: ACM, 2025, 5.9.2: Rated capacity section)
-
Total | 30 | 19890.48 | 19890.48 | 20296.4082 | 2 | 0 | %hr | 0
[5 empty] | Standby Loss for Existing | 0 | Btu/hr
Maximum flow rate (GPM) | 0.5 | CALGreen §5.303.3.4.1 (Title 24, Part 11, 2025)
Design supply temperature (F) | 135 | Ref: T24 2022 - Appendix 5.4B
Cold Water supply temperature (F) | 55 | Ref: ACM, 2025, 5.9.2: Rated capacity section
WH system factor | 0.6 | Ref: ACM, 2025, 5.9.2: Rated capacity section
Reheat multiplier | 0.4
* The 0.40 multiplier is a storage sizing factor used to account for the fact that the water heater doesn't need to store the full peak hour demand—it can reheat water during that time. This factor assumes that the heater will recover part of the hot water used during the peak hour, so only 40% of the peak hour demand needs to be stored at any given moment.
**For Gas Water Heater: UA(Btu/h-°F)​=Q˙​SL​ (Btu/h)/ΔT (∘F)​
Ambient temp | 68
Delta T | 67
** For Electric Water Heater: UA(Btu/h-°F)​= 0.0834 *SL​ (%/hr)*V gal
Background Data [To be deleted prior to publication]

## Interior Lights
Interior Lighting - SchoolRelocatable
Space Type | New Construction |  |  | Existing
| Lighting density (W/ft²) | Additional lighting power for porTable lighting (W/ft²) | Source | LPD (W/ft²) | Additional LPD for PorTable Lighting (W/ft²) | Source
Classroom, Lecture, Training, Vocational Areas | 0.6 |  | T24, 2025, Table 140.6 C (Area category method) | 1.2 |  | T24, 2016, Table 140.6 C (Area category method)
Unoccupied-Exclude from Gross Floor Area | 0 |  |  | 0

## Ext Lighting
Exterior Lighting - SchoolRelocatable
Motion Controlled Luminaires (W) | Non-motion Controlled Luminaires (W) | Total (W) | Source
200 | 307.8721 | 507.8721 | T24, 2022 & 2025 2019 Outdoor Lighting CASE report PNNL 90.1-2010 TSD
Exterior Lighting
Items (Assume LZ2) | Assumptions [2019 Outdoor Lighting CASE Report & PNNL 90.1-2010 TS] |  | Unit | Lighting Power Allowance [T24, 2025, Table 140.7-A & 140.7-B] | Unit | Exterior Lighting Power (W)
IWA (Initial Wattage Allowance) |  |  |  | 200 | (W) | 200
Parking area | 400 ft² for every parking space 1 parking space per 830 ft² of gross building area | 0 | (ft²) | 0.019 | (W/ft²) | 0
Building Entrance | 5 building entrance per PNNL Model (1 per 10,000 ft² footprint) | 0 | (count) | 15 | (W/ea) | 0
Hardscape Ornamental Light | 0.1 ft² per 1 ft² of gross building area for hardscape ornamental light | 96.0095 | (ft²) | 0.007 | (W/ft²) | 0.67207
Building façade | 0.1 W per 1 ft² of facade area Façade Area = Perimeter × 0.5 × max ( height and 30) (30 ft is the max height that is lit) * The 0.5 factor assumes that only half of the perimeter walls are lit. -Formula ia developed based on the 2019 Outdoor Lighting CASE report | 3072 | (ft²) | 0.1 | (W/ft²) | 307.2
Motion Controlled Luminaires (W) | [5 empty] | 200
Non-motion-controlled Luminaires | [5 empty] | 307.8721
Total | [5 empty] | 507.8721
Max Height (ft) | 12
Building footprint | 480.0475
Floors | 1
Perimeter(ft) | 128
Background Data [To be deleted prior to publication]
Total floor area (ft²) | 960.095

## Equipment
Equipment - SchoolRelocatable
Space Type | Plug load Power Density (W/ft²) | Gas Power Density (Btu/hr-ft²) | Refrigeration Power Density (W/ft²) | Source
Classroom, Lecture, Training, Vocational Areas | 0.8 | 0 | 0 | T24 2022 - Appendix 5.4A
Unoccupied-Exclude from Gross Floor Area | 0 | 0 | 0

## Schedules
Schedules - SchoolRelocatable
Zone | Schedule Category | Schedule | Source | Type | Hour
[5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
School Zones | Classroom | Occupancy | T24 2022 - Appendix 5.4B [School] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.75 | 0.9 | 0.9 | 0.8 | 0.8 | 0.8 | 0.8 | 0.45 | 0.15 | 0.05 | 0.15 | 0.2 | 0.2 | 0.1 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School Zones | Classroom | Lights | T24 2022 - Appendix 5.4B [School] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.6 | 0.65 | 0.65 | 0.65 | 0.55 | 0.55 | 0.55 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.3 | 0.05 | 0.05
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
School Zones | Classroom | ElecEquipment | T24 2022 - Appendix 5.4B [School] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.85 | 0.95 | 0.95 | 0.95 | 0.8 | 0.8 | 0.8 | 0.7 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.3 | 0.05 | 0.05
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
School Zones | Classroom | ServiceHotWater | T24 2022 - Appendix 5.4B [School] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09
|  |  |  | Saturday | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
|  |  |  | Sunday | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
School Zones | Classroom | GasEquipment | T24 2022 - Appendix 5.4B [School] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.75 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School Zones | Classroom | Refrigeration | T24 2022 - Appendix 5.4B [School] | Weekday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Saturday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Sunday | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
School Zones | Classroom | HVACAvail | T24 2022 - Appendix 5.4B [School] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School Zones | Classroom | HtgSetpt | T24 2022 - Appendix 5.4B | Weekday | 60 | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 60 | 60
|  |  |  | Saturday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  |  | Sunday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
School Zones | Classroom | ClgSetpt | T24 2022 - Appendix 5.4B | Weekday | 85 | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 85 | 85
|  |  |  | Saturday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
|  |  |  | Sunday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
School Zones | Classroom | Infiltration | T24 2022 - Appendix 5.4B | Weekday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
Other
| Building | ExtLightingNonMotionCtrl |  | Weekday | bar: Hour 1 to Hour 24
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
| Building | ExtLightingMotionCtrl |  | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Classroom | Building | MeetingPeopleActivityLevel | Based on Activilty level schedules in CEC Prototypes | Weekday | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2
|  |  |  | Saturday | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2
|  |  |  | Sunday | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2 | 117.2
Background Data [To be deleted prior to publication]

## Energy Usage
CalBEM Energy Consumption - Relocatable School | [11 empty] | Energy Consumption - SchoolRelocatable
Prototype | CZ | CalBEM Electricity EUI (KBTU/ft²) | CalBEM Gas EUI (KBTU/ft²) | CalBEM Total EUI (KBTU/ft²) | New Construction Electricity EUI (KBTU/ft²) | New Construction Gas EUI (KBTU/ft²) | New Construction Total EUI (KBTU/ft²) | National Average | Acceptable Range (25% Higher) | Acceptable Range (25% Lower) | National Average Acceptable EUI Range | Prototype | CZ | Total Floorspace (Thousand of ft²) | CEUS 2023 Electricity EUI (kBtu/ft²) | CEUS 2023 Gas EUI (kBtu/ft²) | CEUS 2023 Total EUI (kBtu/ft²) | Acceptable Range (25% Higher) | Acceptable Range (25% Lower) | CEUS 2022 Acceptable EUI Range
Relocatable School | 1 | 175.8366 | 0 | 175.8366 | 118.81 | 0 | 118.81 | 51.3 | 64.125 | 38.475 | 25.65 | Relocatable School | 1 | 7618.5337 | 32.3492 | 12.8481 | 45.1973 | 56.4966 | 33.898 | 22.5987
| 2 | 141.9838 | 0 | 141.9838 | 98.83 | 0 | 98.83 | 51.3 | 64.125 | 38.475 | 25.65 |  | 2 | 11477.6706 | 15.4216 | 12.914 | 28.3356 | 35.4195 | 21.2517 | 14.1678
| 3 | 107.3558 | 0 | 107.3558 | 78.09 | 0 | 78.09 | 51.3 | 64.125 | 38.475 | 25.65 |  | 3 | 46411.8605 | 20.4796 | 12.7992 | 33.2788 | 41.5986 | 24.9591 | 16.6394
| 4 | 148.8186 | 0 | 148.8186 | 102.27 | 0 | 102.27 | 51.3 | 64.125 | 38.475 | 25.65 |  | 4 | 23032.968 | 21.4937 | 13.0198 | 34.5135 | 43.1419 | 25.8851 | 17.2567
| 5 | 107.8165 | 0 | 107.8165 | 77.29 | 0 | 77.29 | 51.3 | 64.125 | 38.475 | 25.65 |  | 5 | 5978.4428 | 11.9981 | 11.5852 | 23.5833 | 29.4791 | 17.6874 | 11.7916
| 6 | 73.3319 | 0 | 73.3319 | 54.61 | 0 | 54.61 | 51.3 | 64.125 | 38.475 | 25.65 |  | 6 | 57755.9589 | 22.6073 | 9.9467 | 32.5541 | 40.6926 | 24.4156 | 16.277
| 7 | 71.2575 | 0 | 71.2575 | 52.11 | 0 | 52.11 | 51.3 | 64.125 | 38.475 | 25.65 |  | 7 | 35149.9926 | 24.8484 | 6.97 | 31.8184 | 39.773 | 23.8638 | 15.9092
| 8 | 87.2936 | 0 | 87.2936 | 64.68 | 0 | 64.68 | 51.3 | 64.125 | 38.475 | 25.65 |  | 8 | 92353.4113 | 22.9353 | 8.8422 | 31.7775 | 39.7219 | 23.8331 | 15.8888
| 9 | 94.236 | 0 | 94.236 | 69.05 | 0 | 69.05 | 51.3 | 64.125 | 38.475 | 25.65 |  | 9 | 141795.4506 | 26.7973 | 10.0891 | 36.8864 | 46.108 | 27.6648 | 18.4432
| 10 | 100.0645 | 0 | 100.0645 | 74.25 | 0 | 74.25 | 51.3 | 64.125 | 38.475 | 25.65 |  | 10 | 92589.8669 | 22.4904 | 10.109 | 32.5994 | 40.7492 | 24.4495 | 16.2997
| 11 | 157.4074 | 0 | 157.4074 | 111.19 | 0 | 111.19 | 51.3 | 64.125 | 38.475 | 25.65 |  | 11 | 33810.4884 | 26.9287 | 8.7604 | 35.6891 | 44.6114 | 26.7668 | 17.8445
| 12 | 136.2184 | 0 | 136.2184 | 97.98 | 0 | 97.98 | 51.3 | 64.125 | 38.475 | 25.65 |  | 12 | 108342.4341 | 31.7996 | 12.2303 | 44.0299 | 55.0374 | 33.0224 | 22.0149
| 13 | 133.0229 | 0 | 133.0229 | 97.21 | 0 | 97.21 | 51.3 | 64.125 | 38.475 | 25.65 |  | 13 | 46676.8078 | 32.656 | 15.4735 | 48.1296 | 60.162 | 36.0972 | 24.0648
| 14 | 167.7474 | 0 | 167.7474 | 118.15 | 0 | 118.15 | 51.3 | 64.125 | 38.475 | 25.65 |  | 14 | 22787.7389 | 21.8072 | 11.4332 | 33.2403 | 41.5504 | 24.9303 | 16.6202
| 15 | 140.247 | 0 | 140.247 | 97.19 | 0 | 97.19 | 51.3 | 64.125 | 38.475 | 25.65 |  | 15 | 54746.0029 | 21.9543 | 10.4391 | 32.3934 | 40.4918 | 24.2951 | 16.1967
| 16 | 237.7829 | 0 | 237.7829 | 167.29 | 0 | 167.29 | 51.3 | 64.125 | 38.475 | 25.65 |  | 16 | 85267.8904 | 27.0269 | 11.6529 | 38.6798 | 48.3498 | 29.0099 | 19.3399
Ref: CEUS 2022 Report
And by applying FZ-CZ multipliers for converting FZ data to CZ data

## Weights
% of Floor Area per CZ and Vintage Bin - Schools
Prototype | CZ | Vintage Bin
|  | Pre-1978 | 1978-1997 | 1998-2007 | 2008-2018 | Not available
Relocatable School | 1 | 48.5% | 27.4% | 7.6% | 2.9% | 13.6% | 100%
| 2 | 85.8% | 7% | 3.8% | 1.4% | 2% | 100%
| 3 | 66.1% | 20.9% | 1.5% | 0.6% | 10.9% | 100%
| 4 | 68.2% | 17.9% | 0.9% | 0.6% | 12.4% | 100%
| 5 | 53.6% | 42.1% | 2.4% | 0.8% | 1.2% | 100.1%
| 6 | 65.7% | 13.9% | 10.3% | 4.4% | 5.8% | 100.1%
| 7 | 28.8% | 24.7% | 18.8% | 23.5% | 4.2% | 100%
| 8 | 66.6% | 12.5% | 10.3% | 3.6% | 7% | 100%
| 9 | 60.2% | 15.2% | 7.4% | 2% | 15.2% | 100%
| 10 | 32.7% | 20.1% | 31.7% | 11.1% | 4.4% | 100%
| 11 | 47.5% | 30.5% | 7.3% | 1.7% | 13.1% | 100.1%
| 12 | 44.7% | 31% | 9.6% | 2.8% | 11.8% | 99.9%
| 13 | 32.3% | 34.7% | 13.7% | 6.1% | 13.2% | 100%
| 14 | 52.3% | 17.9% | 14.3% | 9.8% | 5.7% | 100%
| 15 | 20.5% | 20.4% | 51% | 4.7% | 3.3% | 99.9%
| 16 | 44.7% | 23.5% | 12.7% | 9.4% | 9.8% | 100.1%
Statewide
Ref: CEUS 2022 dataset
Background Data [To be deleted prior to publication]

## PV (hidden)
PV - SchoolRelocatable
TBD

## EV Charger (hidden)
EV Charger - SchoolRelocatable
TBD
Background Data [To be deleted prior to publication]

## Data (hidden)
Space Function
Aging Eye/Low-vision (Corridor Area)
Aging Eye/Low-vision (Dining)
Aging Eye/Low-vision (Lobby, Main Entry)
Aging Eye/Low-vision (Lounge/Waiting Area)
Aging Eye/Low-vision (Multipurpose Room)
Aging Eye/Low-vision (Religious Worship Area)
Aging Eye/Low-vision (Restroom)
Aging Eye/Low-vision (Stairwell)
Audience Seating Area
Auditorium Area
Auto Repair / Maintenance Area
Barber, Beauty Salon, Spa Area
Civic Meeting Place Area
Classroom, Lecture, Training, Vocational Areas
Concourse and Atria Area
Convention, Conference, Multipurpose and Meeting Area
Copy Room
Corridor Area
Dining Area (Bar/Lounge and Fine Dining)
Dining Area (Cafeteria/Fast Food)
Dining Area (Family and Leisure)
Electrical, Mechanical, Telephone Rooms
Exercise/Fitness Center and Gymnasium Areas
Financial Transaction Area
Healthcare Facility and Hospitals (Exam/Treatment Room)
Healthcare Facility and Hospitals (Imaging Room)
Healthcare Facility and Hospitals (Medical Supply Room)
Healthcare Facility and Hospitals (Nursery)
Healthcare Facility and Hospitals (Nurse's Station)
Healthcare Facility and Hospitals (Operating Room)
Healthcare Facility and Hospitals (Patient Room)
Healthcare Facility and Hospitals (Physical Therapy Room)
Healthcare Facility and Hospitals (Recovery Room)
Hotel Function Area
Kitchen/Food Preparation Area
Kitchenette or Residential Kitchen
Laboratory, Scientific
Laundry Area
Library (Reading Area)
Library (Stacks Area)
Lobby, Main Entry
Locker Room
Lounge, Breakroom, or Waiting Area
Manufacturing, Commercial & Industrial Work Area (Low Bay)
Manufacturing, Commercial & Industrial Work Area (High Bay)
Manufacturing, Commercial & Industrial Work Area (Precision)
Museum Area (Exhibition/Display)
Museum Area (Restoration Room)
Office Area (>250 square feet)
Office Area (<250 square feet)
Parking Garage Area (Parking Zone and Ramps)
Parking Garage Area (Daylight Adaptation Zones) (Note 2)
Pharmacy Area
Retail Sales Area (Grocery Sales)
Retail Sales Area (Retail Merchandise Sales)
Retail Sales Area (Fitting Room)
Religious Worship Area
Restrooms
Stairwell
Storage, Commercial/Industrial (Warehouse)
Storage, Commercial/Industrial (Refrigerated)
Storage, Commercial/Industrial (Shipping & Handling)
Storage (General)
Sports Arena - Playing Area (> 5,000 Spectators)
Sports Arena - Playing Area (2,000 - 5,000 Spectators)
Sports Arena - Playing Area (< 2,000 Spectators)
Sports Arena - Playing Area (Recreational)
Theater Area (Motion Picture)
Theater Area (Performance)
Transportation Function (Baggage Area)
Transportation Function (Ticketing Area)
Videoconferencing Studio
High-Rise Residential Living Spaces
Hotel/Motel Guest Room
All other
Attic
Reception Area
Elevator
Unoccupied-Exclude from Gross Floor Area