## Notes
Data Sources
Dataset | Dodge 2023
| Commercial End-Use Survey (CEUS) 2022 | https://www.energy.ca.gov/publications/2023/2022-california-commercial-end-use-survey-ceus-final-report
| Commercial Buildings Energy Consumption Survey (CBECS) 2018 | https://www.eia.gov/consumption/commercial/data/2018/index.php?view=microdata
| Comstock 2023 | https://data.openei.org/s3_viewer?bucket=oedi-data-lake&prefix=nrel-pds-building-stock%2Fend-use-load-profiles-for-us-building-stock%2F2023%2Fcomstock_amy2018_release_2%2Fmetadata_and_annual_results%2Fby_state%2Fstate%3DCA%2F
Prototype | California Energy Commission (CEC) Medium Retail prototype (CBECC 2022.3.1) | https://bees.noresco.com/software2022.html
| Pacific Northwest National Laboratory (PNNL) Standalone Retail prototypes (90.1-2022) | https://www.energycodes.gov/prototype-building-models#Commercial
| Database for Energy Efficient Resources (DEER) Retail prototypes (June 2023) | https://github.com/sound-data/DEER-Prototypes-EnergyPlus
Codes | Title 24, part 6, referred to as T24 (1984, 1992,1998, 2001, 2005, 2008, 2013, 2016,2019, 2022, 2025) | https://www.energy.ca.gov/publications/2025/2025-building-energy-efficiency-standards-residential-and-nonresidential | 2025
|  | https://codes.iccsafe.org/codes/united-states/california | 2010+
| American Society of Heating, Refrigerating and Air-Conditioning Engineers (ASHRAE) 90.1 (2022) | https://www.ashrae.org/technical-resources/standards-and-guidelines/read-only-versions-of-ashrae-standards
| Code of Federal Regulations (CFR) Title 10 ( 2010) | https://www.govinfo.gov/content/pkg/FR-2009-03-23/pdf/FR-2009-03-23.pdf
| CFR Title 10 ( 2024) | https://www.govinfo.gov/content/pkg/CFR-2024-title10-vol3/pdf/CFR-2024-title10-vol3-part431-subpartF.pdf
Others | Alternative Calculation Method (ACM) (2022) | https://www.energy.ca.gov/publications/2022/2022-nonresidential-and-multifamily-alternative-calculation-method-reference
| ACM (2025) | https://www.energy.ca.gov/publications/2025/2025-nonresidential-and-multifamily-alternative-calculation-method-reference
| Nonres ACM 2022, Appendix 5.4A and Appendix 5.4B | https://www.energy.ca.gov/publications/2022/2022-nonresidential-and-multifamily-alternative-calculation-method-reference
| 2022 Reduced infiltration Codes and Standards Enhancement (CASE) report | https://title24stakeholders.com/wp-content/uploads/2020/10/2022-T24-Final-CASE-Report_Reduce-Infiltration.pdf
| 2019 Outdoor Lighting CASE Report | https://title24stakeholders.com/wp-content/uploads/2016/10/T24-2019-CASE-Study-Results-Report-Outdoor-Sources_Final_with-Attachments.pdf
| PNNL 20405, 2011 | https://www.pnnl.gov/main/publications/external/technical_reports/PNNL-20405.pdf
| Air leakage Memo, NORESCO, 2025 | Infiltration_rate_report_14May2025-Short-Version.docx
| Yousefi, F., Athalye, R., (2025), "Determining Vintage Bins for Prototype Development: An Analysis of California Commercial Buildings," ASHRAE Annual Conference | https://www.thefreelibrary.com/Determining+Vintage+Bins+for+Prototype+Development%3a+An+Analysis+of...-a0879271125
| Retail Building Guide for Entrance Energy Efficiency Measures (2012) | https://www.osti.gov/servlets/purl/1037934
| Proposed Updates to Equipment Power Densities and Building Schedules for the 2028 Energy Code, referred to as "Plug load and schedules project with CEC, 2025" (Docket Number =25-BSTD-03 & TN=265693) | https://efiling.energy.ca.gov/GetDocument.aspx?tn=265693&DocumentContentId=102545
| ENERGY STAR certified commercial water heaters | https://www.energystar.gov/productfinder/product/certified-commercial-water-heaters/results?fuel_filter=Gas&markets_filter=United+States
| Grainger gas tank water heaters (sizes below commercial, e.g. 30–75 kBtu/h) | https://www.grainger.com/category/plumbing/water-heaters/gas-tank-water-heaters
| Grainger electric tank water heaters | https://www.grainger.com/category/plumbing/water-heaters/electric-tank-water-heaters
Construction Rate
Source:Dodge Construction Data, 2023 ( NEW Stores built after 1967) (STC refers to building types in Dodge terminology).
Notes
This prototype represents an open-format general merchandise "big box" typology for retail up to approximately 50,000 ft². It is intended to capture the overall building and energy-use characteristics of non-grocery general merchandise retailers, such as CVS, REI, Tj Max, Home Goods, Ross, Staples, Petco, Marshall, Mattress Firm, Old Navy, and other similar retail shops. This prototype is distinct from grocery stores, warehouse clubs, strip malls, and malls, as their refrigeration, plug/process load, lightings, occupancy, schedules, and other energy-use characteristics can differ substantially from general merchandise retail.

## Prototype
NORESCO, Updated September 2026
RetailMedium
Characteristic | Value | Data Sources
Building Type | General Merchandise Retail
Building Category | Nonresidential
Version | v2-0
Vintages | 4 Vintages: Pre-1978 , 1978-1997 ,1998-2007 , 2008-2018 New Construction (2019+) | Based on the vintage bin analysis. A summary of the findings is presented in the following paper, with a link provided in the Notes tab: Yousefi, F., Athalye, R. (2025). “Determining Vintage Bins for Prototype Development: An Analysis of California Commercial Buildings.” ASHRAE Annual Conference.
Shape |  | Typical medium-sized box retail shop
Total Floor Area (ft²) | 24,692 (178 ft x 139 ft) | Assumption: same as the CBECC RetailMedium prototypes. According to Dodge 2023 construction data, the average floor area of stores between 10,000 ft² and 50,000 ft² in California is approximately 20,414 ft²
Aspect Ratio | 1.28 | Assumption; same as PNNL Retail_Standalone and CBECC RetailMedium prototypes
Number of Floors | 1 | Typical medium-sized box retail shop
Roof type | Flat | Typical medium-sized box retail shop
WWR_Whole Building | 7.1% | Close to the General Merchandise 50% Energy Savings Technical Support Document (PNNL, 2009) which reports a 6.2% whole‑building WWR and 22% front‑façade WWR based on analysis of the 2003 CBECS retail dataset
WWR_South Facade | 25.4%
Shading Geometry | None | Assumption; same as PNNL Retail_Standalone and CBECC RetailMedium prototypes
Floor to floor height (feet) | N/A
Floor to ceiling height (feet) | 20 | Assumption; same as PNNL Retail_Standalone and CBECC RetailMedium prototypes
Glazing sill height (feet) | 5 ft (top of the window is 8.73 ft high with 3.74 ft high glass) | Assumption; same as PNNL Retail_Standalone and CBECC RetailMedium prototypes
Skylight-to-Roof-Ratio (SRR) | 2.07% | Assumption; same as PNNL Retail_Standalone and CBECC RetailMedium prototypes
Background Data
Existing Retail Prototypes
Large size prototype | CEC: Retail_Large | CPUC: Retail_Multistory Large (Rt3) | CPUC: Retail_Single-Story Large (RtL)
Geometry
Total floor area (ft²) | 240000 | 120000 | 130502
Medium size prototype | CEC: Retail_Medium | PNNL : Retail_Standalone | PNNL: Retail_Stripmall | CPUC: Retail_Grocery
Geometry | zoning same as PNNL Stand alone with more skylight
Total floor area (ft²) | 24692 | 24692 | 22500 | 49997
Small size prototype | CEC: Retail_Stripmall (Mixed use) | CPUC: Retail_Small (RtS)
Geometry
Total floor area (ft²) | 9375 | 8001

## Zones
Proposed Layout - RetailMedium | [14 empty] | Spaces and Zoning layout
Building | Space/Thermal Zone | Space Type [Primarily from: T24, 2022 Appendix 5.4A] - See Notes column | HVAC System Name (NC) | HVAC System Name (Existing) | Schedule Category | Conditioned (Y/N) | Area Fraction* | Area (ft²) | Volume (ft³) | Multipliers | Number of People | People (Persons/1,000 ft²) [T24, 2025,Table 120.1-A] | Notes
RetailMedium | Core_Retail | Retail Sales Area (Retail Merchandise Sales) | PSZAC_Core1, PSZAC_Core2, PSZAC_Core3, PSZAC_Core4 | SZVAVHP_Core1, SZVAVHP_Core2, SZVAVHP_Core3, SZVAVHP_Core4 | Retail | Y | 69.8% | 17235.016 | 344700.32 | 1 | 292.9953 | 17
RetailMedium | Point_of_Sale | Retail Sales Area (Retail Merchandise Sales) | PSZAC_Point_Of_Sale | PSZVAVHP_Point_Of_Sale | Retail | Y | 6.6% | 1629.672 | 32593.44 | 1 | 27.7044 | 17
RetailMedium | Front_Retail | Retail Sales Area (Retail Merchandise Sales) | PSZAC_Front_Retail | SZVAVHP_Front_Retail | Retail | Y | 6.6% | 1629.672 | 32593.44 | 1 | 27.7044 | 17
RetailMedium | Front_Entry | Corridor Area |  |  | Retail | N | 0.5% | 123.46 | 2469.2 | 1 | 0.6173 | 5
RetailMedium | Loading_Dock | Storage, Commercial/Industrial (Shipping & Handling) | PSZAC_Storage | SZVAVHP_Storage | Ancillary | Y | 2.4% | 592.608 | 11852.16 | 1 | 1.1852 | 2
RetailMedium | Bulk_Storage | Storage (General) | PSZAC_Storage | SZVAVHP_Storage | Ancillary | Y | 9.7% | 2395.124 | 47902.48 | 1 | 0 | 0
RetailMedium | Office/Stuff | Office Area (>250 square feet) | PSZAC_Office | SZVAVHP_Office | Retail | Y | 2.7% | 666.684 | 13333.68 | 1 | 3.3334 | 5
RetailMedium | Restroom | Restrooms |  |  | Retail | Y | 1.7% | 419.764 | 8395.28 | 1 | 0 | 0 | Restroom: Indirectly conditioned: Transfer air + Exhaust room ( No dedicated HVAC)
Total (1 Building) | Total (8 Spaces) | Total (6 Space types) | Total (8 HVAC Systems) | Total (8 HVAC Systems) |  | Total (8 Conditioned zones) | 100% | 24692 | 493840 |  | 353.5401 | [5 empty] | `
*Note. The area fractions in this prototype align closely with the space distribution shown in the Advanced Energy Design Guide for Medium to Big Box Retail Buildings (ASHRAE),
| which indicates approximately 85% sales area and 15% non-sales area. The CalBEM RetailMedium prototype reflects a similar distribution, with 83% allocated to sales area and 17% to non-sales functions. | [12 empty] | Area Distribution By Space Type
[14 empty] | Space Type |  | % Area
[14 empty] | Retail Sales Area (Retail Merchandise Sales) |  | 83%
[6 empty] | Retail Sales Area (Retail Merchandise Sales) | [7 empty] | Corridor Area |  | 0.5%
[6 empty] | Corridor Area | [7 empty] | Storage, Commercial/Industrial (Shipping & Handling) |  | 2.4%
[6 empty] | Storage, Commercial/Industrial (Shipping & Handling) | [7 empty] | Storage (General) |  | 9.7%
[6 empty] | Storage (General) | [7 empty] | Office Area (>250 square feet) |  | 2.7%
[6 empty] | Office Area (>250 square feet) | [7 empty] | Restrooms |  | 1.7%
[6 empty] | Restrooms | [7 empty] | Total |  | 100%
Floorspace-Types-30Oct2024
Retail (CEUS 2022, statewide %)
|  | Conditioned |  | Ventilated
|  | 82.62% |  | 0.8344
Advanced Energy Design Guide for Medium to Big Box Retail Buildings
|  | Space Type | Medium Box Area (ft²) | Percentage of Total Area
|  | Main sales | 31500 | 77.78%
|  | Perimeter sales | 3076 | 7.6%
|  | Enclosed office | 300 | 0.74%
|  | Meeting room | 500 | 1.23%
|  | Break room | 500 | 1.23%
|  | Restroom | 625 | 1.54%
|  | Mechanical room | 200 | 0.49%
|  | Corridor | 450 | 1.11%
|  | Vestibule | 300 | 0.74%
|  | Active storage | 3050 | 7.53%
|  | Total | 40500 | 100%
|  | Sales |  | 85.38%
|  | Non-Sell |  | 14.61%
N

## Envelope
Envelope - RetailMedium
Element | Prototype | Assembly Type | Construction | Thermal Properties | Vintage | Selected T24 | Note | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
External Wall | RetailMedium | ExtWall_MetalFramed_NonRes | Metal framed wall: Metal frame + insulation + Gypsum board | U-factor IP | Pre 1978 | N/A | ASHRAE 90.1, 2022, Table A3.3.3.1, 3.5", R-0 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352
[5 empty] | 1978-1997 | 1986 | Package A with Heat Capacity 10.0-14.99 (Btu/F-ft²) - Still are lower than the next vintage! | 0.15083 | 0.15748 | 0.15748 | 0.14368 | 0.14368 | 0.21645 | 0.21645 | 0.21645 | 0.21645 | 0.21645 | 0.18622 | 0.18622 | 0.18622 | 0.15873 | 0.15873 | 0.15083
[5 empty] | 1998-2007 | 2001 | Table 1-H | 0.182 | 0.182 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.189 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182 | 0.182
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.098 | 0.062 | 0.082 | 0.062 | 0.062 | 0.098 | 0.098 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062 | 0.062
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.06 | 0.055 | 0.071 | 0.055 | 0.055 | 0.06 | 0.06 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055
Roof | RetailMedium | FlatRoof_WoodFramedAndOther_NonRes | Metal deck roof: Roof membrane + insulation + metal decking | U-factor IP | Pre 1978 | N/A | Considering 30 years for roof/ insulation replacement. | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 1978-1997 | 1992 |  | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 1998-2007 | 2001 | Table 1-H | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.078 | 0.078 | 0.078 | 0.078 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.049 | 0.039 | 0.039 | 0.039 | 0.049 | 0.075 | 0.067 | 0.067 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.047 | 0.047 | 0.047 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028
Window | RetailMedium | FixedWindow_NonRes | CBECS 2018 shows that ~ 50 % of retail that were built before 2000 are single pane | U-factor IP | Pre 1978 | N/A | 2021 ASHRAE Handbook of Fundamentals - Section 15.9 Table 4 for single pane & T24, 2013 Table 140.3-B for double pane (50%-50%) | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74
[5 empty] | 1978-1997 | N/A |  | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74
|  |  | Double pane |  | 1998-2007 | 2001 | Table 1-H | 0.49 | 0.49 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.34 | 0.36 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.36
| RetailMedium | FixedWindow_NonRes | CBECS 2018 shows that ~ 50 % of retail that were built before 2000 are single pane | SHGC | Pre 1978 | N/A | 2021 ASHRAE Handbook of Fundamentals - Section 15.22 Table 10 for single pane & T24, 2013 Table 140.3-B for double pane (50%-50%) | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52
[5 empty] | 1978-1997 | N/A |  | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52 | 0.52
|  |  | Double pane |  | 1998-2007 | 2001 | Table 1-H (Non north 0-10%) | 0.49 | 0.47 | 0.61 | 0.61 | 0.61 | 0.61 | 0.61 | 0.61 | 0.61 | 0.47 | 0.47 | 0.47 | 0.47 | 0.46 | 0.46 | 0.49
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.22 | 0.25 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.25
Skylight | RetailMedium | Skylight | Translucent | U-factor IP | Pre 1978 | N/A | from 1992 code cycle | 0.85 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
[5 empty] | 1978-1997 | N/A |  | 0.85 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
|  |  | Plastic curb mounted |  | 1998-2007 | 2001 | Table 1-H | 0.87 | 1.1 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 0.87
[5 empty] | 2008-2018 | 2013 | Table 140.3-B | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88
[5 empty] | 2019+ | 2025 | Table 140.3-B | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88
| RetailMedium | Skylight | Translucent | SHGC | Pre 1978 | N/A | From 1992 code cycle | 0.7047 | 0.7482 | 0.7482 | 0.7482 | 0.7482 | 0.7482 | 0.7482 | 0.7482 | 0.7482 | 0.7482 | 0.7047 | 0.7047 | 0.7047 | 0.7047 | 0.7047 | 0.7047
[5 empty] | 1978-1997 | N/A |  | 0.7047 | 0.7482 | 0.7482 | 0.7482 | 0.7482 | 0.7482 | 0.7482 | 0.7482 | 0.7482 | 0.7482 | 0.7047 | 0.7047 | 0.7047 | 0.7047 | 0.7047 | 0.7047
|  |  | Plastic curb mounted |  | 1998-2007 | 2001 | Table 1-H (For SRR 0-2%) | 0.77 | 0.77 | 0.79 | 0.79 | 0.79 | 0.77 | 0.77 | 0.77 | 0.77 | 0.77 | 0.77 | 0.77 | 0.77 | 0.71 | 0.71 | 0.77
[5 empty] | 2008-2018 | 2013 | There is no requirement in the code (considered same as 2001) | 0.77 | 0.77 | 0.79 | 0.79 | 0.79 | 0.77 | 0.77 | 0.77 | 0.77 | 0.77 | 0.77 | 0.77 | 0.77 | 0.71 | 0.71 | 0.77
[5 empty] | 2019+ | 2025 |  | 0.77 | 0.77 | 0.79 | 0.79 | 0.79 | 0.77 | 0.77 | 0.77 | 0.77 | 0.77 | 0.77 | 0.77 | 0.77 | 0.71 | 0.71 | 0.77
Infiltration
|  |  | Building | Zones | Vintage | I_75 (cfm/ft²) 6-sdied Infiltration rate @ 75 pa | Note | I-design (cfm/ft²) (4-sided Infiltration rate at normal pressure) (Design flow rate approach and Flow/Exterior Wall Area calculation method)
|  | Infiltration | RetailMedium |  | Pre 1978 | 1.1 | 2022 CASE report (Table 38) | #REF! | [15 empty] | Floor or roof area (ft2) | 24692
[5 empty] | 1978-1997 | 1.1 | 2022 CASE report (Table 38) | #REF! | [15 empty] | Walls area (ft2) | 12680
[5 empty] | 1998-2007 | 1.1 | 2022 CASE report (Table 38) | #REF! | [15 empty] | Building 4 sided area (ft2) | 12680
[5 empty] | 2008-2018 | 1 | 2022 CASE report (Table 38) & T24, part 6, 2008-2016 (Table 140.3-B), Dodge 2023 data | #REF! | [15 empty] | Building 6 sided area (ft2) | 62064
[5 empty] | 2019+ | 0.6 (barrier in all CZ) | 2022 CASE report (Table 38) & T24, part 6, 2025 (Table 140.3-B) | #REF!
Infiltration_rate_report_14May2025-Short-Version.docx
Source: T24 air barrier requirements (all editions) , the standardized infiltration rate reported in the 2022 CASE report, and Dodge 2023 data
Entrance Door Infiltration | [6 empty] | Loading Dock Infiltration
Parameter | Value | Units | Description | Source |  |  | Parameter | Value / Formula | Units | Description | Source
Entrance Door Infiltration | 1105.5366 | cfm | Entrance infiltration airflow;CFM = CA × Door Area × Rp | NREL, Retail Building Guide for Entrance Energy Efficiency Measures, Section 1 |  |  | Loading Dock CFM | 20739.1304 | cfm | Design infiltration rate through loading dock when open | Retail Building Guide for Entrance Energy Efficiency Measures, Section 5, Eq. 5-1
CA | 175.482 | cfm/ft²/√in.H₂O | Airflow coefficient based on PPH and entrance/vestibule configuration | NREL, Retail Building Guide for Entrance Energy Efficiency Measures, Section 1, Equations 1-1 through 1-4 |  |  | Loading Dock Door Area | 90 | ft² | Effective open area of loading dock door | Assumed
PPH | 76.9231 | people/hr | Annual average one-way trips through each modeled entrance during entrance operating hours | NREL, Retail Building Guide for Entrance Energy Efficiency Measures, Section 1 |  |  | Loading Dock Door Number | 2 | # |  | Assumed
Transactions/week | 3500 | transactions/week | Example weekly retail transaction volume used to estimate door traffic | NREL, Retail Building Guide for Entrance Energy Efficiency Measures |  |  | Reference Door Area | 230 | ft² | Reference effective door area used to produce Table 5-1 | Retail Building Guide for Entrance Energy Efficiency Measures, Section 5
Operating hours/week | 91 | hr/week | Weekly hours during which the customer entrance is available for use | 8 AM–9 PM, 7 days/week |  |  | CFM230 | 26500 | cfm | Infiltration rate for 230-ft² reference opening for climate Zone 3B | Retail Building Guide for Entrance Energy Efficiency Measures, Table 5-1
Trips/customer | 2 | one-way trips/customer | Assumes each transaction represents one customer who enters once and exits once | Assumed
Number of main entrances | 1 | entrance | Number of equivalent customer entrances among which traffic is distributed | Based on the Geometry |  |  | Vestibule Types:
Vestibule Type | Sliding doors - across | — | Entrance/vestibule configuration used to select the CA equation | Based on the Geometry |  |  | without a vestibule | No vestibule
Door Area | 42 | ft² | Effective/total open area of modeled entrance door | Based on the Geometry |  |  | vestibule with swinging doors | Swinging doors
Wind Speed | 10 | mph | Average wind speed while the entrance is in use | Assumed based on representative California weather |  |  | vestibule with sliding doors, where the inner and outer doors are across from each other | Sliding doors - across
Wind Impact | Moderate | — | Wind-pressure exposure assumption; Moderate corresponds to Cp = 0.45 | Assumed; Cp definition and options from NREL, Retail Building Guide for Entrance Energy Efficiency Measures, Table 1-1 |  |  | vestibule with sliding doors, where the outer doors are on the left or right side of the vestibule | Sliding doors - side
Rp | 0.15 | √in.H₂O | Pressure factor based on average wind speed and wind-pressure impact | NREL, Retail Building Guide for Entrance Energy Efficiency Measures, Section 1, Step 2, Table 1-1
Wind speed | (C_p=0.45) | (C_p=0.70) | Source
5 mph | 0.07 | 0.09 | NREL, Retail Building Guide for Entrance Energy Efficiency Measures, Section 1, Step 2, Table 1-1
10 mph | 0.15 | 0.18
15 mph | 0.22 | 0.28
20 mph | 0.29 | 0.37

## HVAC System
HVAC system - RetailMedium
Vintage | Heating | Cooling | Air Distribution | Other systems | Source | Note
Existing | PSZAC (furnace) | PSZAC (DX cooling) | CAV | OA mixing Economizer for Vintage 3 and 4 | CEUS 2022 | 4 RTUs for Core zone (each with a max of 20 ton)
New Construction | SZVAVHP | SZVAVHP | VAV | OA mixing Economizer | Title 24, 2025, Engineering judgement | 4 systems for Core zone (each with a max of 20 ton)
Efficiency of HVAC System (Efficiency is capacity-dependent. The following table provides a general estimate of system efficiency based on preliminary simulations in one climate zone, or assuming cooling load based on rule of thumb)
Vintage | Upgrade/Installed year | Heating | Cooling | Source
Pre 1978 | 2008 | Thermal Efficiency of 80% | SEER=13.0 for <65 kBtu/h EER 10.1 for 65-135 kBtu/h EER 9.5 for 135-240 kBtu/h EER 9.3 for 240-760 kBtu/h | T24, Table 112-A (2008) 10 CFR § 431.97, Table 1 (2008) California Title 20 Appliance Efficiency Regulations, Table E-4, Standards for Gas- and Oil-Fired Central Furnaces (2008)
1978-1997
1998-2007
2008-2018 | 2013 | Thermal Efficiency of 80%; | SEER 13 for <65 kBtu/h EER 11.0 for 65-135 kBtu/h EER 10.8 for 135-240 kBtu/h EER 9.8 for 240-760 kBtu/h | T24, 2013 Table 110.2-J & Table 110.2-A (2013) 10 CFR § 431.97(b) Table 1 (2013)
New Construction | 2025 | HSPF 8.0 for <65 kBtu/h COP 3.4 for 65-135 kBtu/h COP 3.3 for 135-240 kBtu/h COP 3.2 for >240 kBtu/h | SEER 14 for <65 kBtu/h EER 10.8, IEER 13.9 for 65-135 kBtu/h EER 10.4, IEER = 13.3 135-240 kBtu/h EER 9.3, IEER=12.3 for >240 kBtu/h | 10 CFR § 431.97(b) Table 1 (2025) Title 20 Appliance Efficiency Regulations, Section 1605.1, Table C-5 (2025) T24, Table 110.2-B (2025)
| cfm | 5000 12.5 tons _ 8000 cfm
Fan Power
Vintage | Approach | System | Total Static Pressure (TSP) (in w.c.) | Fan Efficiency [ACM 2025] | Motor Efficiency | Fan Power Index (W/cfm) | Data Source | Note
Existing | PNNL 90.1-2011, TSP | CAV < 7,437 cfm | 2.5 | 0.65 | ASHRAE 90.1, 2004, Table 10.8 * |  | Fan power formula: PNNL 20405, 2010, section 5.2.2.5 TSP and fan efficiency: PNNL 20405, 2010, Table 5.11, 90.1-04ac values Motor and drive efficiency: ASHRAE 90.1, 2004, Table 10.8
|  | CAV >= 7,437 cfm | 4.09
Brake horsepower (bhp) = (Supply cfm × TSP in w.c.) / (6356 × fan efficiency)
Fan power (w/cfm) = (bhp × 746) / ( supply cfm × motor efficiency )
New Construction | ACM 2025 | SZVAVHP (System 7b), >5,000 and ≤10,000 cfm | TSP = fan power × motor efficiency × fan efficiency × 6356 / 746 | 0.65 | 2025 ACM Table 12 ** | 0.72 | Fan power index: [ACM 2025, Table 13] Motor efficiency: [ACM 2025, Table 12]
|  | SZVAVHP (System 7b), >10,000 cfm | TSP = fan power × motor efficiency × fan efficiency × 6356 / 746 |  |  | 0.676
* According to PNNL 20405 section 5.2.2.5, the full-load efficiency of the motor serving the fan is taken from ASHRAE 90.1, 2004, Table 10.8, based on motor nameplate and assuming enclosed motors operating at 1,800 rotations per minute (rpm) Motor nameplate size (bhp) = brake horsepower (bhp) × 1.1 ( using a 10% oversizing factor)
** The full‑load efficiency of the motor serving the fan is taken from ACM 2025 Table 12 based on the cfm of the fan. Brake horsepower (bhp) = (Supply cfm from sizing run × fan power in W/cfm) / 746. Note: HVAC: 4 core systems, each max 20 ton (about 8,000 cfm). ACM System 7b mid bin. Note: Only if a unit exceeds 10,000 cfm. Design note is max 20 ton, which is the row above.
〖𝐹𝑎𝑛 𝑝𝑜𝑤𝑒𝑟〗_(𝑤/𝑐𝑓𝑚)=(〖𝑇𝑆𝑃〗_(𝑖𝑛 𝑤.𝑐)∗746)/(6356∗𝜇_𝑓𝑎𝑛∗𝜇_𝑚𝑜𝑡𝑜𝑟 )
𝑏ℎ𝑝=(𝑐𝑓𝑚∗〖𝑇𝑆𝑃〗_(𝑖𝑛 𝑤.𝑐.))/〖6356∗𝜇〗_𝑓𝑎𝑛
〖𝐹𝑎𝑛 𝑝𝑜𝑤𝑒𝑟〗_(𝑤/𝑐𝑓𝑚)=(𝑏ℎ𝑝∗746)/(𝑐𝑓𝑚∗𝜇_𝑚𝑜𝑡𝑜𝑟 )
𝑏ℎ𝑝=(〖𝐹𝑎𝑛 𝑝𝑜𝑤𝑒𝑟〗_(𝑤/𝑐𝑓𝑚)∗𝑐𝑓𝑚∗𝜇_𝑚𝑜𝑡𝑜𝑟)/746

## Ventilation
Outdoor Airflow Rate - RetailMedium
Space/Thermal Zone | Number of People | Floor Area (ft²) | cfm/person [T24, 2025, Equation 120.1-F and Table 120.1-A] | cfm/ft² [T24, 2025, Equation 120.1-F and Table 120.1-A] | Required Exhaust Rate [T24, 2025, Table 120.1-B – minimum exhaust rates] | Total cfm Driven by People | Total cfm Driven by Area | Total cfm Driven by Exhaust | Total cfm | Notes
Core_Retail | 292.9953 | 17235.016 | 15 | 0.2 |  | 4394.9291 | 3447.0032 | 0 | 4394.9291
Point_of_Sale | 27.7044 | 1629.672 | 15 | 0.2 |  | 415.5664 | 325.9344 | 0 | 415.5664
Front_Retail | 27.7044 | 1629.672 | 15 | 0.2 |  | 415.5664 | 325.9344 | 0 | 415.5664
Front_Entry | 0.6173 | 123.46 | 15 | 0.15 |  | 9.2595 | 18.519 | 0 | 18.519
Loading_Dock | 1.1852 | 592.608 | 15 | 0.15 |  | 17.7782 | 88.8912 | 0 | 88.8912 | Shipping/receiving
Bulk_Storage | 0 | 2395.124 | 15 | 0.15 |  | 0 | 359.2686 | 0 | 359.2686 | Warehouses
Office/Stuff | 3.3334 | 666.684 | 15 | 0.15 |  | 50.0013 | 100.0026 | 0 | 100.0026
Restroom | 0 | 419.764 | 15 | 0.15 | 4*50/70 (cfm/unit) | 0 | 62.9646 | 200 | 200
Currently assuming the entry is not actively ventilated due to doors (and connection to core) providing air.

## Thermostat
Thermostat Setpoints - RetailMedium
Spaces/Zones | Setpoint | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16 | Source
All spaces except Bulk_Storage and Loading_Dock | Heating Setpoint (F) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | T24 2022 - Appendix 5.4B
| Heating Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
| Cooling Setpoint (F) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
| Cooling Setback (F) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
Bulk_Storage and Loading_Dock | Heating Setpoint (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | Engineering Judgment (Semi‑conditioned space)
| Heating Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
| Cooling Setpoint (F) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
| Cooling Setback (F) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85

## Water Heater
Water Heater - RetailMedium
Vintage | WH Type | Efficiency | Number of WH | Tank Volume (gal) | Tank Loss | Source
Existing | Electric | 1 | 1 | 30 See table below for CZ-specific values: Climate Zone Water Heater Sizing and Loss Coefficients, Storage Volume column (col F) | 1.2 %/hr See table below: Climate Zone Water Heater Sizing and Loss Coefficients, Standby Loss column (col G) | See table below for sources: Climate Zone Water Heater Sizing and Loss Coefficients
New Construction | Electric | 1 | 1 | 30 See table below for CZ-specific values: Climate Zone Water Heater Sizing and Loss Coefficients, Storage Volume column (col F) | 1.2 %/hr See table below: Climate Zone Water Heater Sizing and Loss Coefficients, Standby Loss column (col G) | See table below for sources: Climate Zone Water Heater Sizing and Loss Coefficients
Peak Hot Water Consumption
Space Name | Baseline WH Type [CEUS 2022] | Total Area (ft²) | Number of People | Hot Water Usage Specification (gal/hr per person) [T24, 2022, Appendix 5.4A , sheet: "2022 SpaceFuncData-Input"] | Peak Hot Water Usage (gal/hr) | Peak Hot Water Usage (gal/min) | Note
Core_Retail | Electric | 17235.016 | 292.9953 | 0.18 | 52.7391 | 0.87899 | For space types marked with an asterisk (the ‘*’ symbol), the water‑heater type is listed as electric in Appendix 5.4A, sheet ‘2022 SpaceFuncData‑Input.’ However, we modified the value based on CEUS data, which indicates that gas is the primary fuel type.
Point_of_Sale | Electric | 1629.672 | 27.7044 | 0.18 | 4.9868 | 0.083113
Front_Retail | Electric | 1629.672 | 27.7044 | 0.18 | 4.9868 | 0.083113
Front_Entry | Electric | 123.46 | 0.6173 | 0 | 0 | 0
Loading_Dock | Electric | 592.608 | 1.1852 | 0.18 | 0.21334 | 0.0035556
Bulk_Storage | Electric | 2395.124 | 0 | 0 | 0 | 0
Office/Stuff | Electric | 666.684 | 3.3334 | 0.18 | 0.60002 | 0.01
Restroom | Electric | 419.764 | 0 | 0 | 0 | 0
Total | Gas storage |  |  |  | 0 |  | Minimum peak hot water usage is 75 gal according to ACM 2025
Total | Electric resistance |  |  |  | 75
Design supply temperature (°F) | 135 | CEC-400-2022-009-CMF-REV2-AP5.4B
WH system factor | 0.6 | 2025 ACM §5.9.2 Rated Capacity
Water mass conversion (lb/gal) | 8.2877 | 2025 ACM §5.9.2 Rated Capacity
Reheat multiplier | 0.4 | 2025 ACM §5.9.2 Storage Volume
Climate Zone Water Heater Sizing and Loss Coefficients (Individual WH)
Water Heater Name | Climate Zone | Minimum Monthly Mains Temp (°F) [T24 2022 - Appendix 5.4B] | Heat Output (Btu/hr) [ACM, 2025, 5.9.2: Rated capacity section] | WH Capacity (Btu/hr) [ACM, 2025, 5.9.2: Rated capacity section] | Required Energy Input (Btu/hr) | Storage Volume (gal) | Standby Loss [Title 20, §1605.1 Table F-4; Appendix B: Water Heating Calculation Method] |  | Off/On Cycle Loss Coefficient to Ambient Temp |  | Source/Note
WH_RetailMedium | CZ01 | 47.9 | 54139.4002 | 32483.6401 | 34121 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F | Required Energy Input: vendor/available catalog size (Market data table). Storage Volume: standard/available catalog tank size (Market data table).
WH_RetailMedium | CZ02 | 50.8 | 52336.8255 | 31402.0953 | 34121 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F
WH_RetailMedium | CZ03 | 52.2 | 51466.617 | 30879.9702 | 34121 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F
WH_RetailMedium | CZ04 | 52.7 | 51155.8282 | 30693.4969 | 30709 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F
WH_RetailMedium | CZ05 | 51.6 | 51839.5635 | 31103.7381 | 34121 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F
WH_RetailMedium | CZ06 | 56.8 | 48607.3605 | 29164.4163 | 30709 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F
WH_RetailMedium | CZ07 | 58.4 | 47612.8365 | 28567.7019 | 30709 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F
WH_RetailMedium | CZ08 | 58.4 | 47612.8365 | 28567.7019 | 30709 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F
WH_RetailMedium | CZ09 | 57.6 | 48110.0985 | 28866.0591 | 30709 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F
WH_RetailMedium | CZ10 | 57.1 | 48420.8872 | 29052.5323 | 30709 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F
WH_RetailMedium | CZ11 | 50.5 | 52523.2987 | 31513.9792 | 34121 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F
WH_RetailMedium | CZ12 | 51.4 | 51963.879 | 31178.3274 | 34121 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F
WH_RetailMedium | CZ13 | 51.7 | 51777.4057 | 31066.4434 | 34121 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F
WH_RetailMedium | CZ14 | 50.1 | 52771.9297 | 31663.1578 | 34121 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F
WH_RetailMedium | CZ15 | 63.2 | 44629.2645 | 26777.5587 | 27297 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F
WH_RetailMedium | CZ16 | 41.4 | 58179.654 | 34907.7924 | 40946 | 30 | 1.2 | %/hr | 3.0024 | Btu/h·°F
Market data
Catalog gas input (Btu/h) | Input source | Elec resistance tank (kW) | Elec resistance (Btu/h) | Catalog gas tank (gal) | Tank source | Elec tank (gal) | Elec tank source | Sources and links → Note tab
60000 | Grainger | 1.5 | 5118 | 34 | ENERGY STAR | 6 | Grainger
75100 | Grainger | 2 | 6824 | 35 | Grainger | 10 | Grainger
76000 | Both | 3 | 10236 | 48 | Grainger | 15 | Grainger
80000 | Grainger | 4.5 | 15355 | 50 | Both | 20 | Grainger
99900 | ENERGY STAR | 6 | 20473 | 55 | ENERGY STAR | 28 | Grainger
100000 | Both | 8 | 27297 | 60 | ENERGY STAR | 30 | Grainger
120000 | ENERGY STAR | 9 | 30709 | 65 | Both | 36 | Grainger
125000 | Both | 10 | 34121 | 72 | Grainger | 40 | Grainger
130000 | Both | 12 | 40946 | 75 | Both | 47
145000 | ENERGY STAR | 12.1 | 41287 | 76 | Grainger | 50
150000 | ENERGY STAR | 18 | 61419 | 80 | Both | 65
156000 | Grainger | 24 | 81891 | 82 | Grainger | 80
160000 | Both | 27 | 92128 | 85 | Grainger | 85
175000 | ENERGY STAR | 36 | 122837 | 90 | Both | 105
180000 | Grainger | 54 | 184256 | 91 | Grainger | 120
199000 | ENERGY STAR |  |  | 100 | Both
199900 | Both |  |  | 110 | ENERGY STAR
200000 | ENERGY STAR |  |  | 119 | Both
250000 | Both |  |  | 125 | ENERGY STAR
251000 | ENERGY STAR
270000 | Grainger
285000 | ENERGY STAR
300000 | Both
320000 | ENERGY STAR
360000 | Grainger
398000 | ENERGY STAR
399000 | ENERGY STAR
399900 | Both
499900 | Grainger
550000 | Grainger
715000 | Grainger

## Interior Lights
Interior Lighting - RetailMedium
Space Type | New Construction |  |  | Existing
| LPD (W/ft²) | Additional LPD for Portable Lighting (W/ft²) | Source | LPD (W/ft²) | Additional LPD for Portable Lighting (W/ft²) | Source | Note
Office Area (>250 square feet) | 0.6 | 0.1 | T24, part 6, 2025, Table 140.6-C (Area category method) | 0.75 | - | T24, part 6, 2016, Table 140.6-C (Area category method) | It is assumed that 50% of the additional allowance lighting is in use.
Storage, Commercial/Industrial (Shipping & Handling) | 0.6 |  |  | 0.9 |  |  | Used the value for General Commercial and Industrial Work Areas in 2016
Restrooms | 0.65 |  |  | 0.6
Storage (General) | 0.4 |  |  | 0.6 |  |  | Space type used: Storage, Commercial/Industrial _ Warehouse in 2025 Commercial and Industrial Storage Area in 2016
Retail Sales Area (Retail Merchandise Sales) | 0.95 | 0.104 |  | 1.2 | 0.06 |  | The percentage of additional lighting depends heavily on the specific store type. As a general assumption, additional lighting is calculated for 20% of the Retail Sales Area.
Corridor Area | 0.7 |  |  | 0.95 |  |  | The values from Table 140.6-C have been slightly adjusted for this space to align with main entry space type

## Ext Lighting
Exterior Lighting - RetailMedium
Motion Controlled Luminaires (W) | Non-motion Controlled Luminaires (W) | Total (W) | Source
796.2756 | 651.2844 | 1447.56 | T24, 2022
Exterior Lighting
Items (Assume LZ2) | Assumptions [2019 Outdoor Lighting CASE Report & PNNL 90.1-2010 TSD] |  | Unit | Lighting Power Allowance [T24, 2025, Table 140.7-A & 140.7-B] | Unit | Exterior lighting power (w)
IWA (Initial Wattage Allowance) |  |  |  | 200 | W | 200
Parking area | 400 ft² for every parking space [2019 Lighting CASE report, Appendix H] 1 parking space per 360 ft² of gross building area [2019 Lighting CASE report,Table 38] | 27435.5556 | (ft²) | 0.019 | (W/ft²) | 521.2756
Building Entrance | 1 per 5,000 sf footprint [2019 Lighting CASE report,Table 36] | 5 | (count) | 15 | (W/ea) | 75
Hardscape Ornamental Light | 0.1 ft² per 1 ft² of gross bldg area [2019 Lighting CASE report,Table 36] *The 0.5 multiplier has not been applied, as it is assumed it will be incorporated later during the measure analysis study. | 2469.2 | (ft²) | 0.007 | (W/ft²) | 17.2844
Building façade | 0.1 W per 1 ft² of facade area Façade Area = Perimeter × 0.5 × 20 ft The 0.5 factor assumes that only half of the perimeter walls are lit. -Formula ia developed based on the 2019 Outdoor Lighting CASE report | 6340 | (ft²) | 0.1 | (W/ft²) | 634
Sales canopy | 0.1 ft² per ft² of gross bldg area | 0 | (ft²) | 0.47 | (W/ft²) | 0
Motion controlled Luminaires | [5 empty] | 796.2756
Non-motion-controlled Luminaires | [5 empty] | 651.2844
Total | [5 empty] | 1447.56
*Developed based on 2019 Outdoor Lighting CASE Report
Perimeter | 634
Total floor area | 24692
Floors | 1
The referenced report for many of the assumptions on this tab is the 2019 Outdoor Lighting CASE Report, which contains the following table. For retail, they applied the value to only 50% of the floor area. Perhaps the same factor should be applied to the prototype.

## Equipment
Equipment - RetailMedium
Space Type | Plug load Power Density (W/ft²) | Gas Power Density (Btu/hr-ft²) | Refrigeration Power Density (W/ft²) | Source | Note
Office Area (>250 square feet) | 0.7 |  |  | Proposed Updates to Equipment Power Densities and Schedules in the 2028 Energy Code Nonresidential and Multifamily Alternative Calculation Method (NRMFACM) Reference Manual, August 7, 2025
Storage, Commercial/Industrial (Shipping & Handling) | 0.5 |  |  | T24 2022 - Appendix 5.4A: Space Use Data-T24N-2022
Restrooms | 0 |  |  | T24 2022 - Appendix 5.4A: Space Use Data-T24N-2022
Storage (General) | 0.2 |  |  | T24 2022 - Appendix 5.4A: Space Use Data-T24N-2022 | Matches Retail/All Other; PNNL prototype =~0.7; T24 Appendix 5.4A =0.2
Retail Sales Area (Retail Merchandise Sales) | 0.3 |  |  | Mix of sources including "High-Efficiency Retrofit Lessons for Retail from a SuperTarget" (2013) & ASHRAE 90.1 Prototype
Corridor Area | 0 |  |  | T24 2022 - Appendix 5.4A: Space Use Data-T24N-2022
Background Data [To be deleted prior to publication]
[6 empty] | ~W PNNL | ft² | W/ft² PNNL | W/ft² CEC
[5 empty] | BACK_SPACE | 3000 | 4089.1018 | 0.73366 | 0.2
[5 empty] | CORE_RETAIL | 5000 | 17227.4227 | 0.29023 | 0.4
[5 empty] | POINT_OF_SALE | 3000 | 1623.3053 | 1.8481 | 0.4
[5 empty] | FRONT_RETAIL | 500 | 1623.3053 | 0.30801 | 0.4
it is reasonable to leave the current 5.0 W/ft² assumption in the NMACM for refrigeration loads in Grocery Sales area

## Schedules
Schedules - RetailMedium
Zone | Schedule Category | Schedule | Source | Type | Hour
[5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
All Zones | Retail | Occupancy | NLR Study "Final Optimization Report: Empowering Energy Efficiency in Existing Big-Box Retail/Grocery Stores", (2020) & Adjusted based on Google Popular Time | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.7 | 0.8 | 0.8 | 0.6 | 0.3 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.6 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.8 | 0.7 | 0.6 | 0.5 | 0.3 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.5 | 0.7 | 0.8 | 0.8 | 0.8 | 0.8 | 0.7 | 0.7 | 0.6 | 0.5 | 0.4 | 0.2 | 0 | 0 | 0
All Zones | Retail | Lights | T24 2022 - Appendix 5.4B, [Retail] | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.7 | 0.05 | 0.05
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.7 | 0.05 | 0.05
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.7 | 0.05 | 0.05
All Zones | Retail | ElecEquipment | Plug load and schedules project with CEC, 2025 | Weekday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.4 | 0.4 | 0.4
|  |  |  | Saturday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.4 | 0.4 | 0.4
|  |  |  | Sunday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.4 | 0.4 | 0.4
All Zones | Retail | HVACAvail | T24 2022 - Appendix 5.4B, [Retail] | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
All Zones | Retail | ServiceHotWater | T24 2022 - Appendix 5.4B, [Retail] | Weekday | 0.04 | 0.05 | 0.05 | 0.04 | 0.04 | 0.04 | 0.04 | 0.15 | 0.23 | 0.32 | 0.41 | 0.57 | 0.62 | 0.61 | 0.5 | 0.45 | 0.46 | 0.47 | 0.42 | 0.34 | 0.33 | 0.23 | 0.13 | 0.08
|  |  |  | Saturday | 0.11 | 0.1 | 0.08 | 0.06 | 0.06 | 0.06 | 0.07 | 0.2 | 0.24 | 0.27 | 0.42 | 0.54 | 0.59 | 0.6 | 0.49 | 0.48 | 0.47 | 0.46 | 0.44 | 0.36 | 0.29 | 0.22 | 0.16 | 0.13
|  |  |  | Sunday | 0.07 | 0.07 | 0.07 | 0.06 | 0.06 | 0.06 | 0.07 | 0.1 | 0.12 | 0.14 | 0.29 | 0.31 | 0.36 | 0.36 | 0.34 | 0.35 | 0.37 | 0.34 | 0.25 | 0.27 | 0.21 | 0.16 | 0.1 | 0.06
All Zones | Retail | Infiltration | T24 2022 - Appendix 5.4B, [Retail] | Weekday | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1
|  |  |  | Saturday | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1
|  |  |  | Sunday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1
All Zones | Retail | HtgSetpt | T24 2022 - Appendix 5.4B, [Retail] | Weekday | 60 | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 60 | 60 | 60
|  |  |  | Saturday | 60 | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 60 | 60
|  |  |  | Sunday | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 60 | 60 | 60 | 60 | 60
All Zones | Retail | ClgSetpt | T24 2022 - Appendix 5.4B, [Retail] | Weekday | 85 | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 85 | 85 | 85
|  |  |  | Saturday | 85 | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 85 | 85
|  |  |  | Sunday | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 85 | 85 | 85 | 85 | 85
Storage & Loading Dock
Storage & Loading Dock | Ancillary | Occupancy | T24 2022 - Appendix 5.4B | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.7 | 0.8 | 0.8 | 0.6 | 0.3 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.6 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.8 | 0.7 | 0.6 | 0.5 | 0.3 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.5 | 0.7 | 0.8 | 0.8 | 0.8 | 0.8 | 0.7 | 0.7 | 0.6 | 0.5 | 0.4 | 0.2 | 0 | 0 | 0
Storage & Loading Dock | Ancillary | Lights | T24 2022 - Appendix 5.4B | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.7 | 0.05 | 0.05
|  |  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.7 | 0.05 | 0.05
|  |  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.7 | 0.05 | 0.05
Storage & Loading Dock | Ancillary | ElecEquipment | Plug load and schedules project with CEC, 2025 | Weekday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.4 | 0.4 | 0.4
|  |  |  | Saturday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.4 | 0.4 | 0.4
|  |  |  | Sunday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.4 | 0.4 | 0.4
Storage & Loading Dock | Ancillary | HVACAvail | T24 2022 - Appendix 5.4B | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
Storage & Loading Dock | Ancillary | ServiceHotWater | T24 2022 - Appendix 5.4B | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Storage & Loading Dock | Ancillary | Infiltration | T24 2022 - Appendix 5.4B | Weekday | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1
|  |  |  | Saturday | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1
|  |  |  | Sunday | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1
Storage & Loading Dock | Ancillary | HtgSetpt | Engineering Judgement | Weekday | 50 | 50 | 50 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
|  |  |  | Saturday | 50 | 50 | 50 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
|  |  |  | Sunday | 50 | 50 | 50 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
Storage & Loading Dock | Ancillary | ClgSetpt | Engineering Judgement | Weekday | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
|  |  |  | Saturday | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
|  |  |  | Sunday | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
Loading Dock EL1 | Ancillary | Loading Dock Door Infiltration | CASE Report - Dock Seals (2017) Truck Trip Generation by Grocery Stores (2010) | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Other
| Building | ExtLightingNonMotionCtrl |  | Weekday | bar: Hour 1 to Hour 24
Saturday | bar: Hour 1 to Hour 24
Sunday | bar: Hour 1 to Hour 24
| Building | ExtLightingMotionCtrl |  | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  |  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Retails | Building | RetailSalePeopleActivityLevel | Based on Activity level schedules in CEC Prototypes | Weekday | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
|  |  |  | Saturday | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
|  |  |  | Sunday | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
Retails | Building | CommonAreaPeopleActivityLevel | Based on Activity level schedules in CEC Prototypes | Weekday | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5
|  |  |  | Saturday | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5
|  |  |  | Sunday | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5 | 146.5

## Energy Usage (hidden)
CalBEM Energy Consumption - RetailMedium | [7 empty] | National Average (EnergyStar Portfoli Manager) |  |  |  | CEUS Energy Consumption : Retail | [8 empty] | PNNL RetailStandAlone 2007 (with floor area of 24,700 ft2) for San Diego shows 55.6 KBTU/ft2 (92% Electricity) |  |  | Elec GJ | Gas GJ
Prototype | CZ | CalBEM Electricity EUI (KBTU/ft²) | CalBEM Gas EUI (KBTU/ft²) | CalBEM Total EUI (KBTU/ft²) | New Construction Electricity EUI (KBTU/ft²) | New Construction Gas EUI (KBTU/ft²) | New Construction Total EUI (KBTU/ft²) | National Average | Acceptable Range (25% Higher) | Acceptable Range (25% Lower) | National Average Acceptable EUI Range | Prototype | CZ | Total Floorspace (Thousand of ft²) | CEUS 2023 Electricity EUI (kBtu/ft²) | CEUS 2023 Gas EUI (kBtu/ft²) | CEUS 2023 Total EUI (kBtu/ft²) | Acceptable Range (25% Higher) | Acceptable Range (25% Lower) | CEUS 2022 Acceptable EUI Range | PNNL RetailStandAlone 2022 (with floor area of 22,500 ft2) for San Diego shows 25.8 KBTU/ft2 (85% Electricity) | Electricty consumption in PNNL 2022 is almost 57% lower than PNNL 2007 rate and Gas is only 16% lower | PNNL 2007 | 1330 | 119
RetailMedium | 1 | [6 empty] | 46.8 | 58.5 | 35.1 | 23.4 | Retail | 1 | 13814 | 37.8732 | 10.4407 | 48.3139 | 60.3924 | 36.2354 | 24.157 |  |  | PNNL 2022 | 573 | 100
| 2 | [6 empty] | 58.4 | 73 | 43.8 | 29.2 |  | 2 | 25239 | 26.6136 | 14.8422 | 41.4558 | 51.8197 | 31.0918 | 20.7279 |  |  |  | 56.92% | 15.97%
| 3 | [6 empty] | 52.3 | 65.375 | 39.225 | 26.15 |  | 3 | 88648 | 34.8024 | 11.8738 | 46.6762 | 58.3452 | 35.0071 | 23.3381
| 4 | [6 empty] | 60.9 | 76.125 | 45.675 | 30.45 |  | 4 | 44551 | 35.4848 | 11.5326 | 47.0174 | 58.7717 | 35.263 | 23.5087
| 5 | [6 empty] | 50.4 | 63 | 37.8 | 25.2 |  | 5 | 9847 | 31.7316 | 14.6034 | 46.335 | 57.9187 | 34.7512 | 23.1675
| 6 | [6 empty] | 57.8 | 72.25 | 43.35 | 28.9 |  | 6 | 92562 | 29.3432 | 4.6062 | 33.9494 | 42.4367 | 25.462 | 16.9747
| 7 | [6 empty] | 57.8 | 72.25 | 43.35 | 28.9 |  | 7 | 63471 | 35.1436 | 3.1732 | 38.3168 | 47.8959 | 28.7376 | 19.1584
| 8 | [6 empty] | 58.9 | 73.625 | 44.175 | 29.45 |  | 8 | 147354 | 29.002 | 4.4697 | 33.4717 | 41.8396 | 25.1038 | 16.7359
| 9 | [6 empty] | 59.6 | 74.5 | 44.7 | 29.8 |  | 9 | 212697 | 32.0728 | 4.7768 | 36.8496 | 46.062 | 27.6372 | 18.4248
| 10 | [6 empty] | 60.2 | 75.25 | 45.15 | 30.1 |  | 10 | 149832 | 31.7316 | 5.2545 | 36.9861 | 46.2326 | 27.7396 | 18.493
| 11 | [6 empty] | 62.3 | 77.875 | 46.725 | 31.15 |  | 11 | 45934 | 36.1672 | 9.2806 | 45.4478 | 56.8098 | 34.0859 | 22.7239
| 12 | [6 empty] | 61.3 | 76.625 | 45.975 | 30.65 |  | 12 | 195816 | 37.532 | 9.7924 | 47.3244 | 59.1555 | 35.4933 | 23.6622
| 13 | [6 empty] | 62.3 | 77.875 | 46.725 | 31.15 |  | 13 | 67122 | 42.3088 | 8.9053 | 51.2141 | 64.0176 | 38.4106 | 25.6071
| 14 | [6 empty] | 62.6 | 78.25 | 46.95 | 31.3 |  | 14 | 39049 | 29.3432 | 4.3674 | 33.7106 | 42.1382 | 25.2829 | 16.8553
| 15 | [6 empty] | 60.1 | 75.125 | 45.075 | 30.05 |  | 15 | 73160 | 34.12 | 8.257 | 42.377 | 52.9713 | 31.7828 | 21.1885
| 16 | [6 empty] | 61.2 | 76.5 | 45.9 | 30.6 |  | 16 | 149464 | 32.7552 | 5.3227 | 38.0779 | 47.5974 | 28.5584 | 19.039
Ref: CEUS 2022 Report
And converted FZ level data to CZ level
CEUS has only one category for all the retails
Background Data [To be deleted prior to publication]

## Weights (hidden)
% of Floor Area per CZ and Vintage Bin - Retail | [7 empty] | % of Floor Area per CZ and Vintage Bin - Retail
Prototype | CZ | Vintage Bin | [5 empty] | Prototype | Vintage Bin | CZ
|  | Pre-1978 | 1978-1997 | 1998-2007 | 2008-2018 | Not available |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
Retail | 1 | [5 empty] | 0% | Retail | Pre-1978 | [16 empty] | 0%
| 2 | [5 empty] | 0% |  | 1978-1997 | [16 empty] | 0%
| 3 | [5 empty] | 0% |  | 1998-2007 | [16 empty] | 0%
| 4 | [5 empty] | 0% |  | 2008-2018 | [16 empty] | 0%
| 5 | [5 empty] | 0% |  | Not available | [16 empty] | 0%
| 6 | [5 empty] | 0% |  | Total | [16 empty] | 0%
| 7 | [5 empty] | 0%
| 8 | [5 empty] | 0%
| 9 | [5 empty] | 0%
| 10 | [5 empty] | 0%
| 11 | [5 empty] | 0%
| 12 | [5 empty] | 0%
| 13 | [5 empty] | 0%
| 14 | [5 empty] | 0%
| 15 | [5 empty] | 0%
| 16 | [5 empty] | 0%
| Statewide | [5 empty] | 0%
Ref: CEUS 2022 dataset
And converted FZ level data to CZ level
CEUS has only one category for all the retails

## PV (hidden)
PV - RetailMedium
TBD

## EV Charger (hidden)
EV Charger - RetailMedium
TBD
Background Data [To be deleted prior to publication]

## Data (hidden)
Space Function | Electric Equipment Load Intensity | Electric Equipment Load Intensity | LPD
Aging Eye/Low-vision (Corridor Area) |  |  | 2013 | 2016 | 2019 | 2025
Aging Eye/Low-vision (Dining)
Aging Eye/Low-vision (Lobby, Main Entry)
Aging Eye/Low-vision (Lounge/Waiting Area)
Aging Eye/Low-vision (Multipurpose Room)
Aging Eye/Low-vision (Religious Worship Area)
Aging Eye/Low-vision (Restroom)
Aging Eye/Low-vision (Stairwell)
Audience Seating Area
Auditorium Area
Auto Repair / Maintenance Area
Barber, Beauty Salon, Spa Area
Civic Meeting Place Area
Classroom, Lecture, Training, Vocational Areas
Concourse and Atria Area
Convention, Conference, Multipurpose and Meeting Area
Copy Room
Corridor Area
Dining Area (Bar/Lounge and Fine Dining)
Dining Area (Cafeteria/Fast Food)
Dining Area (Family and Leisure)
Electrical, Mechanical, Telephone Rooms
Exercise/Fitness Center and Gymnasium Areas
Financial Transaction Area
Healthcare Facility and Hospitals (Exam/Treatment Room)
Healthcare Facility and Hospitals (Imaging Room)
Healthcare Facility and Hospitals (Medical Supply Room)
Healthcare Facility and Hospitals (Nursery)
Healthcare Facility and Hospitals (Nurse's Station)
Healthcare Facility and Hospitals (Operating Room)
Healthcare Facility and Hospitals (Patient Room)
Healthcare Facility and Hospitals (Physical Therapy Room)
Healthcare Facility and Hospitals (Recovery Room)
Hotel Function Area
Kitchen/Food Preparation Area
Kitchenette or Residential Kitchen
Laboratory, Scientific
Laundry Area
Library (Reading Area)
Library (Stacks Area)
Lobby, Main Entry
Locker Room
Lounge, Breakroom, or Waiting Area
Manufacturing, Commercial & Industrial Work Area (Low Bay)
Manufacturing, Commercial & Industrial Work Area (High Bay)
Manufacturing, Commercial & Industrial Work Area (Precision)
Museum Area (Exhibition/Display)
Museum Area (Restoration Room)
Office Area (>250 square feet)
Office Area (<250 square feet)
Parking Garage Area (Parking Zone and Ramps)
Parking Garage Area (Daylight Adaptation Zones)
Pharmacy Area
Retail Sales Area (Grocery Sales)
Retail Sales Area (Retail Merchandise Sales)
Retail Sales Area (Fitting Room)
Religious Worship Area
Restrooms
Stairwell
Storage, Commercial/Industrial (Warehouse)
Storage, Commercial/Industrial (Refrigerated)
Storage, Commercial/Industrial (Shipping & Handling)
Storage (General)
Sports Arena - Playing Area (> 5,000 Spectators)
Sports Arena - Playing Area (2,000 - 5,000 Spectators)
Sports Arena - Playing Area (< 2,000 Spectators)
Sports Arena - Playing Area (Recreational)
Theater Area (Motion Picture)
Theater Area (Performance)
Transportation Function (Baggage Area)
Transportation Function (Ticketing Area)
Videoconferencing Studio
High-Rise Residential Living Spaces
Hotel/Motel Guest Room
All other
Attic
Reception Area
Elevator
Plenum
IT Room (EPD 12)
Computer Room (EPD 20)
Server Room (EPD 45)